## Sheet1
DECK No. | Action Description | KBR Comment | Company | KBR Discipline | Status | Date Cleared by KBR | Petrobras Response By | Petrobras Response Date | Petrobras Response | Petrobras Remarks | Petrobras Discipline | Petrobras Responsible | Seatrium Remarks | Zone | Date Cleared by Petrobras | S3D Item Tags | Punch No | KBR Target Date | Days Since Date Cleared by KBR | Days Since Date Cleared by Seatrium | Punched by (Group) | Petrobras Need Operation to close? (Y/N) | Date Cleared by Petrobras Operation | Petrobras Operation accept closing? (Y/N) | Is Reopen? (Y/N) | Seatrium Target Date Calculated | Petrobras Operation Target Date Calculated | Petrobras Target Date Calculated | Petrobras Target Date | Petrobras Operation Target Date | Seatrium Target Date
None | (General comment all modules) Ensure plate and bottom recess is modelled at the open drain line and overboard line in the gutter as per standard detail | None | None | PIP | OPEN | 01/02/2026 | None |  | None | None | PIP | None | None | M07A |  | TS-M07A-STR-OUTFIT-ELEV1-GUTTER-FWD | 9001C | 26/01/2026 | -25.0000000000000 |  | PB - Operation | False |  | False | False | 04/02/2026 |  |  |  |  | 04/02/2026
None | Coaming overlap to follow I-DE-3010.2S-1400-140-S2N-025_B_STANDARD - TYPICAL DRAIN PIT, DRAIN GUTTER & DRAIN BOX DETAILS sheet 13 | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-07A |  | TS-M07A-STR-OUTFIT-ELEV1-COAMING | 9002C | 22/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Increase the operation volume up to 1m (as close as possible to 1m). | 02-01-26-operation volume updated. | None | PIP | Pending PB Reply | 01/01/2026 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | NO PIPING DCN REQUIRED | M-01 |  | OVERBOARD SIPHON ACCESS VOLUME | 9003C | 15/01/2026 | 0 | 7.00000000000000 | PB - Operation | True | 09/01/2026 | True | None | 04/01/2026 | 04/01/2026 | 11/01/2026 | 11/01/2026 | 04/01/2026 | 04/01/2026
None | Add missing nozzle details | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 3"-DA-B9-XXX1-NI | 9004C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
None | Typical for all modules - Drain box in material handling path should be heavy duty type | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | M10B-L1-DB1-001 | 9005C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Move the coaming as marked | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M10B |  | TS-M10B-STR-OUTFIT-ELEV1-COAMING | 9006C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
None | Quarter cut pipe to be replaced with step | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M10B |  | OFLD-M12-0098842 | 9007C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
None | (General comment all modules) Ensure plate and bottom recess is modelled at the open drain line and overboard line in the gutter as per standard detail | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M10B |  | M10B-L1-DB1-005 | 9008C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Width of removable coaming and handling path to be aligned | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M10B |  | OFLD-M10B-0085350 | 9009C | 27/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Coaming to be arranged clearing the opening for level instrument | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M10B |  | SS-M10B-0016059 | 9010C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
None | Coaming to be modified to cover the drain valve for all PCHE drain lines | None | None | PIP | OPEN | 01/02/2026 | None |  | None | None | PIP | None | None | M07A |  | 3"-W-B3-3636-NI | 9011C |  | -25.0000000000000 |  | PB - Operation | None |  | None | None | 04/02/2026 |  |  |  |  | 04/02/2026
None | Model the coaming as marked | 27-12-25-Coaming model and drain pit missng during DR90 .Now updated as per comment | None | PIP | RE-OPEN | 26/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M-01 |  | TS-M01-STR-OUTFIT-ELEV1-COAMING | 9012C | 16/01/2026 | 1.00000000000000 | 11.0000000000000 | PB - Operation | None |  | None | None | 29/12/2025 | 30/12/2025 | 01/01/2026 | 01/01/2026 | 30/12/2025 | 29/12/2025
None | Coaming to be straight as marked (TYPICAL COMMENT) | 27-12-25-Coaming changed as straight in all location | KBR | STR | RE-OPEN | 26/12/2025 | None |  | None | None | PIP | None | NO PIPING DCN REQUIRED | M-01 |  | TS-M01-STR-OUTFIT-ELEV1-COAMING | 9013C | 28/01/2026 | 1.00000000000000 | 11.0000000000000 | PB - Operation | None |  | None | None | 29/12/2025 | 30/12/2025 | 01/01/2026 | 01/01/2026 | 30/12/2025 | 29/12/2025
None | Model the quarter cut pipe | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | TS-M01-STR-OUTFIT-ELEV1-COAMING | 9014C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Remove the half cut pipe at this location as drain gutter is available | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | OFLD-M14-0053492 | 9015C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Remove the quarter cut pipe and move the drain gutter to this location | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | OFLD-M14-0053494 | 9016C | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Extend the gutter to manual handling path | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M-15 |  | None | 9017C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Review clash with pipe support and deluge line | There is no interferance of davit opening with pipe support and with deluge line. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | BFY8 - Ok - Can be closed - 28/11/2025 | PIP | None | DCN required | M-12/13/13B | 30/11/2025 | FG-1221-N6 | 0001C |  | 1.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
1 | Update davit handling volume | Davit handling volume modelled for Fuel gas filters and duplex filters. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | BFY8 - OK - Can be closed - OP Team - 28/11/2025 | PIP | None | DCN REQUIRED | M-12/13/13B | 30/11/2025 | FT-5135001C/D FT-5133002C/D | 0002C |  | 1.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
1 | Model scaffolding box volume for accessing spectacle blind | scaffolding box volume for accessing spectacle blind is modelled | PB | HAND | CLOSE |  | Julius Orzales | 08/01/2026 | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M-12/13/13B | 08/01/2026 | ESP-51350016 ESP-51350024 | 0003C | 30/12/2025 |  | 10.0000000000000 | PB - Operation | True | 07/01/2026 | True | None |  | 01/01/2026 | 09/01/2026 | 11/01/2026 | 01/01/2026
1 | 50mm gap between piping and tundish required | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13B |  | 1&quot;-DA-B9-2413-NI 1&quot;-DA-B9-2403-NI | 0004C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Review location of panel considering valve access | Panel has been deleted (reserved for heat tracing but now confirmed there is no heat tracing requirement for this module). | KBR | ELE | CLOSE | 30/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | BFY8 - OK - Can be closed - OP Team - 28/11/2025 | PIP | None | No piping DCN required | M-13B | 30/11/2025 | FG-1221-N6 | 0005C |  | -3.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 03/12/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 03/12/2025
1 | Model the strainer volume | Strainer maintenance volume modelled. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | BFY8 - OK - Can be closed - OP Team - 28/11/2025 | PIP | None | No piping DCN required | M-12/13/13B | 30/11/2025 | FT-5135001C/D FT-5133002C/D | 0006C |  | 1.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
1 | Trays directly below strainer - ensure clearance for strainer maintenance | None | KBR | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-12/13/13B |  | ESP-51478084 IT-M13B-S-S-TRAY-01016-TRAY-0184 | 0007C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check if the space between valves is sufficient for maintenance activities and actuator removal | SDV-5135001D-2 is handled by beam clamps and SDV-5135001D-1 is handled by using hydraulic stacker | KBR | HAND | RE-OPEN |  | None |  | None | None | HAND | None | None | M-13B |  | SDV-5135001D-2 SDV-5135001D-1 | 0008C | 30/01/2026 |  | 42.0000000000000 | PB - Operation | None |  | None | None |  | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025
1 | Review modification of handrail to avoid interference considering valve removal | Guardrail has been modified to give clearance for valve removal | KBR | STR | CLOSE | 11/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | BFY8 - OK - Can be closed - OP Team - 28/11/2025 | PIP | None | No piping DCN required | M13B | 30/11/2025 | VALV-51470828 | 0009C |  | 16.0000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 14/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 16/11/2025
1 | Drain point to be added as per vendor P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | 2"-W-B10-3149-NI | 0010C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Low point drain valves to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | 4"-W-B10-0425-NI | 0011C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve lever operation too close to deluge piping | Deluge piping adjusted. 30 Dec 25: Other filters (FT-5133002A/B/C/D/E/F) have been verified with no similar issue. | KBR | PIP | Pending PB Reply | 29/12/2025 | None |  | None | Can not be closed - 28/11/2025 - Has to verify the others filters that has the same problem FT-5133002A/B/C/D/E/F | PIP | None | no piping dcn required | M13B |  | VALV-51330473 | 0012C |  | 0 | 9.00000000000000 | PB - Operation | True |  | None | None | 01/01/2026 | 01/01/2026 |  |  | 01/01/2026 | 01/01/2026
1 | Check against vendor P&ID if line can be drained through equipment | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | 2"-D-G3-0519-NI | 0013C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Provide supports for this tubing line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | 3/4"-BG-T3A-0754-NI | 0014C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Pipe supports to be modelled | Supports modelled. | KBR | PIP | CLOSE | 13/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | BFY8 - OK - Can be closed - OP Team - 28/11/2025 | PIP | None | No piping DCN required | M13B | 30/11/2025 | 2"-FW-B7-1586-NI | 0015C |  | 14.0000000000000 | 3.00000000000000 | SEA/KBR | None |  | None | None | 16/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 16/11/2025
2 | Branch bracing gussett support to be provided as per stress requirements | As per KBR Stress and support team, for hydrotest vent/drain (without any valve) gussets are not required as these are short connections with no significant weight. | KBR | PIP | Pending PB Reply | 30/11/2025 | None |  | None | None | PIP | None | DCN required | M13B |  | 3/4"-OL-B3-0191-PP | 0016C |  | 17.0000000000000 | 21.0000000000000 | PB - Operation | True |  | None | None | 03/12/2025 | 20/12/2025 |  |  | 21/12/2025 | 03/12/2025
2 | Line to be connected to line from piperack | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13B |  | 2"-SW-B23-1251-NI | 0017C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Low point drain to be added | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13B |  | 2"-SW-B23-1251-NI | 0018C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Model the access volume for the valves | Access volume modelled. | KBR | PIP | Pending Seatrium Reply | 15/12/2025 | None |  | None | None | PIP | None | None | M13B |  | VALV-51240262 VALV-51240279 VALV-51240287 VALV-51240286 | 0019C |  | 23.0000000000000 |  | PB - Operation | None |  | None | None | 18/12/2025 |  |  |  |  | 18/12/2025
3 | PTFE pad is missing from support | PTFE pads are shown. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M13B | 30/11/2025 | SP-M13B-02252 | 0020C |  | 1.00000000000000 | 3.00000000000000 | SEA/KBR | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
3 | Re-pad is missing from support. Check if u-bolt can be used. | U-bolt is modelled now which is the suitable support here. | KBR | PIP | Pending PB Reply | 30/11/2025 | None |  | None | None | PIP | None | No piping DCN required | M13B |  | SP-M13B-03054 | 0021C |  | 17.0000000000000 | 21.0000000000000 | SEA/KBR | None |  | None | None | 03/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 03/12/2025
5 | Check if the steam vent to safe location at height directly above safety route is acceptable | None | KBR | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-12/13/13B |  | 10"-HWP-B4-0970-PP | 0022C | 20/01/2026 |  |  | PB - Engineering | None |  | None | None
5 | Check if the steam vent to safe location at height directly above safety route is acceptable | None | KBR | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-12/13/13B |  | 10"-HWP-B4-0971-PP | 0023C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | Avoid loop in vent line | The piping has been modified such that there is sufficient clearance from the laydown area. | KBR | PIP | CLOSE | 13/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | BFY8 - Can be closed - OK - OP Team - 28/11/2025 | PIP | None | No piping DCN required | M13B | 30/11/2025 | 10"-HWP-B4-0971-PP | 0024C |  | 14.0000000000000 | 3.00000000000000 | SEA/KBR | None |  | None | None | 16/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 16/11/2025
4 | Review relocating of hose stand to marked column | Hose stand has been shifted closer to utiliy station. | KBR | PIP | CLOSE | 13/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | BFY8 - Can be closed - OK - OP Team - 28/11/2025 | PIP | None | No piping DCN required | M13B | 30/11/2025 | M13B-L4-US-0005-HS | 0025C |  | 14.0000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 16/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 16/11/2025
5 | Update PSVs with correct tags | Tags updated. | KBR | PIP | CLOSE | 13/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M13B | 30/11/2025 | 1&quot;-FG-E6N-0077-PP 1&quot;-FG-E6N-0031-PP | 0026C |  | 14.0000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 16/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 16/11/2025
5 | Flame arrestor to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | 12"-F-B3-1916-NI | 0027C | 25/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Flame arrestor to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | 8"-F-B3-1912-NI | 0028C | 25/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Flame arrestor to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | 12&quot;-F-B3-1917-NI 8&quot;-F-B3-1911-NI | 0029C | 25/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Gusset supports to be modeled | Gusset supports are modelled. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M13B | 30/11/2025 | 3/4&quot;-F-B10-1836-NI 3/4&quot;-F-B10-1831-NI | 0030C |  | 1.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
5 | PG and valve to be in vertical | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13B |  | 1-1/2"-W-B10-3139-NI | 0031C | 15/01/2026 |  |  | PB - Engineering | None |  | None | None
5 | PG and valve to be in vertical | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13B |  | 1-1/2"-W-B10-3145-NI | 0032C | 15/01/2026 |  |  | PB - Engineering | None |  | None | None
5 | Check drain requirement downstream of check valve | Refer to Close-out snapshot, KBR Process informs drain valve is not required. | KBR | PRO | Pending PB Reply | 13/11/2025 | None |  | None | None | PIP | None | SEA PRO(30/12/25) : Agreed. This is GTG fuel gas warm up line, and purge (from upstream) to remove any condensate formed within system. Discussion with PB (Mellisa) on 19/12/25 and confirmed that drain valve on this line is not required. | M-12/13/13B |  | 2"-F-E3N-1861-NI | 0033C |  | 46.0000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 16/11/2025 | 01/01/2026 | 03/01/2026 | 04/01/2026 | 01/01/2026 | 16/11/2025
5 | Piping is disconnected | Line is connected now. | KBR | PIP | Pending PB Reply | 26/11/2025 | None |  | None | None | PIP | None | No piping DCN required | M13B |  | 3"-FG-E6N-0006-PP | 0034C |  | 21.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 30/11/2025
1 | Escape route to be shown on M13B Safety Plan | 09/12/25 : This comment will be updated in the next revision of Safety Plan 19/12/25 ; Safety Plan will be reissued once Revised Equipment Layout and comments on the submitted Safety plan is received. | None | SAF | RE-OPEN | 18/12/2025 | None |  | None | None | SAF | None | None | M-13B |  | TS-M13B-SAFE-PPRACK-VOL | 0035C | 18/12/2025 | -9.00000000000000 | 29.0000000000000 | SEA/KBR | None |  | None | None | 21/12/2025 | 12/12/2025 | 14/12/2025 | 14/12/2025 | 14/12/2025 | 21/12/2025
1 | Typical: Level 1 extinguishers are missing supports | Supports are now provided for Lvl 1 extinguishers. | KBR | PIP | CLOSE | 13/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M-13B | 01/12/2025 | Z-5428351 | 0036C | 13/11/2025 | 14.0000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 16/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 16/11/2025
1 | Missing SCBA (breathing mask) from model | SCBA (Z-5434420) has been modelled. | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | None | M13B |  | None | 0037C |  | 17.0000000000000 |  | PB - Engineering | None |  | None | None | 24/12/2025 |  |  |  |  | 24/12/2025
1 | Missing SCBA (breathing mask) from model | SCBA (Z-5434419) has been modelled. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M13B | 01/12/2025 | None | 0038C |  | 1.00000000000000 | 4.00000000000000 | PB - Engineering | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
2 | Escape route to be shown on M13B Safety Plan | 09/12/25 : This comment will be updated in the next revision of Safety Plan 19/12/25 : Safety Plan will be reissued once Revised Equipment Layout and comments on the submitted Safety plan is received. | None | SAF | RE-OPEN | 18/12/2025 | None |  | None | None | SAF | None | None | M-13B |  | LEVEL-2-5-4524 | 0039C | 18/12/2025 | 19.0000000000000 | 1.00000000000000 | SEA/KBR | None |  | None | None | 21/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 21/12/2025
1 | Handrails are misaligned - reduce the gap between handrails to meet 75mm gap requirement | Handrails been updated to achieve 75min-120max clear gap | KBR | STR | Pending PB Reply | 02/12/2025 | None |  | None | None | STR | None | None | M13B |  | DesignedHandrail-Default-7-0916 | 0040C |  | 2.00000000000000 | 34.0000000000000 | PB - Operation | None |  | None | None | 05/12/2025 | 07/12/2025 | 09/12/2025 | 09/12/2025 | 07/12/2025 | 07/12/2025
1 | Escape route to be modelled | Escape route modelled (obstruction volume included). | KBR | PIP | Pending PB Reply | 30/11/2025 | None |  | None | None | PIP | None | None | M13B |  | P84\TS\TS-M13B\TS-M13B-SAFE\TS-M13B-SAFE-VOL\OBSTRUCTION\ESCAPE_OBST\SECONDARY\LEVEL-1 | 0041C |  | 37.0000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 03/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 03/12/2025
1 | Primary escape route to be in colour green | Escape route in green now. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | 07/01/2026 - UP56 - ok - close | SAF | None | None | M13B |  | P84\TS\TS-M13B\TS-M13B-SAFE\TS-M13B-SAFE-PPRACK-VOL\OBSTRUCTION\PRIMARY\LEVEL-1 | 0042C |  | 23.0000000000000 | 1.00000000000000 | PB - Operation | None | 07/01/2026 | True | None | 17/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 17/12/2025
1 | Access path to be moved inside platform | Access path shifted onto platform. | KBR | PIP | Pending PB Reply | 26/11/2025 | None |  | None | 07/01/2026 - UP56 - ok - close | SAF | None | None | M13B |  | LEVEL-1-5-5405 | 0043C |  | 13.0000000000000 | 29.0000000000000 | PB - Operation | None | 07/01/2026 | True | None | 29/11/2025 | 12/12/2025 | 14/12/2025 | 14/12/2025 | 14/12/2025 | 30/11/2025
2 | Stair handrail is misaligned | Gap has been closed off | KBR | STR | Pending PB Reply | 30/11/2025 | None |  | None | None | STR | None | None | M13B |  | OFSR-M13B-0000004 | 0044C |  | 2.00000000000000 | 36.0000000000000 | PB - Operation | None |  | None | None | 03/12/2025 | 05/12/2025 | 07/12/2025 | 07/12/2025 | 07/12/2025 | 03/12/2025
2 | Typical: Level 2 extinguishers are missing supports | Supports modelled for the Level 2 extinguishers. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M13B | 01/12/2025 | Z-5428356 | 0045C |  | 1.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
2 | Extinguisher location on safety plan to be updated | 09/12/25 : This comment will be updated in the next revision of Safety Plan. 19/12/25 : Safety Plan will be reissued once Revised Equipment Layout and comments on the submitted Safety plan is received. | None | SAF | RE-OPEN | 18/12/2025 | None |  | None | None | SAF | None | None | M13B |  | Z-5428359 | 0046C |  | 19.0000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 21/12/2025
2 | Typical: Level 2 Mezz extinguishers are missing supports | Supports modelled for Lvl 2 Mezz extinguishers. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M13B | 01/12/2025 | Z-5428359 | 0047C |  | 1.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
3 | Typical: Level 3 Mezz extinguishers are missing supports | Supports modelled for Lvl 3 extinguishers. | KBR | PIP | Pending PB Reply | 30/11/2025 | None |  | None | 08/01/2026 - UP56 - It was identified a clash (Z-5428360) to be resolved. The clash resolution shall be carried out as per Clash Management forum track and actions. For the punched item, closed | SAF | None | None | M13B |  | Z-5428108 | 0048C |  | 9.00000000000000 | 29.0000000000000 | PB - Operation | None | 08/01/2026 | True | None | 03/12/2025 | 12/12/2025 | 14/12/2025 | 14/12/2025 | 14/12/2025 | 03/12/2025
3 | Relocate stand away from hydrant operating volume | Instrument stand has been relocated. | KBR | CSE | CLOSE | 26/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M-13B | 01/12/2025 | SPI-M13B-301 | 0049C | 26/02/2026 | 1.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
3 | Update hydrant operating volume to front of hydrant | Hydrant volume updated to the front side. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M13B | 01/12/2025 | H-5423115 | 0050C |  | 1.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
3 | Drain pit to be flush with top of deck plate | Drain pit flush with deck plate. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M13B | 01/12/2025 | M13B-L3-DP1-001 | 0051C |  | 1.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
4 | Typical: Level 4 extinguishers are missing supports | Supports modelled for Lvl 4 extinguishers. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M13B | 01/12/2025 | Z-5428363 | 0052C |  | 1.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
5 | Typical: Level 5 extinguishers are missing supports | Supports modelled for Lvl 5 extinguishers. | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M13B | 01/12/2025 | Z-5428418 | 0053C |  | 1.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
1 | Filters should have portable step for access | Portable step included. | KBR | PIP | Pending Seatrium Reply | 14/12/2025 | None |  | None | None | PIP | None | None | M13B |  | FT-5133002-A-F | 0054C |  | 24.0000000000000 |  | PB - Operation | None |  | None | None | 17/12/2025 |  |  |  |  | 17/12/2025
1 | Motor handling volume to be modelled | Motor handling volume is modelled | KBR | HAND | Pending PB Reply |  | None |  | None | 09.01.25_B0RG_CLOSE | HAND | None | 9Jan2026_Cleared. | M-13B |  | UB-TG-5147001C-03 UB-TG-5147001D-03 | 0055C | 06/01/2026 |  | 0 | PB - Operation | True | 09/01/2026 | True | None |  | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
1 | Not possible for HE to operate during maintenance of other HE considering arrangement of removable spools and removable support | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | TG-5147001D.nwd | 0056C | 29/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Rearrange piping to minimise risk of collision considering handling path | Piping routing adjusted. 26 Dec 25: Uncessary couplings are removed. | KBR | PIP | Pending PB Reply | 25/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M13B |  | 1-1/2"-DW-B3-0001-NI | 0057C |  | 2.00000000000000 | 11.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 30/12/2025 | 01/01/2026 | 01/01/2026 | 30/12/2025 | 28/12/2025
1 | Special tool bolting arrangement to be provided if necessary | None | KBR | SEA | OPEN |  | None |  | None | None | STR | None | None | M-12/13/13B |  | MAINTENANCE A-C (08Aug2025).nwc | 0058C | 26/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Electrical trays need to be relocated to clear handling obstruction | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-12/13/13B |  | ET-M13B-L-N-TRAY-30003 ET-M13B-L-E-TRAY-30002 | 0059C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
2 | A-frame and obstruction volume to be modelled | A-frame and obstruction volume is modelled | PB | HAND | CLOSE |  | Julius Orzales | 08/01/2026 | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M-12/13/13B | 08/01/2026 | 0562501001_MONTADO_SKID_AR_DE_SELAGEM_R4:1 (TG-C/D) | 0060C | 19/12/2025 |  | 10.0000000000000 | PB - Operation | True | 07/01/2026 | True | None |  | 01/01/2026 | 09/01/2026 | 11/01/2026 | 01/01/2026
2 | Handling sling volumes to be modelled. Typical for other two trains | Handling sling volumes are modelled. | PB | HAND | CLOSE |  | Julius Orzales | 08/01/2026 | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M-13B | 08/01/2026 | B1CRRU32_105:1 (TG-C/D) | 0061C | 23/12/2025 |  | 10.0000000000000 | SEA/KBR | True | 07/01/2026 | True | None |  | 01/01/2026 | 09/01/2026 | 11/01/2026 | 01/01/2026
5 | Speaker to be relocated away from pick up/drop zone | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13B |  | COR-5518373A | 0062C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Escape routes to be shown on M05B Safety Plan | None | KBR | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05B |  | LEVEL-1-6-6060 LEVEL-1-6-6064 | 0063C |  |  |  | SEA/KBR | None |  | None | None
1 | Equipment supports to be modelled | Support modelled. | None | PIP | CLOSE | 23/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | 08-01-26; KUB7; CLOSE | PIP | None | None | M-05B | 30/11/2025 | Z-5434101 | 0064C |  | 4.00000000000000 | 3.00000000000000 | SEA/KBR | None |  | None | None | 26/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 26/11/2025
1 | Fall arrestor to be modelled on ladders more than 5m height | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-05B |  | V-UC-1225001A-01 V-UC-1225001A-02 V-UC-1225001B-01 V-UC-1225001B-02 | 0065C | 26/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Equipment support modelling to be updated | Relocated to attach from Struc. column. | None | PIP | CLOSE | 13/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | 08-01-26; KUB7; CLOSE | PIP | None | None | M-05B | 30/11/2025 | Z-5428080 | 0066C |  | 14.0000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 16/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 16/11/2025
3 | Equipment support and height to be updated | Support and elevation updated. | None | PIP | CLOSE | 13/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | 08-01-26; KUB7; CLOSE | PIP | None | None | M-05B | 30/11/2025 | Z-5434013 | 0067C |  | 14.0000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 16/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 16/11/2025
4 | Dedicated coaming to be provided for safety shower if area coaming is not available | Coaming provided. | None | PIP | CLOSE | 21/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | 08-01-26; KUB7; CLOSE | PIP | None | None | M-05B | 30/11/2025 | Z-5434341 | 0068C |  | 6.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 24/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 24/11/2025
1 | Model a volume for LIT access (where LIT does not have ladder acess). Typical for all 5 vessels. | Volume provided for all LIT. | SE | PIP | Pending Seatrium Reply | 27/11/2025 | None |  | None | 08-01-26; KUB7; CLOSE | PIP | None | None | M-05B |  | LIT-1225002 LIT-1225007A/B LIT-1225004A/B | 0069C |  | 41.0000000000000 |  | PB - Operation | None |  | None | None | 30/11/2025 |  |  |  |  | 30/11/2025
1 | Avoid pocketing the line | Pocket eliminated. | KBR | PIP | CLOSE | 06/01/2026 | Julius Orzales | 08/01/2026 | None | 07-01-26; KUB7; CLOSE | PIP | None | no piping dcn required | M-05B | 08/01/2026 | 1/2"-PC-B12N-2310-NI | 0070C |  | 0 | 2.00000000000000 | PB - Operation | True | 07/01/2026 | True | None | 09/01/2026 | 09/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
1 | Check the tapping orientation for sample connection, considering the purpose of sampling | None | KBR | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05B |  | ESP-12250160 ESP-12250169 ESP-12250154 ESP-12250159 | 0071C | 21/01/2026 |  |  | PB - Engineering | None |  | False | None
1 | Model the flare lines of the sampling point panels | Flare lines modeled. | KBR | PIP | RE-OPEN | 14/12/2025 | None |  | None | 08-01-25_KUB7_OK | PIP | None | None | M-05B |  | ESP-12250169/SC9-I1 | 0072C | 22/01/2026 | 4.00000000000000 | 20.0000000000000 | PB - Operation | None |  | None | None | 17/12/2025 | 21/12/2025 | 23/12/2025 | 23/12/2025 | 21/12/2025 | 17/12/2025
4 & 5 | Vent without valve to be flanged (typical for all vents without valves) | Updated for all vent without valve. | None | PIP | CLOSE | 19/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | 3/4&quot;-PC-B30N-0618-PP 3/4&quot;-PC-B30N-0835-PP 3/4&quot;-PC-B30N-0836-PP 3/4&quot;-PC-C30N-0735-PP 3/4&quot;-PC-C30N-0701-PP 3/4&quot;-PC-B30N-0618-PP | 0073C |  | 8.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 22/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 23/11/2025
1 | In relation to removal of the spacer, support to be made removable. Scafolding volume to be modelled. | Support removed as trunnion is not require to rest. Guide restraint attached to struc. steel. Scaffold volume modelled. | None | PIP | CLOSE | 21/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | V-UC1225001A-01 Paddle Spacer-1612 | 0074C |  | 6.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 24/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 24/11/2025
1 | TIT to be reoriented to allow access for TIT removal | TIT orientated for access. | None | PIP | CLOSE | 21/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | TIT-1225006A | 0075C |  | 6.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 24/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 24/11/2025
1 | Check orientation of PIT considering fluid is L/V | PIT re-orientate to horizontal. | None | PIP | CLOSE | 24/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | PIT-1225016A/B | 0076C |  | 3.00000000000000 | 3.00000000000000 | SEA/KBR | None |  | None | None | 27/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 27/11/2025
1 | Provide branch bracing | Brach bracing modeled. | KBR | PIP | CLOSE | 04/01/2026 | Julius Orzales | 08/01/2026 | None | 07-01-26; KUB7; CLOSE | PIP | None | no piping DCN required | M-05B | 08/01/2026 | 3/4&quot;-F-B30N-0958-NI 3/4&quot;-F-B30N-0724-NI | 0077C |  | 0 | 4.00000000000000 | PB - Operation | True | 07/01/2026 | True | None | 07/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 07/01/2026
1 | Line is not connected BG-0746 & BG-0751 | Line connected to nozzle. | PB | PIP | CLOSE | 14/12/2025 | Julius Orzales | 08/01/2026 | None | 07-01-26; KUB7; CLOSE | PIP | None | No piping DCN required | M-05B | 08/01/2026 | 3&quot;-F-B3-1616-NI BG-0746 BG-0751 | 0078C |  | 4.00000000000000 | 21.0000000000000 | PB - Operation | True | 07/01/2026 | True | None | 17/12/2025 | 21/12/2025 | 09/01/2026 | 11/01/2026 | 21/12/2025 | 17/12/2025
1 | Valve lever to be reoriented | Lever re-orientated. | None | PIP | CLOSE | 21/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | VALV-12250776 | 0079C |  | 6.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 24/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 24/11/2025
3 | Model valve as PV-1225021 instead of manual valve | Model updated as inst. valve PV-1225021A. | None | PIP | CLOSE | 18/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | PV-1225021 | 0080C |  | 9.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 21/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 23/11/2025
1 | Update to u-bolt as per other vessels | Pipe issued. DCN-P84P85-S2N-TOP-M05B-PIP-KBR-SFB-0007 raised. Model updated. | None | PIP | CLOSE | 26/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | DCN required | M-05B | 30/11/2025 | 3"-PC-B12N-0710-NI | 0081C |  | 1.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
1 | Rectify duplicate support tag | Duplicate support tag rectified. | PB | PIP | CLOSE | 09/12/2025 | Julius Orzales | 08/01/2026 | None | 07-01-26; KUB7; CLOSE | PIP | None | No piping DCN required | M-05B | 08/01/2026 | SP-M05B-48041 SP-M05B-48079 SP-M05B-48232 SP-M05B-48160 SP-M05B-48211 SP-M05B-48136 SP-M05B-49987 SP-M05B-50032 SP-M05B-48052 | 0082C |  | 8.00000000000000 | 22.0000000000000 | SEA/KBR | True | 07/01/2026 | True | None | 12/12/2025 | 20/12/2025 | 09/01/2026 | 11/01/2026 | 21/12/2025 | 14/12/2025
1 | Model the lines IA-1040 and 1041. Typical for Train B | Connecting lines modeled. | KBR | PIP | RE-OPEN | 08/12/2025 | None |  | None | None | PIP | None | None | M-05B |  | IA-1040 IA-1041 | 0083C | 25/01/2026 | 9.00000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 11/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 11/12/2025
1 | Design of lube oil filling line (open end connection and slope) to be aligned with operations requirements, as current design is not practical considering contamination possibility. Typical for Train B | PUN -1644 raise to update PID. Slope provided and funnel end connection with blind. | None | PIP | CLOSE | 27/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | 4"-OL-B3-0104-NI | 0084C |  | 0 | 3.00000000000000 | PB - Operation | None |  | None | None | 30/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
1 | Coaming to be updated | Coaming updated | PB | STR | Pending PB Reply | 25/12/2025 | None |  | None | None | STR | None | None | M-05B |  | OFLD-M05B-0088638 | 0085C | 29/12/2025 | 3.00000000000000 | 8.00000000000000 | None | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Y-Strainer mesh requirement to be confirmed | Mesh requirement as shown in snapshot. | None | PIP | CLOSE | 23/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | 4"-OL-B3-0104-NI | 0086C |  | 4.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 26/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 26/11/2025
1 | Line F-1616 to be reconnected | Line F-1616 & F-1791 connected. | PB | PIP | CLOSE | 30/11/2025 | Julius Orzales | 08/01/2026 | None | 07-01-26; KUB7; CLOSE | PIP | None | No piping DCN required | M-05B | 08/01/2026 | 3"-F-B3-1616-NI | 0087C |  | 17.0000000000000 | 22.0000000000000 | PB - Operation | True | 07/01/2026 | True | None | 03/12/2025 | 20/12/2025 | 09/01/2026 | 11/01/2026 | 21/12/2025 | 03/12/2025
1 | Avoid pocketing the line | Model updated. | None | PIP | CLOSE | 24/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | 1-1/2"-PW-B3-0265-NI | 0088C |  | 3.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 27/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 27/11/2025
2 | Piping and nozzle not aligned - vendor to provide updated stp file. | TP location match Vendor GA. Pipe connected. | None | PIP | CLOSE | 24/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | V-UC-1225001A/B-03.nwd | 0089C |  | 3.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 27/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 27/11/2025
2 | Update as per PUN-1506 | Model updated. | None | PIP | CLOSE | 18/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | SDV-1225022 Drain valve-VALV-12250757 | 0090C |  | 9.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 21/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 23/11/2025
2 | Drain valves to be modeled | Drain valves modeled. | None | PIP | CLOSE | 20/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | VALV-12250409 VALV-12250410 | 0091C |  | 7.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 23/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 23/11/2025
2 | FIT tappings to be modeled | FIT tappings modeled for both FE-1225025A &B | PB | PIP | CLOSE | 04/12/2025 | Julius Orzales | 08/01/2026 | None | 07-01-26; KUB7; CLOSE | PIP | None | No piping DCN required | M-05B | 08/01/2026 | FE-1225028A/B | 0092C |  | 13.0000000000000 | 22.0000000000000 | PB - Operation | True | 07/01/2026 | True | None | 07/12/2025 | 20/12/2025 | 09/01/2026 | 11/01/2026 | 21/12/2025 | 07/12/2025
2 | Model sampling connection | Sampling line connected. | KBR | PIP | RE-OPEN | 08/12/2025 | None |  | None | None | PIP | None | None | M-05B |  | 1/2"-PC-B12N-2557-N | 0093C | 26/01/2026 | 9.00000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 11/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 11/12/2025
2 | Review location of SDV considering high point requirement (P&ID note 54) | None | KBR | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05B |  | SDV-1225005A | 0094C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Lines to be update to include bolts modelling | Bolts updated. | None | PIP | CLOSE | 26/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | PC-0617 PC-0704 PC-0740 | 0095C |  | 1.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 29/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 30/11/2025
2 | Temporary access platform to be under correct model hierarchy/naming | None | KBR | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-05B |  | PN-UC-1225001A-B-ACP | 0096C | 27/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Reselect penetration as plate pen | Penetration updated. | None | PIP | CLOSE | 20/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05B | 30/11/2025 | PD-M05B-L3-47816 PD-M05B-L3-55400 PD-M05B-L3-55421 PD-M05B-L3-47826 | 0097C |  | 7.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 23/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 23/11/2025
5 | Update catalogue to show TIT connection | Model updated. | PB | PIP | CLOSE | 09/12/2025 | Julius Orzales | 08/01/2026 | None | 08-01-26; KUB7; CLOSE | PIP | None | No piping DCN required | M-05B | 08/01/2026 | XSE-1225868A XSE-1225868B XSE-1225800A XSE-1225800B | 0098C |  | 8.00000000000000 | 22.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 12/12/2025 | 20/12/2025 | 10/01/2026 | 11/01/2026 | 21/12/2025 | 14/12/2025
1 | Evaluate material handling path width to avoid dismantling both removable platform for one side handling | Width of the Materil Handling volume reduced to 1800mm. Clash with STR hasbeen resolved. 07Jan26- Largest Item width to be handled is 1560mm VRU Compressor | KBR | HAND | Pending PB Reply | 06/01/2026 | None |  | None | 09.01.25_B0RG_CLOSE | HAND | None | 9Jan2026_Cleared. | M-05B |  | None | 0099C | 09/01/2026 | 2.00000000000000 | 0 | PB - Operation | True | 09/01/2026 | True | None | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
1 | Drain piping to be rerouted to clear interference with handling route | Pipe modified away from handling route. | None | PIP | CLOSE | 18/11/2025 | PIPER | 30/11/2025 | Agreed between PB Operation, Piping, and SEATRIUM | 28/11/25 - BFY8 - OK - Can be closed - OP Team | PIP | None | No piping DCN required | M-05B | 30/11/2025 | 3"-DA-B9-3274-NI | 0100C |  | 9.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 21/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 23/11/2025
1 | Tubing to be rerouted to avoid handling area | None | KBR | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-05B |  | T-01-C-UC-1225001B-01 | 0101C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Gear box handling volume on monorail to be modeled | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05B |  | MR-M05B-1004-10MT | 0102C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Extend laydown handling volume and ensure it clear of interference | Dropzone volume updated, Fire and Safety to relocate Push button Alarm Stand 24-Dec-25: Push button cleared from PICKUP AND DROP AREA. Refer to close-out snapshot 2. | SE | PIP | Pending PB Reply | 23/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | None | M-05B |  | PICKUP AND DROP AREA | 0103C | 23/12/2025 | 14.0000000000000 | 2.00000000000000 | PB - Operation | True | 07/01/2026 | True | None | 26/12/2025 | 09/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 28/12/2025
1 | Instrument support post to be relocated away from handling route. Handling route to be modelled. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05B |  | HSS-M05B-101-E003 | 0104C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Move electrical panel toward aft central between bumper columns | Laydown Area Socket set moved towards AFT side between bumper columns. | PB | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-05B |  | SPS-M05B-001 BM-U102x10.8-of V01 | 0105C |  | 19.0000000000000 | 19.0000000000000 | PB - Operation | True |  | None | None | 03/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 03/12/2025
2 | Model the turning radius | Turning Radius modelled at the marked location | PB | HAND | Pending PB Reply | 11/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M-05B |  | L2/HW/SWL-10MT | 0106C | 09/01/2026 | 18.0000000000000 | 10.0000000000000 | PB - Operation | True | 07/01/2026 | True | None | 14/12/2025 | 01/01/2026 | 09/01/2026 | 11/01/2026 | 01/01/2026 | 14/12/2025
2 | Lifting beam to be centred on valve | Lifting Beam matched with centre of the Valve | PB | HAND | Pending PB Reply |  | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 29Dec2025_Cleared. | M-05B |  | OFBM-M05B-2001-3MT | 0107C | 09/01/2026 |  | 11.0000000000000 | SEA/KBR | True | 07/01/2026 | True | None |  | 31/12/2025 | 09/01/2026 | 11/01/2026 | 31/12/2025
3 | Check the handling method (stacker) for the valve and confirm the width & height of the handling path | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05B |  | VALV-12250266 | 0108C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Fire hydrant operating volume should be clear of obstructions on both sides | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M16 |  | H-5423137 | 0109C | 01/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment support location to be relocated to correct position | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M16 |  | Z-5428402 | 0110C | 02/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment support orientation to be updated | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M16 |  | Z-5428403 | 0111C | 03/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment cannot be mounted on gutter - wall mounted support to be considered | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M16 |  | Z-5428404 | 0112C | 04/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Escape routes to be shown on M16 Safety Plan | 8 Jan 2026: The escape route as pe the rev A Safety plan Level 1 is consistent with the 3D model. | None | SAF | Pending Seatrium Reply | 07/01/2026 | None |  | None | None | SAF | None | None | M16 |  | LEVEL-1-5-5241 | 0113C |  | 0 |  | PB - Operation | None |  | None | None | 10/01/2026 |  |  |  |  | 11/01/2026
4 | Equipment should not be located inside handling area. Equipment support to be modelled. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M16 |  | Z-5428405 Z-5428411 Z-5428412 | 0114C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Handrail to be extended as per standard detail (typical punch) | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M16 |  | None | 0115C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Coaming to be updated as marked | Coaming updated | KBR | STR | Pending PB Reply | 28/12/2025 | None |  | None | None | STR | None | None | M16 |  | None | 0116C | 22/01/2026 | 2.00000000000000 | 8.00000000000000 | PB - Operation | None |  | None | None | 31/12/2025 | 02/01/2026 | 04/01/2026 | 04/01/2026 | 04/01/2026 | 31/12/2025
1 | Utility station support to be modifed to provide more access around WW line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M16 |  | M16-L1-US-0001 3&quot;-WW-B3-5158-NI | 0117C | 26/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Line to be relocated due to risk of collision during lifting operations (previously punched during DR60) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M16 |  | 4"-DW-B3-0024-NI | 0118C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Line is missing from model | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M16 |  | 3/4"-D-B3-0401-NI | 0119C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Isolation valve is missing from end of line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M16 |  | 4"-W-B10-3179-NI | 0120C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Utility station line routing to be completed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M16 |  | M16-L6-US-0001 | 0121C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Handling sequence for hatch cover to be provided. Wood arrangement on hatch cover to be finalised. Consider having the wood directly secured to the hatch cover and liftable together with hatch. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M16 |  | TS-M16-STR-FLPLTE-ELEV1 | 0122C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Lighting fixtures to be relocated behind structure away from lifting area | LIght fixture relocated away from lifting area | None | ELE | RE-OPEN | 18/12/2025 | None |  | None | None | ELE | None | None | M16 |  | LNO-224-26-M16-001 LNO-224-26-M16-002 LEM-351-10-M16-003 | 0123C |  | 10.0000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 21/12/2025
1 | Cable trays to be relocated away from lifting area | None | KBR | ELE | OPEN |  | None |  | None | None | ELE | None | None | M16 |  | ET-M16-L-N-TRAY-10002 IT-M16-S-S-TRAY-01001 | 0124C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Relocate junction box and cable tray to Aft side of column away from lifting area | Junction box Relocated away from lifting area | None | ELE | Pending PB Reply | 18/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 29Dec2025_Cleared. | M16 |  | CXN-L-M16-003 EC-M16-L-E-TRAY-40505 | 0125C |  | 10.0000000000000 | 11.0000000000000 | PB - Operation | True | 07/01/2026 | True | None | 21/12/2025 | 31/12/2025 | 09/01/2026 | 11/01/2026 | 31/12/2025 | 21/12/2025
4 | Lighting fixture to be relocated away from lifting area | None | KBR | ELE | OPEN |  | None |  | None | None | ELE | None | None | M16 |  | LNO-224-27-M16-003 | 0126C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Flare line to be relocated away from lifting area | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M16 |  | 4"-F-B3N-1060-NI | 0127C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Polyamide bar to be provided at top of steel section at boom rest | Polymide bar provided | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | STR | None | None | M16 |  | None | 0128C | 23/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
3 | Pulling post to be located correctly inside module. Detailed pulling post modelling to be done. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05B |  | PP-M05B-3003-10MT PP-M05B-3004-10MT | 0129C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Lifting point of davit to be positioned at centre of hatch. Davit to be positioned so that it can lift the hatch and place on the deck. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05B |  | PORTABLE DAVIT-1MT | 0130C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | General comment - lifting beams to be modelled under correct hierarchy | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05B |  | None | 0131C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Tubing and penetrations to be relocated away from actuator handling space | None | KBR | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-05B |  | XV-1225021A | 0132C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Equipment to be relocated away from drop zone | None | KBR | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-05B |  | COR-5518083A Z-5434014 Z-5428083 | 0133C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Speaker to be relocated away from drop zone | Speaker is relocated from drop zone as per screenshot | SE | TEL | Pending PB Reply | 01/01/2026 | None |  | None | None | TEL | None | None | M-05B |  | COR-5518507B | 0134C | 28/01/2026 | 3.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
Level 1 | The CCTV camera height shall be maintained at 3 meters for better visibility and rotate the camera by 90° to ensure visibility between the two GTGs. | The CCTV camera height has been maintained at 3 meters, and the camera has been rotated by 90° as per given comment. | KBR | TEL | Pending PB Reply | 01/01/2026 | None |  | None | None | TEL | None | None | M13B |  | CCD-55104016 | 10001C | 28/01/2026 | 3.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
Level 2 | PAGA Height to be maintained as 2.2 to 2.5 metres | Speakers have been relocated as per comment. | PB | TEL | Pending PB Reply | 23/12/2025 | None |  | None | None | TEL | None | None | M13B |  | COR-5518364A COR-5518801A COR-5518801B | 10002C |  | 12.0000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 26/12/2025 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 28/12/2025
None | Relocate the item to provide adequate access for cable tray support welding. | Extinguisher has been shifted. | KBR | PIP | Pending PB Reply | 23/12/2025 | None |  | None | None | PIP | None | None | M13B |  | Z-5428436 | 10003C |  | 14.0000000000000 | 1.00000000000000 | SEA/KBR | None |  | None | None | 26/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 28/12/2025
None | Cable tray requires a 90° bend to improve cable routing and ensure smoother cable bending and to tie the cables. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13B |  | TT-M13B-L-E-TRAY-10009 TT-M13B-S-B-TRAY-00007 | 10004C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the item to facilitate cable termination on both sides of the beacon. | LSE has been relocated as per comment | KBR | TEL | Pending PB Reply | 01/01/2026 | None |  | None | None | TEL | None | None | M13B |  | LSE-5518054B | 10005C | 28/01/2026 | 4.00000000000000 | 2.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 04/01/2026
None | Relocate the speaker as per mark up in screenshot | The speaker was relocated as per the markup shown in the screenshot | PB | TEL | Pending PB Reply | 23/12/2025 | None |  | None | None | TEL | None | 05-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M13B |  | COR-5518365A | 10006C |  | 12.0000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 26/12/2025 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 28/12/2025
None | Relocate the speaker as per mark up in screenshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13B |  | COR-5518367B | 10007C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the speaker to inside the platform | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13B |  | SPP-M13B-00060 | 10008C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Provide a cable tray to support each individual JB cables. Verify all JB cable gland positions to ensure sufficient spacing between glands for proper cable securing and tightening. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13B |  | IT-M13B-S-I-TRAY-02002 | 10009C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Typical | When two or more JBs are connected through a single cable tray, additional cable tray length/support shall be provided to properly secure the cables. Applicable for all JBs. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13B |  | General | 10010C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Relocate the cable trays. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13B |  | IT-M13B-S-S-TRAY-01007-TRAY-0024 IT-M13B-S-I-TRAY-01005 | 10011C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | The distance between MCT should be 100mm. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13B |  | I-M13B-S-MCT-001 I-M13B-S-MCT-002 I-M13B-S-MCT-003 I-M13B-S-MCT-004 | 10012C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | To provide support for cable trays. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13B |  | IT-M13B-S-I-TRAY-00004 IT-M13B-S-S-TRAY-00004 IT-M13B-S-S-TRAY-00004 | 10013C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate the cable trays. | 02-JAN-26 KBR COMMENT: Tray relocated and clash resolved. | KBR | CSE | Pending Seatrium Reply | 01/01/2026 | None |  | None | None | INST | None | None | M-13B |  | IC-M13B-S-I-01032 | 10014C | 29/01/2026 | 6.00000000000000 |  | SEA/KBR | None |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
Level 1 | Extend the cable tray near to the valve and termination point | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-13B |  | IC-M13B-S-I-01009 | 10015C | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Cable tray to be extended to reduce the gap between the two cable trays | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-13B |  | IC-M13B-S-I-01012 | 10016C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Relocate the instrument to resolve piping clash | 03-JAN-26 KBR COMMENT: Instruments relocated and clash resolved. Instruments kept at 900mm elevation to ensure instruments are not blocking access to Lighting JB which located above the instruments. | KBR | CSE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | INST | None | None | M-13B |  | LIT-5135001D LIT-5135002D LIT-5135004D | 10017C | 29/01/2026 | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
Level 1 | Relocate the instrument to resolve piping clash and to maintain 1.5 metres height | 03-JAN-26 KBR COMMENT: Instruments relocated and placed at 1.5M elevation. | KBR | CSE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | INST | None | None | M-13B |  | LIT-5135001C LIT-5135002C LIT-5135004C | 10018C | 29/01/2026 | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Relocate the PIT blocking the beacon | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-13B |  | PIT-5147018D | 10019C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Instrument to be relocated and re-orientated inside the platform | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-13B |  | PDIT-5135002D SPI-M13B-154 | 10020C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Tubing need to be modelled from valve to volume tank. Vessel and BDV tag number to be updated. | 02-JAN-26 KBR COMMENT: Tubing modelled from valve to volume tank and volume tanks are renamed as per BDV. | KBR | CSE | Pending Seatrium Reply | 01/01/2026 | None |  | None | None | INST | None | None | M-13B |  | BDV-5147005C/D | 10021C | 29/01/2026 | 6.00000000000000 |  | PB - Operation | None |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
None | Update the deck penetration spacing as per structure guideline and standard | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-13B |  | I-M13B-S-PEN-202 I-M13B-S-PEN-203 I-M13B-S-PEN-205 I-M13B-S-PEN-206 I-M13B-S-PEN-208 I-M13B-S-PEN-209 I-M13B-S-PEN-210 I-M13B-S-PEN-217 I-M13B-S-PEN-216 I-M13B-S-PEN-301 I-M13B-S-PEN-302 I-M13B-S-PEN-303 I-M13B-S-PEN-401 I-M13B-S-PEN-402 | 10022C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Relocate the BLE | BLE is moved as per mark up | SE | TEL | Pending PB Reply | 01/01/2026 | None |  | None | None | TEL | None | None | M-05B |  | BLE-5511082 | 10023C | 28/01/2026 | 3.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
None | Relocate the BLE to the best coverage area | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05B |  | BLE-5511083 | 10024C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Move the frame away from the piping. | Frame is moved from piping as per markup | SE | TEL | Pending PB Reply | 01/01/2026 | None |  | None | None | TEL | None | None | M-05B |  | SPP-M05B-00002 | 10025C | 28/01/2026 | 3.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
None | Relocate the speaker for better accessibility. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05B |  | COR-5518075A | 10026C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the speaker. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05B |  | COR-5518076A | 10027C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the access point for better position. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05B |  | PA-5517010 | 10028C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Relocate the BLE support inside the platform. | BLE support is moved inside the Platform as per markup | SE | TEL | Pending PB Reply | 01/01/2026 | None |  | None | None | TEL | None | None | M-05B |  | SPP-M05B-00062 | 10029C | 28/01/2026 | 3.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
None | Raise lighting height. | LIght fixture Re located to have better clearance from telecom item | PB | ELE | CLOSE | 18/12/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG - close | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-05B | 08/01/2026 | SPL-M05B-00302 | 10030C |  | 4.00000000000000 | 17.0000000000000 | PB - Engineering | True | 07/01/2026 | True | None | 21/12/2025 | 25/12/2025 | 09/01/2026 | 11/01/2026 | 25/12/2025 | 21/12/2025
None | Relocate the speaker | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05B |  | COR-5518082A | 10031C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the speaker support inside the platform. | Moved the speaker support inside the Platform | SE | TEL | Pending PB Reply | 01/01/2026 | None |  | None | None | TEL | None | None | M-05B |  | SPP-M05B-00042 | 10032C | 28/01/2026 | 3.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
None | Relocate lighting support inside the platform. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05B |  | SPL-M05B-00332 | 10033C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
None | TEL and ELE to swap location of CXE-L-M05B-318 & PA-5517011. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05B |  | PA-5517011 CXE-L-M05B-318 | 10034C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the speaker support inside the platform. | Moved the speaker support inside the Platform as per markup | SE | TEL | Pending PB Reply | 01/01/2026 | None |  | None | None | TEL | None | None | M-05B |  | SPP-M05B-00056 | 10035C | 28/01/2026 | 3.00000000000000 | 3.00000000000000 | SEA/KBR | None |  | None | None | 04/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
None | Relocate the speaker support inside the platform. | Moved the speaker inside the platform as per markup | SE | TEL | Pending PB Reply | 01/01/2026 | None |  | None | None | TEL | None | None | M-05B |  | SPP-M05B-00069 | 10036C | 28/01/2026 | 3.00000000000000 | 3.00000000000000 | SEA/KBR | None |  | None | None | 04/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
None | Penetration to be move north to avoid the bolt and nut installation. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | None | 10037C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | All JBs need vertical dropper. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | JBIF-1415-212 | 10038C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Add necessary vertical dropper tray or move the horizontal trays. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | JBC-1415-205 JBC-1415-908 IT-M05B-S-I-TRAY-03006-TRAY-0002 | 10039C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Horizontal tray extend up to JB frame end and vertical dropper without bend extend up to horizontal tray and keep the distance between 150mm. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | JBIF-1415-215 | 10040C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Electrical tray to check with vendor if it is bottom entry or side entry and extend up to JB. | None | KBR | ELE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | IT-M05B-S-I-TRAY-03006 | 10041C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
None | Elevate cable tray towards upside main. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | IC-M05B-S-I-TRAY-01021-TRAY-0005 | 10042C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
None | Tray to be moved centrally | Cable tray has been moved centre of the Vendor interface. | SE | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 10-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-13B |  | ET-M13B-L-E-TRAY-10009 | 10043C |  | 16.0000000000000 | -1.00000000000000 | SEA/KBR | None |  | None | None | 27/12/2025 | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026 | 28/12/2025
None | Ensure the cables and the tie in not obstructed by the cable tray support. | Cable tray support is updated and provided space for cable Tie-in vendor interface. | SE | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 10-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-13B |  | EC-M13B-L-E-TRAY-01015 | 10044C |  | 16.0000000000000 | -1.00000000000000 | SEA/KBR | None |  | None | None | 27/12/2025 | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026 | 28/12/2025
None | To provide common deck penetration. | Electrical and Instrument combined deck penetration is updated. | SE | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 10-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) NOTE: KBR TO ENSURE THIS TYPE OF PENETRATION DETAIL SHOULD BE INCORPORATED INTO TYPICAL DRAWING AND STRUCTURAL GUIDELINE. | M-13B |  | E-M13B-L-PEN-015 | 10045C |  | 16.0000000000000 | 0 | SEA/KBR | None |  | None | None | 27/12/2025 | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026 | 28/12/2025
None | Ensure the cables transition with no issues from the topside cable to the vendor cable tray. | Cable tray modified to have better transition from the topside cable to the vendor cable tray. | PB | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 10-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) NOTE: KBR TO ENSURE THIS TYPE OF PENETRATION DETAIL SHOULD BE INCORPORATED INTO TYPICAL DRAWING AND STRUCTURAL GUIDELINE. | M-13B |  | EC-M13B-L-N-TRAY-10036 | 10046C |  | 16.0000000000000 | 0 | PB - Engineering | None |  | None | None | 27/12/2025 | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026 | 28/12/2025
None | Cable tray part number should show part number of tray with cover. | Cable tray updated with cover part number | PB | ELE | Pending PB Reply | 05/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: KBR TO ENSURE TO HAVE WELDING ACCESS IN BETWEEN THE MCT (E-M13B-H-MCT-001) and CABLE LADDER SUPPORT (ESPT-M13B-05019). | M-13B |  | ET-M13B-H-TRAY-05004 | 10047C |  | 15.0000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 08/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 08/12/2025
None | MCT and cable tray support to ensure constructibility space. | Cable tray support is moved towards downside and provided space for MCT constructability. | SE | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 10-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13B |  | E-M13B-H-MCT-001 | 10048C |  | 16.0000000000000 | 0 | SEA/KBR | None |  | None | None | 27/12/2025 | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026 | 28/12/2025
None | To update the cable model and the cable entry to show the actual cable spreadout from cable up to the terminal box. To check and confirm the cable entry and arrangement of 1C HV cables to turbogen phase terminal box. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-13B |  | ET-M13B-H-TRAY-05004 | 10049C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
None | Cable tray tie-in to shorten the gap to vendor tray and ensure proper tray support is placed. | Awaiting info from Vendor BH | SE | MECH | OPEN |  | None |  | None | None | ELE | None | None | M13B |  | EC-M13B-L-N-TRAY-10035 | 10050C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Vendor tray to be shown, request vendor to update the stp file (GTG vendor). JB-18, JB-19, JB-20. | Awaiting info from Vendor BH | SE | MECH | OPEN |  | None |  | None | None | ELE | None | None | M13B |  | EC-M13B-L-E-TRAY-01504 | 10051C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | The support to be provided by vendor. | Awaiting info from Vendor BH | SE | MECH | OPEN |  | None |  | None | None | ELE | None | None | M13B |  | EC-M13B-L-E-TRAY-10011 | 10052C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | Vendor STP model (GTG vendor) to be updated to show the cable trays. | Vendor STP model is updated and provided cable tray | PB | ELE | CLOSE | 11/12/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG-close | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13B | 08/01/2026 | EC-M13B-L-N-TRAY-10002 | 10053C |  | 9.00000000000000 | 19.0000000000000 | PB - Operation | True | 07/01/2026 | True | None | 14/12/2025 | 23/12/2025 | 09/01/2026 | 11/01/2026 | 23/12/2025 | 14/12/2025
None | Vendor cable to be extended closer to the topside cable tray model. | Awaiting info from Vendor BH | SE | MECH | OPEN |  | None |  | None | None | ELE | None | None | M13B |  | EC-M13B-L-E-TRAY-10573 | 10054C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the two JBs away from the space in front of the sockets. | The mentioned two JB's are relocated to adjacent Column. | PB | ELE | RE-OPEN | 05/12/2025 | None |  | None | None | ELE | None | None | M-13B |  | CXN-L-M13B-008 CXN-L-M13B-015 | 10055C |  | 15.0000000000000 | 18.0000000000000 | PB - Operation | None |  | None | None | 08/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 08/12/2025
None | Review the location of the LED lighting support to be moved inside the handrail and ensure accessibility of equipment. | Light fixture location updated. (Moved from Handrail to Platform) | PB | ELE | CLOSE | 30/11/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG -close | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13B | 08/01/2026 | LEM-349-06-M13B-001 | 10056C |  | 20.0000000000000 | 19.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 03/12/2025 | 23/12/2025 | 10/01/2026 | 11/01/2026 | 23/12/2025 | 03/12/2025
None | Relocate the lighting pole support inside the handrail. | Light fixture location updated. (Moved from Handrail to Platform) | PB | ELE | CLOSE | 30/11/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG -close | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13B | 08/01/2026 | LEM-348-08-M13B-002 | 10057C |  | 20.0000000000000 | 19.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 03/12/2025 | 23/12/2025 | 10/01/2026 | 11/01/2026 | 23/12/2025 | 03/12/2025
None | Move the lighting pole to area behind the shower and still near to the handrail. | The lighting pole adjusted inside the handrail as discussed with Piping. | PB | ELE | CLOSE | 05/12/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG -close | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13B | 08/01/2026 | LEM-349-08-M13B-002 | 10058C |  | 15.0000000000000 | 19.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 08/12/2025 | 23/12/2025 | 10/01/2026 | 11/01/2026 | 23/12/2025 | 08/12/2025
None | Adjust the location of this flood light and tis support to ensure the accessbility of the JB is not obstructed by the small bore pipe. | Light fixture location updated. | PB | ELE | CLOSE | 30/11/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG -close | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13B | 08/01/2026 | LES-711-XS-M13B-007 | 10059C |  | 20.0000000000000 | 19.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 03/12/2025 | 23/12/2025 | 10/01/2026 | 11/01/2026 | 23/12/2025 | 03/12/2025
None | Lighting will be attached to the pipe support. | Light fixture moved to pipe support. | PB | ELE | CLOSE | 30/11/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG -close | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-13B | 08/01/2026 | LMO-224-10-M13B-002 | 10060C |  | 20.0000000000000 | 19.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 03/12/2025 | 23/12/2025 | 10/01/2026 | 11/01/2026 | 23/12/2025 | 03/12/2025
None | Vendor tray to align with the KBR proposed tie-in location. | Awaiting info from Vendor Everllence | SE | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05B |  | EC-M05B-L-N-TRAY-10009 | 10061C | 22/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Instrument tray to confirm tie in to the vendor package and update the model. | None | KBR | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-05B |  | IT-M05B-S-I-TRAY-01002 | 10062C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
None | To add channel tray between JB and nearby cable tray. | channel tray and support is updated. | PB | ELE | CLOSE | 30/11/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG -close | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-05B | 08/01/2026 | CXN-L-M05B-451 | 10063C |  | 19.0000000000000 | 20.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 03/12/2025 | 22/12/2025 | 10/01/2026 | 11/01/2026 | 22/12/2025 | 03/12/2025
None | Relocate light to inside the module. | light relocated to inside the module. | PB | ELE | CLOSE | 18/12/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG -close | ELE | None | 23-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-05B | 08/01/2026 | LEM-324-05-M05B-004 | 10064C |  | 4.00000000000000 | 17.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 21/12/2025 | 25/12/2025 | 10/01/2026 | 11/01/2026 | 25/12/2025 | 21/12/2025
None | Relocate the lighting fixture to remove clash. | Lighting fixture relocated to avoid the clash. | PB | ELE | CLOSE | 18/12/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG -close | ELE | None | 23-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-05B | 08/01/2026 | LEM-325-04-M05B-003 | 10065C |  | 4.00000000000000 | 17.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 21/12/2025 | 25/12/2025 | 10/01/2026 | 11/01/2026 | 25/12/2025 | 21/12/2025
None | Adjust the cable tray volume away from fire hydrant. | None | KBR | TEL | OPEN |  | None |  | None | None | ELE | None | None | M16 |  | CDI-5518020A TT-M16-S-A-TRAY-00003 | 10066C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
None | Secondary trays are missing for Telecom equipment. General for M16. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M16 |  | General | 10067C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Secondary trays are missing for Telecom equipment. General for M13B. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13B |  | General | 10068C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Secondary trays are missing for Telecom equipment. General for M05B. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05B |  | General | 10069C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Cable tray to be align with JB frame and vertically bend and connect to the MCT. Remove the support and support to be taken from JB Frame. | None | KBR | CSE | OPEN |  | None |  | None | None | TEL | None | None | M16 |  | None | 10070C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | JB to relocate to the best location of FGS stand as per the CBD. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M16 |  | TS-M16-AUTO-INST | 10071C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | The two GTG instrument interfaces to the vendor skid are not aligned. KBR to review and confirm the total number of required interfaces, ensuring all areas are aligned with the vendor’s interface points. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13B |  | None | 10072C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | KBR confirmed the pressure gauge is not required. This need to be removed from the 3D Model. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | PG-1225001 | 10073C | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Re-route the sub-cable tray to avoid running through the Material Handling Volume and maintain adequate clearance from the vertical ladder as per safety and accessibility requirements. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | None | 10074C | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Change the instrument to column mount. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | PDIT-1225020B PIT-1225007B | 10075C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Lower the cable tray below the JB to facilitate bottom entry for cables. Ensure that all sub-cable trays are properly terminated and connected to the bottom of each JB. All lighting fixtures shall be connected using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all lights and JB within Module M05B. | cable tray lowered to have better clerance with JB Cable trays are routed with proper fitting wherever is feasible | KBR | ELE | RE-OPEN | 18/12/2025 | None |  | None | None | ELE | None | None | M-05B |  | CXE-L-M05B-213 LES-299-07-M05B-001 (General for all lighting) | 10076C |  | 4.00000000000000 | 16.0000000000000 | SEA/KBR | None |  | None | None | 21/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 21/12/2025
None | Relocate floodlight to a location with no obstructing pipe. | Flood light fixture relocated in other area to avoid pipe obstrcution | PB | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: CABLE TRAY FOR LIGHTING MUST BE PROPERLY CONNECTED/MODELLED UNTIL THE CABLE TERMINATION. | M-05B |  | LNO-212-13-M05B-002 | 10077C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
None | Relocate instrument away from front side of light fitting. | None | KBR | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-05B |  | PIT-1225004B | 10078C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate JB to an accessible location at the same structural column. | JB relocated to have better access | PB | ELE | CLOSE | 18/12/2025 | Julius Orzales | 08/01/2026 | None | 08-01-2025-RTWG -close | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: JB CABLE TRAYS MUST BE PROPERLY MODEL/CONNECTED UNTIL THE JB CABLE ENTRY (BOTTOM). (DR90 GENERAL COMMENT) | M-05B | 08/01/2026 | CXN-L-M05B-033 | 10079C |  | 4.00000000000000 | 17.0000000000000 | SEA/KBR | True | 08/01/2026 | True | None | 21/12/2025 | 25/12/2025 | 10/01/2026 | 11/01/2026 | 25/12/2025 | 21/12/2025
None | Deck penetration and lighting pole location to bring closer and shorten the current existing gap. | Penetration relocated closer to lighting pole | KBR | ELE | RE-OPEN | 18/12/2025 | None |  | None | None | ELE | None | None | M-05B |  | LES-299-07-M05B-003 | 10080C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 21/12/2025
None | As per PB and SEA advice, move the flood light to the pipe support | Floods are relocated and attached with Pipe supports | PB | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: KBR ELEC TO ENSURE TO MODEL AND CONNECT THE CABLE TRAYS (SUB TRAYS FOR LIGHTING/JB) PROPERPLY FROM MAIN TRAY TO CABLE TERMINATION POINT. | M-05B |  | LNO-212-17-M05B-001 | 10081C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
None | Adjust location of PDA to provide access space for light fixture. | None | KBR | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-05B |  | PDA-M05B-E-006 | 10082C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Shift floodlight location to the external flange face of pipe support. Minimum welding space to be observed. | Floodlight relocated to have better minimum welding space | PB | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-05B |  | LES-299-06-M05B-002 | 10083C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
None | Adjust the floodlight location slightly away from vertical pipe. Same structural column to be used for mounting. | light fixture relocated to have better clearance from piping | PB | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-05B |  | LES-299-05-M05B-002 | 10084C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
None | Ensure that all sub-cable trays are properly terminated and connected to the bottom of each JB. All lighting fixtures shall be connected using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all lights and JB within Module M16. | Cable trays are routed with proper fitting wherever is feasible | SE | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 05-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M16 |  | LEM-350-10-M16-001 General for all lighting | 10085C |  | 17.0000000000000 | 3.00000000000000 | SEA/KBR | True |  | None | None | 21/12/2025 | 07/01/2026 |  |  | 07/01/2026 | 21/12/2025
None | Floodlights to be mounted on top of the structural beam but to keep at the same location. Trays droppers to avoid protruding outside the piperack space, to be shifted within piperack space. | Floodlights trelocated and mounted on top of the structural beam | SE | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 05-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M16 |  | LEM-351-10-M16-003 | 10086C |  | 17.0000000000000 | 3.00000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 07/01/2026 |  |  | 07/01/2026 | 21/12/2025
None | Adjust tray to move closer to the structural beam, to avoid obstruction for accessing the light fitting. | Tray moved closer to the structural beam to have better access for light fixture | SE | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 05-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M16 |  | LEM-351-10-M16-004 LNO-224-27-M16-002 | 10087C |  | 17.0000000000000 | 3.00000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 07/01/2026 |  |  | 07/01/2026 | 21/12/2025
None | Relocate JB within the same column but different side, away from the laydown area side, to avoid exposure to potential damage. | JB Re located | KBR | ELE | OPEN |  | None |  | None | None | ELE | None | None | M16 |  | CXN-L-M16-003 | 10088C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
None | Maintain lighting position, swap the circuit assignment, emergency light shall be closer to the access way. | Light fixture position swaped and emergency light located closer to the access way. | SE | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 05-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M16 |  | LEM-351-10-M16-004 | 10089C |  | 17.0000000000000 | 3.00000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 07/01/2026 |  |  | 07/01/2026 | 21/12/2025
None | Adjust socket assembly, tray dropper, and junction box (with support), closer to nearest structural column at FWD side, away from the safety shower. | None | KBR | ELE | OPEN |  | None |  | None | None | ELE | None | None | M16 |  | CXN-L-M16-421 | 10090C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
None | Swap location of socket assembly and telecom speaker assembly, to eliminate the MCT cable penetration for the sockets. | None | KBR | ELE | OPEN |  | None |  | None | None | ELE | None | None | M16 |  | TEL-5516007 | 10091C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
None | Verify the new access way (coordinate with layout team) model against the location of socket assembly. Resolve overlapping of space reserve. | None | KBR | ELE | OPEN |  | None |  | None | None | ELE | None | None | M16 |  | SKN-M16-424 | 10092C | 22/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Shift location of socket for wash trolley to AFT side of GTG package, near turbine area. (Cable reach is maximum 15m - socket to wash trolley.) | Washing trolley 63A power socket is relocated near to the turbine area GTG’s package. | SE | ELE | RE-OPEN | 24/12/2025 | None |  | None | None | ELE | None | None | M-13B |  | SKN-M13B-423 SKN-M13B-424 | 10093C |  | 16.0000000000000 | 0 | PB - Operation | None |  | None | None | 27/12/2025 | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026 | 28/12/2025
None | Move cable tray below the access platform marked area | None | KBR | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-05B |  | SPI-M05B-164 | 10094C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
None | Provide combined stantion for push button | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | SPI-M05B-166 | 10095C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | To provide the additon of cable trays for each JB at a distance of 300mm. Typical. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13 |  | JBC-1424-804 JBC-1424-805 JBC-1424-806 | 10096C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | To add cable tray 90deg to main cable tray. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13 |  | IT-M13-S-I-TRAY-01009 | 10097C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Relocate the JB to avoid multiple bend for the main cable. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13 |  | JBS-1424-101 | 10098C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | To relocate cable tray and provide cable tray penetration to connect with GTG interface. Typical for 22 interface JB to GTG skid. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13 |  | General | 10099C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | KBR to model and incorporate the necessary supports in accordance with the standard KBR typical drawings for all 90 deg Bends. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M13 |  | General | 10100C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | KBR to model and add the required cable trays from each penetration point to the respective field instruments. Typical for all instruments | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | General | 10101C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Transmitter move to near tapping point location (Typical) | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | General | 10102c | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Gas service transmitter tapping to Transmitter need to minimum height | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | None | 10103c | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
None | 1. For liquid service, the instrument connection should be lower than the tapping point. 2. For gas service, the instrument connection should be higher than the tapping point. These installation requirements shall be implemented in all applicable areas. Where this arrangement cannot be maintained, KBR shall notify PB and obtain confirmation prior to implementation. Typical to all Instruments and Tappings to be check for the Modules M05B | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | General | 10104c | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Transmitter move to the near the tapping location | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | None | 10105c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
None | Transmitter dial blocking pipe. Relocate | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | None | 10106c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate the fire station or the air manifold | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05B |  | None | 10107c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Penetration needs to be modified according to standards | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-13 |  | IC-M13-S-I-02007 | 10108c | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | All the trays to be elevated above the coaming | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-13 |  | IC-M13-S-I-02027 | 10109c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all Instruments, JB and valves M13. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-13 |  | General | 10110c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Vendor tray for tie-in shall be modelled (LTG. JB / Ignition XFR JB). | None | KBR | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-13 |  | EC-M13-L-E-TRAY-01014-TRAY-0104 | 10111c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Common penetration shall be modelled for electrical & instrument tray tie-in. | Common penetration for electrical and instrument tray are modelled updated. | PB | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13 |  | EC-M13-L-N-TRAY-10006-TRAY-0103 EC-M13-L-N-TRAY-10007-TRAY-0101 | 10112c |  | 2.00000000000000 | 18.0000000000000 | SEA/KBR | True |  | None | None | 21/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 21/12/2025
None | Ensure the cables transition with no issues from the topside cable to the vendor cable tray. | Cable tray modified to have better transition from the topside cable to the vendor cable tray. | PB | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13 |  | None | 10113c |  | 2.00000000000000 | 18.0000000000000 | PB - Engineering | None |  | None | None | 21/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 21/12/2025
None | MCT and cable tray support to ensure constructibility space. | MCT and cable tray support is updated and provided constructibility space. | PB | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13 |  | None | 10114c |  | 9.00000000000000 | 18.0000000000000 | PB - Engineering | None |  | None | None | 14/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 14/12/2025
1 | M13 Safety plan to be updated as per model | 09/12/25 : This comment will be updated in the next revision of Safety Plan | KBR | SAF | RE-OPEN | 08/12/2025 | None |  | None | None | SAF | None | None | M-13 |  | LEVEL-1-5-5159 | 0135C | 08/12/2025 | 1.00000000000000 | 29.0000000000000 | SEA/KBR | None |  | None | None | 11/12/2025 | 12/12/2025 | 14/12/2025 | 14/12/2025 | 14/12/2025 | 11/12/2025
1 | Escape route to be extended to connect | Escape route extended. | KBR | PIP | Pending PB Reply | 30/11/2025 | None |  | None | 07/01/2026 - UP56 - ok - close | SAF | None | None | M13 |  | LEVEL-1-5-5622 | 0136C |  | 9.00000000000000 | 29.0000000000000 | PB - Operation | None | 07/01/2026 | True | None | 03/12/2025 | 12/12/2025 | 14/12/2025 | 14/12/2025 | 14/12/2025 | 03/12/2025
1 | Escape route to be extended to connect | Escape route extended. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | 07/01/2026 - UP56 - ok - close | SAF | None | None | M13 |  | LEVEL-1-5-5164 | 0137C |  | 23.0000000000000 | 1.00000000000000 | PB - Operation | None | 07/01/2026 | True | None | 17/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 17/12/2025
1 | Escape route volume to be modelled to ladder | Escape route volume included now. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | 08/01/2026 - UP56 - It was identified a clash to be resolved. The clash resolution shall be carried out as per Clash Management forum track and actions. For the punched item, closed - close | SAF | None | None | M13 |  | LEVEL-1-5-5149 | 0138C |  | 23.0000000000000 | 1.00000000000000 | PB - Operation | None | 08/01/2026 | True | None | 17/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 17/12/2025
1 | Rearrange equipment so that Safety Shower is not blocked | None | None | CSE | OPEN |  | None |  | None | None | SAF | None | None | M-13 |  | Z-5434385 HSS-M13-101-N003 SCBA | 0139C | 23/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Evaluate the access to the SCBA | Location of SCBA adjusted. It is accessible now. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | None | SAF | None | None | M13 |  | None | 0140C |  | 23.0000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 17/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 17/12/2025
2 | Gap between handrails to be reduced as per standard detail | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-13 |  | OFHR-M13-0000056 | 0141C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Gap between handrails to be reduced as per standard detail | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-13 |  | OFHR-M13-0000075 | 0142C | 08/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Gap to be closed | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-13 |  | CO-H400x201-0010292 conj_protecao_damper_link:1 | 0143C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handrail gap to be minimised as per standard detail | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-13 |  | OFHR-M13-0000118 | 0144C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handrail gap to be minimised as per standard detail | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-13 |  | OFHR-M13-0000095 | 0145C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Handrail gap to be minimised as per standard detail | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-13 |  | OFHR-M13-0000141 | 0146C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Tundish size to be checked and updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | 2"-DA-B9-2296-NI | 0147C | 13/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model a volume to secure access space in front of valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13 |  | VALV-51470465 | 0148C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Hose stand is blocking valve access. Accessway to be extended up to valves. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13 |  | OFHR-M13-0000141 | 0149C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Model access volume to reserve space in front of piping | Access volume modelled. | KBR | PIP | Pending Seatrium Reply | 14/12/2025 | None |  | None | None | PIP | None | None | M13/M12 |  | 1"-P-E6N-0083-NI | 0150C |  | 24.0000000000000 |  | PB - Operation | None |  | None | None | 17/12/2025 |  |  |  |  | 17/12/2025
1 | Piping to be connected | Lines are connected. | KBR | PIP | CLOSE | 14/12/2025 | Julius Orzales | 08/01/2026 | None | 08.01.2026_U4EW_Close | PIP | None | No piping DCN required | M13 | 08/01/2026 | 2"-FG-E3N-0015-HC | 0151C |  | 3.00000000000000 | 22.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 17/12/2025 | 20/12/2025 | 10/01/2026 | 11/01/2026 | 21/12/2025 | 17/12/2025
1 | Line to go towards tundish | Line is over tundish now. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | 09.01.2026_U4EW_Close | PIP | None | No piping DCN required | M13 |  | 3/4"-DA-B9-2362-NI | 0152C |  | 3.00000000000000 | 22.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 17/12/2025 | 20/12/2025 | 11/01/2026 | 11/01/2026 | 21/12/2025 | 17/12/2025
1 | Line to be over the tundish | Line is over the tundish now. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | 09.01.2026_U4EW_Close | PIP | None | No piping DCN required | M13 |  | 3/4"-DA-B9-3227-NI | 0153C |  | 3.00000000000000 | 22.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 17/12/2025 | 20/12/2025 | 11/01/2026 | 11/01/2026 | 21/12/2025 | 17/12/2025
1 | Rotate valve towards the accessway | Valve has been rotated. | KBR | PIP | CLOSE | 01/12/2025 | Julius Orzales | 08/01/2026 | None | 08.01.2026_U4EW_Close | PIP | None | No piping DCN required | M13 | 08/01/2026 | VALVE -51470669 | 0154C |  | 16.0000000000000 | 22.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 04/12/2025 | 20/12/2025 | 10/01/2026 | 11/01/2026 | 21/12/2025 | 04/12/2025
1 | Valve handwheel to be toward AFT to provide access | Valve cannot be rotated to face AFT as the handwheel will go into the handling volume under the monorail. | KBR | PIP | Pending PB Reply | 11/12/2025 | None |  | None | 10.01.2026_U4EW_Close. | PIP | None | DCN required | M13/M12 |  | VALV-51470614 | 0155C |  | 6.00000000000000 | 23.0000000000000 | PB - Operation | True | 10/01/2026 | True | None | 14/12/2025 | 20/12/2025 | 12/01/2026 | 12/01/2026 | 21/12/2025 | 14/12/2025
1 | Valves to be modelled | Valves are modelled now. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | 10.01.2026_U4EW_Close. All the 8 valves (2 for each GTG) were modelled. | PIP | None | No piping DCN required | M-12/13/13B |  | VALV-51470409 VALV-51470410 | 0156C |  | 3.00000000000000 | 23.0000000000000 | PB - Operation | True | 10/01/2026 | True | None | 17/12/2025 | 20/12/2025 | 12/01/2026 | 12/01/2026 | 21/12/2025 | 17/12/2025
1 | Check the support with shoe, u-bolt, hold-down | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13 |  | SP-M13-30210 | 0157C | 13/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Support is duplicated | Duplicate support is deleted. | KBR | PIP | CLOSE | 14/12/2025 | Julius Orzales | 08/01/2026 | None | 08.01.2026_U4EW_Close | PIP | None | No piping DCN required | M13 | 08/01/2026 | SP-M13-04003 | 0158C |  | 3.00000000000000 | 22.0000000000000 | SEA/KBR | True | 08/01/2026 | True | None | 17/12/2025 | 20/12/2025 | 10/01/2026 | 11/01/2026 | 21/12/2025 | 17/12/2025
1 | Access to valves/sampling point to be considered | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-12/13/13B |  | TG-5147001B.nwd | 0159C | 26/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Delete couplings and tag valves | Excess coupling is deleted. Valves are tagged. | KBR | PIP | CLOSE | 14/12/2025 | Julius Orzales | 08/01/2026 | None | 08.01.2026_U4EW_Close | PIP | None | No piping DCN required | M13 | 08/01/2026 | 1"-DW-B3-0005-NI | 0160C |  | 3.00000000000000 | 22.0000000000000 | SEA/KBR | True | 08/01/2026 | True | None | 17/12/2025 | 20/12/2025 | 10/01/2026 | 11/01/2026 | 21/12/2025 | 17/12/2025
1 | Review suitability of drain line connection considering one line is pressurised | Process informed the lines should not be connected directly. They should connect to the sub-headers. Accordingly, piping has been updated. | KBR | PIP | Pending PB Reply | 01/12/2025 | None |  | None | None | PIP | None | DCN required | M-12/13/13B |  | 1"-DA-B9-3014-NI | 0161C |  | 16.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 04/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 04/12/2025
2 | Access to hose stand is blocked by piping | Piping is adjusted and hose stand is not blocked now. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | 08.01.2026_U4EW_The line 1"-IA-B3-1074-NI modelling aren´t finished. Need to complete to evaluete whether any line part are interfering in the access the rose stand | PIP | None | No piping DCN required | M13 |  | M13-MEZZ-US-0003-HS | 0162C |  | 3.00000000000000 | 21.0000000000000 | PB - Operation | True | 08/01/2026 | False | None | 17/12/2025 | 20/12/2025 | 10/01/2026 | 11/01/2026 | 21/12/2025 | 17/12/2025
3 | Evaluate whether line should be considered hook-up and moved to hook-up hierarchy | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-13 |  | 16"-SW-B23-1321-NI | 0163C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | Ensure support steel is strong enough - typical comment for this line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-13 |  | SE-M13-01254 | 0164C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | PIT Tapping to be oriented to correct direction | PIT orientation corrected. | KBR | PIP | CLOSE | 07/01/2026 | Julius Orzales | 08/01/2026 | None | 08.01.2026_U4EW_Close | PIP | None | no piping dcn required | M13 | 08/01/2026 | HWP-0043 | 0165C |  | 0 | 1.00000000000000 | SEA/KBR | True | 08/01/2026 | True | None | 10/01/2026 | 10/01/2026 | 10/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
2 | PIT Tapping to be oriented to correct direction | PIT tapping orientation is corrected. | KBR | PIP | CLOSE | 07/01/2026 | Julius Orzales | 08/01/2026 | None | 08.01.2026_U4EW_Close | PIP | None | no piping dcn required | M13 | 08/01/2026 | HWP-0078 | 0166C |  | 0 | 1.00000000000000 | SEA/KBR | True | 08/01/2026 | True | None | 10/01/2026 | 10/01/2026 | 10/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
3 | Update tundish size and make flush with HWP pipe | The tundish is flush with HWP pipe. | KBR | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13/M12/M13B |  | DA-1577 | 0167C | 12/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Route line straight without pocket | Line cannot be routed straight, as per comment. The current line routing downwards is so the piping will be clear of the swinging effects from the crane at the laydown area. | KBR | PIP | CLOSE | 01/12/2025 | Julius Orzales | 08/01/2026 | None | 08.01.2026_U4EW_Close to PB operation team. | PIP | None | No piping DCN required | M13 | 08/01/2026 | HWP-0969 | 0168C |  | 16.0000000000000 | 22.0000000000000 | SEA/KBR | True | 08/01/2026 | True | None | 04/12/2025 | 20/12/2025 | 10/01/2026 | 11/01/2026 | 21/12/2025 | 04/12/2025
1 | Telecom equipment to be moved clear of removal area | None | KBR | TEL | OPEN |  | None |  | None | None | HAND | None | None | M13/M12 |  | COR-5518318A | 0169C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Obstruction volume for M12 pulling post to be modelled | Obstruction volume for M12 pulling post is modelled | KBR | HAND | Pending PB Reply |  | None |  | None | 09.01.25_B0RG_CLOSE | HAND | None | 9Jan2026_Cleared. | M-13 |  | MR-M13-1008 | 0170C | 11/01/2026 |  | 0 | PB - Operation | True | 09/01/2026 | True | None |  | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
1 | Beam clamp sling volume to be modelled and ensure no interference with piping | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-13 |  | BC-M13-1004-2MT | 0171C | 08/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Lighting/piping to be moved away from drop zone | Piping: Piping is dropped down to deck level when it nears the drop zone. Also, at any point piping is already more than 300mm away from the drop zone. | None | ELE | OPEN |  | None |  | None | None | HAND | None | None | M13/M12 |  | LES-311-25-M13-001 LNO-223-35-M13-003 | 0172C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Telecom equipment/lighting to be moved away from drop zone | Light Fixture location updated. | KBR | TEL | OPEN |  | None |  | None | None | HAND | None | None | M13 |  | LEM-347-16-M13-003 BLE-5511271 | 0173C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
None | Trays shall be modelled showing complete connectivity. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-13 |  | None | 10115c | 29/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Ensure that all sub-cable trays are properly terminated and connected to the bottom of each JB. All lighting fixtures shall be connected using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all lights and JB within Module M13. | None | SE | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-13 |  | General | 10116c | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Lighting sub-tray shall be adjusted to suit the floodlight location. | Lighting sub-tray adjusted to suit the floodlight location. | SE | ELE | Pending PB Reply | 11/12/2025 | None |  | None | 09.01.2026_U4EW_Close | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-13 |  | LNO-223-29-M13-003 | 10117c |  | 9.00000000000000 | 19.0000000000000 | SEA/KBR | True | 09/01/2026 | True | None | 14/12/2025 | 23/12/2025 | 11/01/2026 | 11/01/2026 | 23/12/2025 | 14/12/2025
None | Shift/relocate JB to other side of column, mounted at the column web, to avoid obstructing the escape/access way. | Lighting JB moved to Web to clear the escape way. | PB | ELE | Pending PB Reply | 05/12/2025 | None |  | None | 09.01.2026_U4EW_Close | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-13 |  | CXE-L-M13-302 | 10118c |  | 15.0000000000000 | 19.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 08/12/2025 | 23/12/2025 | 11/01/2026 | 11/01/2026 | 23/12/2025 | 08/12/2025
None | Shift/relocate JB below the light fitting at the same structural column. Remove the excess lighting sub-tray. | Lighting JB relocated. | PB | ELE | Pending PB Reply | 11/12/2025 | None |  | None | 09.01.2026_U4EW_Close | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: ENSURE THE CABLE TRAY IS MODELLED UNTIL THE JB CABLE TERMINATION POINT. | M-13 |  | CXE-L-M13-206 | 10119c |  | 9.00000000000000 | 19.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 14/12/2025 | 23/12/2025 | 11/01/2026 | 11/01/2026 | 23/12/2025 | 14/12/2025
None | Shift pipe/ tray closer to nearby beam, to create clearance away from lighting. (Close out shall be tag wise for lighting) | Piping is shifted away from lighting. | PB | PIP | CLOSE | 21/12/2025 | Julius Orzales | 08/01/2026 | None | 08.01.2026_U4EW_Close | PIP | None | No piping DCN required | M13 | 08/01/2026 | LEM-346-14-M13-006 (General applicable to all module) | 10120c |  | 1.00000000000000 | 17.0000000000000 | PB - Operation | True | 08/01/2026 | True | None | 24/12/2025 | 25/12/2025 | 10/01/2026 | 11/01/2026 | 25/12/2025 | 24/12/2025
None | Floodlight to be shifted higher to create clearance away from guard rail. Guard rail to bridge the space gap with nearby column. | Floodlight Fixture moved higher to create clearance away from guard rail. | PB | ELE | Pending PB Reply | 05/12/2025 | None |  | None | 09.01.2026_U4EW_Not acepted. The floodligth position was adjusted, but the GAP between the structure and the guard rail shall be filled, as described in punch. | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-13 |  | LES-311-22-M13-002 | 10121c |  | 15.0000000000000 | 19.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 08/12/2025 | 23/12/2025 | 11/01/2026 | 11/01/2026 | 23/12/2025 | 08/12/2025
None | Adjust/shift vertical pipe as it is very close to light fitting. Access to lighting to be maintained. | The vertical pipe is moved away from light fixture, and the maintenance access also maintained. | PB | ELE | Pending PB Reply | 05/12/2025 | None |  | None | 09.01.2026_U4EW_Close | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-13 |  | LEM-347-14-M13-003 | 10122c |  | 15.0000000000000 | 19.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 08/12/2025 | 23/12/2025 | 11/01/2026 | 11/01/2026 | 23/12/2025 | 08/12/2025
None | Shift instrument tray away from lighting to avoid obstructing the illumination throw. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-13 |  | LNO-223-31-M13-003 | 10123c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
None | Mount the lighting fixture to the nearby pipe support. | Light Fixture attcahed with pipe support. | SE | ELE | Pending PB Reply | 05/12/2025 | None |  | None | 09.01.2026_U4EW_Close | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-13 |  | LEM-346-16-M13-001 | 10124c |  | 15.0000000000000 | 19.0000000000000 | SEA/KBR | True | 09/01/2026 | True | None | 08/12/2025 | 23/12/2025 | 11/01/2026 | 11/01/2026 | 23/12/2025 | 08/12/2025
None | Shift support away from path of cable routing. | Tray support is updated away from the cable routing | PB | ELE | RE-OPEN | 11/12/2025 | None |  | None | None | ELE | None | None | M-13 |  | ESPT-M13-20035 | 10125c |  | 9.00000000000000 | 18.0000000000000 | PB - Operation | None |  | None | None | 14/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 14/12/2025
1 | Escape route to be extended to M11 | Escape route extended from M11. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | 07/01/2026 - UP56 - ok - close | SAF | None | None | M12 |  | LEVEL-1-5-5338 | 0174C |  | 23.0000000000000 | 1.00000000000000 | PB - Operation | None | 07/01/2026 | True | None | 17/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 17/12/2025
1 | Access to safety shower from escape route is blocked. Equipment to be relocated | None | KBR | TEL | OPEN |  | None |  | None | None | SAF | None | None | M12 |  | Z-5434380 SPP-M12-00082 | 0175C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Extinguisher not required at this location. To be deleted from the model and reflected on Safety Plan. | Extinguisher has been deleted. | KBR | PIP | Pending PB Reply | 08/12/2025 | None |  | None | 07/01/2026 - UP56 - ok - close | SAF | None | None | M12 |  | Z-5147001 | 0176C | 08/12/2025 | 1.00000000000000 | 29.0000000000000 | SEA/KBR | None | 07/01/2026 | True | None | 11/12/2025 | 12/12/2025 | 14/12/2025 | 14/12/2025 | 14/12/2025 | 11/12/2025
1 | Pipe support over gutter to be adjusted | Piping has been adjusted and there is no support over the gutter now. 24 Dec 25: Piping is shifted further PORT side into the coamed area now. | KBR | PIP | Pending PB Reply | 23/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M12 |  | 1"-DW-B3-0020-NI | 0177C |  | -5.00000000000000 | 20.0000000000000 | PB - Operation | None |  | None | None | 26/12/2025 | 21/12/2025 | 23/12/2025 | 23/12/2025 | 21/12/2025 | 28/12/2025
1 | Access restricted by area coaming and cable trays. | Location of extinguisher has been adjusted. 22 Dec 25: Coaming is no longer within the extinguisher reserved volume. | KBR | PIP | RE-OPEN | 21/12/2025 | None |  | None | None | SAF | None | None | M12 |  | Z-5428321 | 0178C | 08/01/2026 | -12.0000000000000 | 29.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 12/12/2025 | 14/12/2025 | 14/12/2025 | 14/12/2025 | 24/12/2025
1 | Handrail gap to be minimised as per standard detail (typical punch for this module) | Handrail Gap updated | KBR | STR | RE-OPEN | 28/12/2025 | None |  | None | None | SAF | None | None | M12 |  | OFHR-M12-0000002 | 0179C | 22/01/2026 | 0 | 10.0000000000000 | PB - Operation | None |  | None | None | 31/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 31/12/2025
1 | Escape route to be modelled on stair landing | Escape route volume has been modelled. | KBR | PIP | Pending PB Reply | 01/12/2025 | None |  | None | 08/01/2026 - UP56 - ok - close | SAF | None | None | M12 |  | L2-LANDING-1-VOL | 0180C |  | 8.00000000000000 | 29.0000000000000 | PB - Operation | None |  | None | None | 04/12/2025 | 12/12/2025 | 14/12/2025 | 14/12/2025 | 14/12/2025 | 04/12/2025
2 | Kick plate to be adjusted to correct position closer to equipment | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M12 |  | OFLD-M12-0096781 | 0181C | 26/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Cage is not required considering ladder height, to be removed from model. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M12 |  | KBRLadder_Right-7-0605 | 0182C | 26/01/2026 |  |  | SEA/KBR | None |  | None | None
3 | Escape route to be updated | Escape route updated. | KBR | PIP | Pending Seatrium Reply | 07/01/2026 | None |  | None | None | SAF | None | None | M12 |  | LEVEL-3-5-3377 | 0183C |  | 0 |  | PB - Operation | None |  | None | None | 10/01/2026 |  |  |  |  | 11/01/2026
3 | Supports to be cleared from top rail of handrail (typical punch for supports on handrails) | None | None | TEL/ELE | OPEN |  | None |  | None | None | SAF | None | None | M12/M13/M13B |  | SPP-M12-00047 SPL-M12-00311 | 0184C |  |  |  | PB - Operation | None |  | None | None
3 | Structure to update coaming to clear clash. Piping to remove duplicate coaming. | Coaming updated by Structure. Duplicate coaming is deleted by Piping.Handling to clear clash | KBR | HAND | RE-OPEN | 09/01/2026 | None |  | None | None | SAF | None | None | M12 |  | Z-5434382 | 0185C | 15/01/2026 | -12.0000000000000 | 12.0000000000000 | PB - Operation | None |  | None | None | 12/01/2026 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 12/01/2026
4 | Structure to update coaming to clear clash. Piping to remove duplicate coaming. | Coaming is updated by Structure. Duplicate coaming is deleted by Piping. 10/01/2026- Coaming updated | KBR | STR | Pending Seatrium Reply | 09/01/2026 | None |  | None | None | SAF | None | None | M12 |  | Z-5434383 | 0186C | 15/01/2026 | -12.0000000000000 | 12.0000000000000 | PB - Operation | None |  | None | None | 12/01/2026 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 12/01/2026
5 | Structure to update coaming to clear clash. Piping to remove duplicate coaming. | Coaming is updated by Structure. Duplicate coaming is deleted by Piping. | KBR | STR | RE-OPEN | 21/12/2025 | None |  | None | None | SAF | None | None | M12 |  | Z-5434384 | 0187C | 15/01/2026 | 7.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 24/12/2025
1 | Davit opening through ladder - to be resolved | Ladder adjusted and clear of davit opening. | KBR | PIP | Pending PB Reply | 23/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M12 |  | FT-5135001E | 0188C |  | 7.00000000000000 | 8.00000000000000 | PB - Operation | None |  | None | None | 26/12/2025 | 02/01/2026 | 04/01/2026 | 04/01/2026 | 04/01/2026 | 28/12/2025
1 | Access volume to be extended to provide access to the y-type strainers | Access volume extended. | KBR | PIP | Pending PB Reply | 07/01/2026 | None |  | None | None | PIP | None | no piipng dcn required | M12 |  | LEVEL-1-5-5253 | 0189C |  | 1.00000000000000 | -1.00000000000000 | PB - Operation | None |  | None | None | 10/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
1 | Valve to be relocated to accessible position | Valve has been relocated to accessible location. | KBR | PIP | Pending PB Reply | 02/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M12 |  | VALV-51470672 | 0190C |  | 15.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 05/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 07/12/2025
1 | Accessway to be modelled | Accessway has been modelled. | KBR | PIP | Pending Seatrium Reply | 23/12/2025 | None |  | None | None | PIP | None | None | M12 |  | JBIF-1423-003 JBIF-1423-001 JBS-1423-001 | 0191C |  | 15.0000000000000 |  | PB - Operation | None |  | None | None | 26/12/2025 |  |  |  |  | 28/12/2025
2 | PG and valve to be in vertical | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M12 |  | PG-5147009F | 0192C | 15/01/2026 |  |  | SEA/KBR | None |  | None | None
2 | PG and valve to be in vertical | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M12 |  | PG-5147009E | 0193C | 15/01/2026 |  |  | SEA/KBR | None |  | None | None
3 | Confirm with Process the correct drain configuration | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M12 |  | HWP-0171 | 0194C | 12/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Gap between shoe and support steel - check if it is required | 20mm vertical gap is required as per stress report. | KBR | PIP | Pending PB Reply | 15/12/2025 | None |  | None | None | PIP | None | DCN required | M12 |  | SP-M12-30165 | 0195C |  | 3.00000000000000 | 20.0000000000000 | SEA/KBR | None |  | None | None | 18/12/2025 | 21/12/2025 | 23/12/2025 | 23/12/2025 | 21/12/2025 | 18/12/2025
3 | Gap between shoe and support steel - check if it is required | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M12 |  | SP-M12-24619 | 0196C | 20/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Piping to terminate facing horizontal or downwards only | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M12/M13/M13B |  | 3&quot;-BG-B10-0192-NI 2&quot;-IA-B3-1055-NI | 0197C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Line routing to be checked and updated | W-0502 has been optimised. | KBR | PIP | Pending PB Reply | 15/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M12 |  | 2"-W-B3-0502-NI | 0198C |  | 3.00000000000000 | 20.0000000000000 | PB - Operation | None |  | None | None | 18/12/2025 | 21/12/2025 | 23/12/2025 | 23/12/2025 | 21/12/2025 | 18/12/2025
1 | Removable handrail is longer than maximum allowed. Handrails to be split. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M12 |  | HNDRL PLTF_REM | 0199C | 18/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Safety equipment to be relocated away from handling path | Hose box has been shifted outside of handling path. | KBR | PIP | Pending PB Reply | 15/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 26Dec2025_Cleared. | M12 |  | PL-5148012 Z-H-5423101 | 0200C |  | 10.0000000000000 | 14.0000000000000 | PB - Operation | True | 07/01/2026 | True | None | 18/12/2025 | 28/12/2025 | 09/01/2026 | 11/01/2026 | 28/12/2025 | 18/12/2025
1 | Beam clamp SWL to be renamed as per MH drawing | Beam clamp SWL is renamed | PB | HAND | Pending PB Reply |  | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M12 |  | BC-M12-1005-2MT BC-M12-1004-2MT | 0201C | 08/12/2025 |  | 10.0000000000000 | PB - Operation | True | 07/01/2026 | True | None |  | 01/01/2026 | 09/01/2026 | 11/01/2026 | 01/01/2026
1 | Cable trays in front of rotor removal area to be relocated | None | None | ELE | OPEN |  | None |  | None | None | HAND | None | None | M12 |  | ET-M12-L-N-TRAY-10013 IT-M12-S-I-TRAY-01001-TRAY-0008 | 0202C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
3 | Handling volume for M11 exchanger to be checked and path size updated | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M12 |  | LEVEL-3-5-3232 | 0203C | 09/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Check if removable handrail is required for handling exchanger | Handrail is made removable type for handling of exchanger | KBR | HAND | Pending Seatrium Reply |  | None |  | None | None | HAND | None | None | M12 |  | OFHR-M12-0000128 | 0204C | 07/01/2026 |  |  | SEA/KBR | None |  | None | None
5 | Lighting and telecom equipment to be moved away from drop zone. Handrail height at marked area to be increased to higher than light fixture. | None | KBR | ELE | OPEN |  | None |  | None | None | HAND | None | None | M12 |  | LEM-344-07-M12-003 BLE-5511251 LNO-222-11-M12-004 OFHR-M12-0000191 | 0205C | 18/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Evaluate if utility station piping can be mover further toward port side to give more clearance from drop zone. Drop zone size to checked and reduced if possible | Utility station piping adjusted PORT side and drop zone is cleared. | KBR | PIP | Pending PB Reply | 07/01/2026 | None |  | None | 09.01.25_B0RG_CLOSE | HAND | None | 9Jan2026_Cleared. | M12 |  | M12-L2-US-0002 | 0206C |  | 1.00000000000000 | 0 | SEA/KBR | True | 09/01/2026 | True | None | 10/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
1 | Handrail not required on step less than 600mm high | Handrail removed on step | KBR | STR | Pending PB Reply | 31/12/2025 | None |  | None | None | SAF | None | None | M11 |  | CROSS OVER STEP(7) | 0207C | 19/01/2026 | 1.00000000000000 | 6.00000000000000 | SEA/KBR | None |  | None | None | 03/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
1 | Escape route to be modelled on stair landings (typical for stair landings in M11) | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M11 |  | Slab-7-1352 Slab-7-1353 Slab-7-1340 Slab-7-1342 Slab-7-1354 Slab-7-1355 | 0208C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment located on gutter, to check feasibility of supporting at this location vs relocating equipment (note - relocation of IO panel at this stage is difficult) | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M11 |  | PN-UH-5139011 | 0209C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment support height to be updated as per I-DE-3010.2S-1400-140-S2N-029 STANDARD SAFETY EQUIPMENT SUPPORT TYPICAL DETAILS (Typical comment for M11) | None | KBR | PIP | OPEN |  | None |  | None | None | SAF | None | None | M11 |  | Z-H-5423095 | 0210C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Escape route volume to M09 to be modelled | Escape route volume to M09 is modelled | KBR | PIP | Pending Seatrium Reply | 21/12/2025 | None |  | None | None | SAF | None | None | M11 |  | LEVEL-1-MEZZ | 0211C |  | 17.0000000000000 |  | PB - Operation | None |  | None | None | 24/12/2025 |  |  |  |  | 24/12/2025
1 | Gap at handrails to be as per standard detail | Handrail gap updated | KBR | STR | Pending PB Reply | 31/12/2025 | None |  | None | 08/01/2026 - UP56 - ok - close | SAF | None | None | M11 |  | HNDR-ELEV1-MEZZ-FRP | 0212C | 19/01/2026 | 4.00000000000000 | 3.00000000000000 | PB - Operation | None | 08/01/2026 | True | None | 03/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
2 | Handrails to be modelled at interconnections | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-11 |  | None | 0213C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Gap at handrails to be as per standard detail | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-11 |  | PultrudedHandrail_E4-7-1168 | 0214C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Escape route interconnection to M12 to be modelled | Escape route interconnection to M12 is modelled. | KBR | PIP | Pending Seatrium Reply | 21/12/2025 | None |  | None | None | SAF | None | None | M11 |  | LEVEL-2-6-3674 | 0215C |  | 17.0000000000000 |  | PB - Operation | None |  | None | None | 24/12/2025 |  |  |  |  | 24/12/2025
2 | Handrail mid rail to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-11 |  | OFHR-M11-0000080 | 0216C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Handrail to be modelled | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-11 |  | PS-M11-0004841 | 0217C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Operating volume for hydrant to be updated | Operating volume for hydrant is updated | KBR | PIP | Pending Seatrium Reply | 21/12/2025 | None |  | None | None | SAF | None | None | M11 |  | H-5423159 | 0218C |  | 17.0000000000000 |  | PB - Operation | None |  | None | None | 24/12/2025 |  |  |  |  | 24/12/2025
3 | Operating volume to be modelled (Typical for safety equipment at Level 3) | Operating volume is modelled | KBR | PIP | Pending Seatrium Reply | 21/12/2025 | None |  | None | None | SAF | None | None | M11 |  | Z-5428309 | 0219C |  | 17.0000000000000 |  | PB - Operation | None |  | None | None | 24/12/2025 |  |  |  |  | 24/12/2025
4 | Hydrant tag to be updated as per Safety Plan | 8 Jan 2026: Due to adjustment by hydrant Piping in M11, change of tag number is required in the FFLS equipment list, M11 Safety Plan and M11 Hydrant P&ID and Hydrant Coverage Report, as found in the attached markup provided by Piping. | None | SAF | RE-OPEN | 07/01/2026 | None |  | None | None | SAF | None | None | M11 |  | H-5423161 | 0220C |  | 0 |  | SEA/KBR | None |  | None | None | 10/01/2026 |  |  |  |  | 11/01/2026
4 | Gap at handrails to be as per standard detail | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-11 |  | OFHR-M11-0000145 OFHR-M11-0000138 | 0221C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Removal volume to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 16"-DA-B22-3482-NI | 0222C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Add drain at bottom of strainer and remove drain in downstream (typical punch) | Drain added at bottom of strainer and removed drain in downstream | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M11 |  | ESP-12510052 | 0223C |  | 1.00000000000000 | 16.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 24/12/2025
1 | Check suitability if this FRP support type considering valve body - bottom of butterly valve interfering with pipe support | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | SP-M11-49574 VALV-12510375 | 0224C | 16/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Portable steps to be modelled for filter removal | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | ESP-12510051 | 0225C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Space reservation volumes to be modelled for instrument access | Space reservation volumes modelled for instrument access | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M11 |  | 18"-IW-C30-0043-NI | 0226C |  | 1.00000000000000 | 16.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 24/12/2025
1 | Access to valve is blocked by cable tray (typical for all 3 pumps) | None | None | ELE | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | VALV-12510128 VALV-12510064 VALV-12510080 | 0227C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check for modelling of drain in vendor package shown on P&ID | Drain valve modelled in vendor ackage has been checked aainst P&ID. They are complete. | None | MECH | RE-OPEN | 03/12/2025 | None |  | None | None | PIP | None | None | M11 |  | B-1251002A Water Injection Main Pump Sulzer | 0228C | 02/12/2025 | 14.0000000000000 | 22.0000000000000 | PB - Operation | None |  | None | None | 06/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 07/12/2025
1 | Check if spacers can be located at pump nozzle, P&ID to be updated with position as per model if not possible | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | ESP-12510014 ESP-12510013 | 0229C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | 1/2" Nitrogen and fresh water lines to injection pumps to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | valv-12510710 VALV-12510113 | 0230C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check if removable spool is within allowable size. Reduce horizontal length is necessary. (typical comment) | Removal spool flange location moved to as close possible | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M11 |  | 12"-IW-C30-0106-NI | 0231C |  | 0 | 16.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 25/12/2025
1 | Valve to be in horizontal | line rerouted for change the valve position. | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M11 |  | 3"-BG-B10-0058-NI | 0232C |  | 0 | 16.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 25/12/2025
1 | Increase of line (4"-DA-B22-0423-NI) to 6" shall be upstream of line 4"-DA-B22-0421-NI - reducer to be relocated | Reducer location moved after 4"-DA-B22-0421-NI line tapping | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M11 |  | 4&quot;-DA-B22-0423-NI 4&quot;-DA-B22-0421-NI | 0233C |  | 0 | 16.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 25/12/2025
1 | One valve to be in horizontal to allow space for short spool at sample point outlet | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 2"-IWC-B23-0005-NI | 0234C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check if TIT can be located at accessible position, check with process if tapping sequence can be changed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | TIT-1251006 | 0235C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check for relocating corrosion coupon located in dead leg, and check with Process on removal of flanges at end of line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 20"-IW-H12N-0157-NI | 0236C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check with stress team if possible to avoid protruding hanger through deck | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | SM-M11-00006 | 0237C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Low point drain to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 18"-IW-C30N-0091-NI | 0238C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Make the valve handwheel horizontal | the valve handwheel updated | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | DCN required | M11 |  | VALV-12510131 | 0239C | 23/01/2026 | 1.00000000000000 | 16.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 24/12/2025
1 | Valve stem to be in vertical for access from starboard side. (typical for all pumps) | Valve stem position updaed to vertical | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | DCN required | M11 |  | VALV-12510114 | 0240C | 23/01/2026 | 0 | 16.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 25/12/2025
1 | Locate vent downstream of check valves (typical for all 3 pumps) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 18"-IW-H30N-0103-NI | 0241C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Strainer to be equipped with a drain as per P&ID Note 6 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | ESP-12510036 ESP-12510031 ESP-12510038 | 0242C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model a space reservation volume for accessing CIP valves | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 18"-IW-B23-0101-NI | 0243C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | Drain to terminate inside coaming | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 1-1/2"-IW-H30N-0029-NI | 0244C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Provide gap between coaming and drain pit for welding (typical) | Coaming updated | None | STR | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | no piing dcn required | M11 |  | M11-L2-DP1-001 P-1251001A | 0245C | 08/01/2026 | 1.00000000000000 | 0 | SEA/KBR | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
2 | Access to utility hose connection is blocked. Check with Process if possible to change to bottom orientation so it can also be used as drain (inside coaming area). | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | VALV-12510206 VALV-12510175 | 0246C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Penetration sleeve to be updated for plated area matching with coaming height | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | PD-M11-L2-25987 | 0247C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
2 | Check with process if utility connection can change to vertical orientation for use as vent, with nozzle in horizontal | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | VALV-12510445 VALV-12510455 VALV-12510484 VALV-12510479 | 0248C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Valves too low to floor - height to be raised | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | VALV-51240288 VALV-51240281 | 0249C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | TIT and drain to be repositioned to give more space for bolt removal | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 20"-IW-H12N-0157-NI | 0250C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Confirm with process the location of PSEs consider the distance from the cooler nozzles (P&ID I-DE-3010.2S-1251-944-S2N-006 note 6 states 9m limit). | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | PSE-1251013A-A / A-B / B-A / B-B | 0251C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Multistage FOs to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | FO-1251002A FO-1251001A | 0252C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Spec blind to be modelled as per P&ID | Spec blind modelled as per P&ID | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | DCN required | M11 |  | 8&quot;-IW-H12N-0161-NI 8&quot;-IW-B23-0115-NI | 0253C | 23/01/2026 | 0 | 16.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 25/12/2025
2 | Open drain line is connected to pressurised SW system - to check and update | DA-3503 drain line connected to DA-1612 header | KBR | PRO | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M11 |  | 1"-DA-B22-3503-NI | 0254C | 22/12/2025 | 0 | 17.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 25/12/2025
2 | Structure to be provided for pipe support | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M-11 |  | SP-M11-09791 | 0255C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Move the vent close to Mezzanine deck | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 3/4"-W-C10-0600-NI | 0256C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | High point vent to be added | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 10"-IW-B22-0725-NI | 0257C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | CIP connecting lines to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 20"-IWC-B23-0005-NI | 0258C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve handwheel too close to support, reorient valve stem or adjust support position to provide clearance | Support location adjusted. Clash resolved | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M11 |  | VALV-12510250 VALV-12510247 | 0259C |  | 0 | 16.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 25/12/2025
4 | High point vent to be modeled at this location | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 20"-SW-B23-0319-NI | 0260C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Additional flanges required for break-out spool due to wafer type valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 12"-IW-B22-0146-NI | 0261C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Drain box tapping to be at Aft side of gutter | Drain box tapping moved at Aft side of gutter | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M11 |  | 6"-DA-B22-0004-NI | 0262C |  | 0 | 16.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 25/12/2025
4 | Pipe support and drain is blocking space for bolt removal | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | 20"-SW-B23-0147-NI | 0263C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Escape route volume to be modeled on stair landing (typical punch for M02) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | Slab-7-1445 | 0264C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Safety equipment support height to be as per standard detail I-DE-3010.2S-1400-140-S2N-029 STANDARD SAFETY EQUIPMENT SUPPORT TYPICAL DETAILS (typical punch for M02) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | None | 0265C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 & 2 | Operating volumes to be adjusted to correct position | Operating volumes moved to correct position H-5423009 H-5423010 | None | PIP | Pending Seatrium Reply | 16/12/2025 | None |  | None | None | PIP | None | None | M-02 |  | H-5423009 H-5423010 | 0266C | 16/01/2026 | 22.0000000000000 |  | PB - Operation | None |  | None | None | 19/12/2025 |  |  |  |  | 21/12/2025
1 | Safety equipment to move as close as possible to edge of coaming | Safety equipment moved close as possible to edge of coaming Z-5428017 Z-5434003 | None | PIP | Pending Seatrium Reply | 16/12/2025 | None |  | None | None | SAF | None | None | M-02 |  | Z-5428017 Z-5434003 | 0267C | 16/01/2026 | 22.0000000000000 |  | PB - Operation | None |  | None | None | 19/12/2025 |  |  |  |  | 21/12/2025
1 | Piping to be connected to safety shower | Piping connected to safety shower | None | PIP | Pending Seatrium Reply | 16/12/2025 | None |  | None | None | SAF | None | None | M-02 |  | Z-5434333 1-1/2&quot;-PW-B3-0231-NI | 0268C | 16/01/2026 | 22.0000000000000 |  | PB - Operation | None |  | None | None | 19/12/2025 |  |  |  |  | 21/12/2025
1 | Kickplate on stair landing to be extended OFHR-M02-0000017 | Kickplate on stair landing extended. | KBR | STR | Pending PB Reply |  | None |  | None | None | STR | None | None | M-02 |  | OFHR-M02-0000015 OFHR-M02-0000017 | 0269C | 26/01/2026 |  | 23.0000000000000 | PB - Operation | None |  | None | None |  | 18/12/2025 | 20/12/2025 | 21/12/2025 | 18/12/2025
2 | Instrument panel to be clear of safety equipment operating space | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-02 |  | Z-5428445 | 0270C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Equipment to be modelled as EEBD | Z-5434002 Equipment modelled as EEBD | KBR | PIP | Pending Seatrium Reply | 06/01/2026 | None |  | None | None | PIP | None | None | M-02 |  | Z-5434002 | 0271C | 16/01/2026 | 1.00000000000000 |  | PB - Operation | None |  | None | None | 09/01/2026 |  |  |  |  | 11/01/2026
3 | Equipment to be modelled as SCBA | Z-5434451 modelled as SCBA | None | PIP | Pending Seatrium Reply | 16/12/2025 | None |  | None | None | SAF | None | None | M-02 |  | Z-5434451 | 0272C | 16/01/2026 | 22.0000000000000 |  | PB - Operation | None |  | None | None | 19/12/2025 |  |  |  |  | 21/12/2025
3 | Access path connecting to metering skid to be provided | Access path connecting to metering skid updated in 3D model. | None | PIP | Pending PB Reply | 16/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | None | M-02 |  | Z-5135001 | 0273C | 16/01/2026 | 16.0000000000000 | 7.00000000000000 | PB - Operation | True | 09/01/2026 | True | None | 19/12/2025 | 04/01/2026 | 11/01/2026 | 11/01/2026 | 04/01/2026 | 21/12/2025
5 | Escape route volume to be extended | Escape route volume updated | KBR | PIP | Pending Seatrium Reply | 06/01/2026 | None |  | None | None | PIP | None | None | M-02 |  | LEVEL-5-6-3387 | 0274C | 23/01/2026 | 1.00000000000000 |  | PB - Operation | None |  | None | None | 09/01/2026 |  |  |  |  | 11/01/2026
1 | Piping to be relocated toward aft side of ladder | Awaiting a response from Vendor Siemens. | None | MECH | OPEN | 27/01/2026 | None |  | None | None | MECH | None | None | M-02 |  | 2&quot;-DA-B9-1745-NI 2&quot;-DA-B9-3358-NI 2&quot;-DA-B9-3368-NI | 0275C | 28/01/2026 | -19.0000000000000 |  | PB - Operation | None |  | None | None | 30/01/2026 |  |  |  |  | 01/02/2026
1 | Handrail to be provided by vendor in this area to prevent falling hazard | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M-02 |  | COMPRESSOR-WORKING-1.nwd COMPRESSOR-WORKING-2.nwd COMPRESSOR-WORKING-3.nwd | 0276C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Kickplate to be shortened and run straight (typical for all trains) | Kickplate removed since gap between platform grating to vendor Equipment is not greater than 25mm. | KBR | STR | Pending PB Reply |  | None |  | None | None | STR | None | None | M-02 |  | SS-M02-0003043 | 0277C | 26/01/2026 |  | 23.0000000000000 | PB - Operation | None |  | None | None |  | 18/12/2025 | 20/12/2025 | 21/12/2025 | 18/12/2025
1 | Line to be sloped as per P&ID (typical for all trains) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | DFC-1858 | 0278C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | FOs to be modeled upstream of valve (typical for all trains) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | FO-1254006A FO-1254007A FO-1254006B FO-1254007B FO-1254006C | 0279C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check if reinforcement pad is required | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | SP-M02-16605 SP-M02-16552 SP-M02-16605 | 0280C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Provide more space for maintenance of LIT by modifying FW line | FW line modified & more space provided for maintenance of LIT. updated for both train B & C. | None | PIP | RE-OPEN | 16/12/2025 | None |  | None | None | PIP | None | None | M-02 |  | FW-1695 LIT-1254020A | 0281C | 23/01/2026 | 2.00000000000000 | 20.0000000000000 | PB - Operation | None |  | None | None | 19/12/2025 | 21/12/2025 | 23/12/2025 | 23/12/2025 | 21/12/2025 | 21/12/2025
2 | FIT valves to be modelled (typical for all 6 FE in Level 2) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | FE-1254003A/B/C FE-1254027A/B/C | 0282C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | 1.5" bypass valves to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | LV-1254008B | 0283C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Modelling of support to be checked and updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | SE-M02-03066 | 0284C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Gap in equipment coaming to be filled | Equipment coaming gap filled. | KBR | PIP | RE-OPEN | 06/12/2025 | None |  | None | None | PIP | None | None | M-02 |  | None | 0285C | 23/01/2026 | 15.0000000000000 | 17.0000000000000 | PB - Operation | None |  | None | None | 09/12/2025 | 24/12/2025 | 26/12/2025 | 28/12/2025 | 24/12/2025 | 09/12/2025
1 | 300mm height coaming at marked point to be provided at centre of drain box to prevent overflow spillage during deluge | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | None | 0286C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Compressor skid drain lines to be aligned as per vendor tie-in location (TYPICAL FOR ALL TRAINS) | Compressor skid drain lines aligned to vendor tie-in. updated for all locatins | KBR | PIP | Pending PB Reply | 06/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-02 |  | 2"-DA-B9-1746 2"-DA-B9-1742-NI 2"-DA-B9-1744-NI | 0287C | 30/01/2026 | 11.0000000000000 | 22.0000000000000 | PB - Operation | None |  | None | None | 09/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 09/12/2025
1 | Collection pots to be aligned with PSV outlet line and drain lines. Outlet line to be inside funnel | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | PSV-1254109A/B/C PSV-1254106A/B/C PSV-1254107A/B/C PSV-1254108A/B/C | 0288C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | For voricon drain line, valve to be added (typical for all trains) as per I-DE-3010.2S-1254-944-DG3-002_B | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | 2"-DA-B9-XX01-NI | 0289C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Verify if the vent to safe location directly above safety route is acceptable. Reroute if necessary. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | 2"-IA-B3-1145-NI | 0290C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Corrosion coupon to be modelled | Corrosion coupon modelled | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M-02 |  | XE-5135004 | 0291C | 30/01/2026 | 0 | 1.00000000000000 | SEA/KBR | None |  | None | None | 09/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
1 | Vent to be provided on inlet or outlet of motor cooling water line | Vent provided on outlet line of motor cooling water line | None | PIP | RE-OPEN | 06/12/2025 | None |  | None | None | PIP | None | None | M-02 |  | 4"-W-B10-3225-NI | 0292C | 30/01/2026 | 11.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 09/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 09/12/2025
2 | AIT tappings to be modelled | AIT-1254003A/B/C tappings modelled for all the trains | None | PIP | Pending PB Reply | 16/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-02 |  | AIT-1254003A/B/C | 0293C | 30/01/2026 | 2.00000000000000 | 20.0000000000000 | PB - Operation | None |  | None | None | 19/12/2025 | 21/12/2025 | 23/12/2025 | 23/12/2025 | 21/12/2025 | 21/12/2025
2 | PDIT-1254059B to be modelled downstream of strainer | PDIT-1254059B to be modelled downstream of strainer | None | PIP | Pending PB Reply | 06/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-02 |  | PDIT-1254059B 4&quot;-W-B10-3225-NI | 0294C | 30/01/2026 | 11.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 09/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 09/12/2025
2 | Sampling point on P-0866 to be modelled | Sampling point on P-0866 is modelled | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M-02 |  | P-0866 | 0295C | 30/01/2026 | 0 | 1.00000000000000 | PB - Operation | None |  | None | None | 09/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
4 | Valve missing handwheel to be updated | valve is modelled | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M-02 |  | VALV-12540373 | 0296C | 06/02/2026 | 0 | 1.00000000000000 | PB - Operation | None |  | None | None | 09/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
4 | Vent without valve to be flanged (typical for all vents without valves) | High point vent updated as Flange+Blind Flange, typically updated for all PCHE inlet line. | None | PIP | Pending PB Reply | 06/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-02 |  | 3/4"-P-C6N-0899-NI | 0297C | 06/02/2026 | 11.0000000000000 | 21.0000000000000 | PB - Engineering | None |  | None | None | 09/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 09/12/2025
4 | Instrument stands to be relocated considering removable spool handling | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-02 |  | SPI-M02-427 SPI-M02-459 SPI-M02-466 SPI-M02-423 SPI-M02-472 SPI-M02-451 | 0298C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
4 | All duplex filters PGs to be modelled as per P&ID - total count 12 | All duplex filters PGs modelled as per P&ID (updated for all duplex filters) | None | PIP | Pending PB Reply | 06/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-02 |  | PG-1254006A-A PG-1254006A-B PG-1254006B-A PG-1254006B-B PG-1254006C-A PG-1254006C-B PG-1254004A-A PG-1254004A-B PG-1254004B-A PG-1254004B-B PG-1254004C-A PG-1254004C-B PG-1254003A PG-1254003B PG-1254003C | 0299C | 06/02/2026 | 11.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 09/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 09/12/2025
4 | Drain valves to be oriented so that hose connection will be within coamed area | Utility connection oriented to 90deg as requested. | None | PIP | Pending PB Reply | 06/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-02 |  | W-3714-N6A W-3714-N6B | 0300C | 06/02/2026 | 11.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 09/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 09/12/2025
4 | ESP tags to be assigned (typical for all 6 trains) Drains to be provided on T-type strainers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | 28"-P-C6N-0898-NI | 0301C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
4 | Check the connection of the PIT - typically flanged | PIT connection updated as flanged. | None | PIP | Pending PB Reply | 06/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-02 |  | PIT-1254060A/B/C | 0302C | 06/02/2026 | 11.0000000000000 | 21.0000000000000 | PB - Engineering | None |  | None | None | 09/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 09/12/2025
1 | Scrubber inlet line P&ID note for 5D straight length to be modifed as per piping arrangement approved by Vendor, I-DE-3010.2S-1254-944-S2N-001 to 6 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M02/M05/M07A&B/M05B |  | 18"-P-C6N-0901-NI | 0303C |  |  |  | PB - Engineering | None |  | None | None
3 | Line connection to pipe rack to be completed | P-0860 Line connected to pipe rack | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M-02 |  | P-0860 | 0304C | 06/02/2026 | 0 | 1.00000000000000 | PB - Operation | None |  | None | None | 09/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
1 | Line connection to be top of pipe P-1889 (confirm with Process) to prevent accumulation of liquid from conditioning skid | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | PC-2008 | 0305C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Spring connection with elbow to be modelled as padeye. Spring hanger to be clear of interference from structure | Spring connection with elbow modelled as padeye. Spring hanger interference with structure is cleared | KBR | PIP | RE-OPEN | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M-02 |  | SP-M02-12973 | 0306C | 13/02/2026 | 1.00000000000000 | 0 | PB - Engineering | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
1 | Line connection to skid to be fixed | line routing corrected (verically straight updated) | None | PIP | RE-OPEN | 06/12/2025 | None |  | None | None | PIP | None | None | M-02 |  | 2"-P-F3N-1888-NI | 0307C | 13/02/2026 | 11.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 09/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 09/12/2025
5 | Flame arrestor to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | 6&quot;-OL-B3-0129-NI 6&quot;-OL-B3-0153-NI 6&quot;-OL-B3-0156-NI | 0308C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Flange at spec break to be reselected as 600# Valve handwheel to close to adjacent pipe | Flange at spec break updatedas 600# Valve handwheel cleared to adjacent pipe | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M-02 |  | VALV-12540160 | 0309C | 13/02/2026 | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
5 | Valve tags to be added | valve tag updated as per the comment. | None | PIP | RE-OPEN | 06/12/2025 | None |  | None | None | PIP | None | None | M-02 |  | None | 0310C | 13/02/2026 | 32.0000000000000 |  | PB - Operation | None |  | None | None | 09/12/2025 |  |  |  |  | 09/12/2025
5 | Valve missing from model | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | None | 0311C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | BDV lines to be sloped to meet free draining requirement | Upstream of BDV lines maintained free draining as per PID. | None | PIP | RE-OPEN | 06/12/2025 | None |  | None | None | PIP | None | None | M-02 |  | None | 0312C | 13/02/2026 | 11.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 09/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 09/12/2025
1 | Secondary escape route volumes to be modeled (typical for all levels) | 15NOV25- Secondary escape route volume availble in the Model. | KBR | PIP | CLOSE | 14/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M-05 | 01/12/2025 | None | 0313C |  | 13.0000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 17/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 17/11/2025
1 | Quarter pipe or coaming to be shifted to close the gap in containment | Layout team to the escape path so that it clears the clash and aligns with the coaming | KBR | PIP | RE-OPEN | 28/12/2025 | None |  | None | None | STR | None | None | M-05 |  | OFLD-M05-0071058 OFLD-M05-0040035 OFLD-M05-0040037 | 0314C | 11/01/2026 | 4.00000000000000 | 6.00000000000000 | PB - Operation | None |  | None | None | 31/12/2025 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 31/12/2025
1 | Escape route to be modeled on stair landing (typical comment) | Escape route modeled on stair landing | PB | STR | Pending PB Reply | 29/11/2025 | None |  | None | None | STR | None | None | M-05 |  | None | 0315C |  | 10.0000000000000 | 29.0000000000000 | PB - Operation | None |  | None | None | 02/12/2025 | 12/12/2025 | 14/12/2025 | 14/12/2025 | 14/12/2025 | 02/12/2025
1 | Coaming to be shifted away from the hydrant and hydrant box operating area | The coaming already shifted away | PB | STR | Pending PB Reply | 29/11/2025 | None |  | None | None | STR | None | None | M-05 |  | H-5423023 Z-H-5423023 | 0316C |  | 1.00000000000000 | 38.0000000000000 | PB - Operation | None |  | None | None | 02/12/2025 | 03/12/2025 | 05/12/2025 | 07/12/2025 | 03/12/2025 | 02/12/2025
1 | Equipment support to be modelled | 25NOV25 - Support modeled for Z-543007 | KBR | PIP | CLOSE | 23/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M-05 | 01/12/2025 | Z-5434007 | 0317C |  | 4.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 26/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 26/11/2025
1 | Evaluate extending the platform towards FWD side to cover the gap without handrail on the skid or if not possible, provide handrail as per snapshot 2 location | Platform extension completed on 5-1-2026. Layout/Piping team for the follow up remaining action on handrail modeling 09Jan2026: Handrail Requirement on compressor Skid is by Vendor(siemens) and follow-up is by Mechanical PRE | KBR | PIP | OPEN | 16/12/2025 | None |  | None | None | STR | None | None | M-05 |  | E1A4829066_A | 0318C | 08/01/2026 | 0 | 23.0000000000000 | PB - Operation | None |  | None | None | 19/12/2025 | 19/12/2025 | 21/12/2025 | 21/12/2025 | 21/12/2025 | 21/12/2025
1 | Gap between handrails to be as per standard details | Already added handrail | PB | STR | Pending PB Reply | 29/11/2025 | None |  | None | None | STR | None | None | M-05 |  | KBRLadder_Front-5-0706 | 0319C |  | 1.00000000000000 | 38.0000000000000 | PB - Operation | None |  | None | None | 02/12/2025 | 03/12/2025 | 05/12/2025 | 07/12/2025 | 03/12/2025 | 02/12/2025
1 | Ladder volume to be updated to correct size (typical for Train B & C) | Reserve volume for ladder updated | KBR | ELE | RE-OPEN | 04/12/2025 | None |  | None | None | ELE | None | None | M-05 |  | KBRLadder_Front-5-0716 | 0320C |  | 15.0000000000000 | 19.0000000000000 | SEA/KBR | None |  | None | None | 07/12/2025 | 22/12/2025 | 24/12/2025 | 24/12/2025 | 22/12/2025 | 07/12/2025
1 | Reserve volume size to be updated for temp access as marked | 24NOV25 - Reserve Volume size updated as per the comment | KBR | PIP | RE-OPEN | 23/11/2025 | None |  | None | None | PIP | None | None | M-05 |  | UC-1231001A-VOLUME | 0321C | 26/01/2026 | 45.0000000000000 |  | SEA/KBR | None |  | None | None | 26/11/2025 |  |  |  |  | 26/11/2025
2 & 3 | Escape routes to be aligned with model on Safety Plan drawing | Transfer to Layout 13dec25- Transfer to Safety discipline to update and re-issue the safety layout. | None | SAF | OPEN |  | None |  | None | None | STR | None | None | M-05 |  | None | 0322C |  |  |  | SEA/KBR | None |  | None | None
2 | Gap at handrails to be as per standard details (typical 75mm, max 120 mm) | Handrail updated | PB | STR | Pending PB Reply | 04/12/2025 | None |  | None | None | STR | None | None | M-05 |  | None | 0323C |  | 12.0000000000000 | 22.0000000000000 | SEA/KBR | None |  | None | None | 07/12/2025 | 19/12/2025 | 21/12/2025 | 21/12/2025 | 21/12/2025 | 07/12/2025
3 | Block valve handwheel to be oriented behind hydrant | 24NOV25 : Valve Handle Re-orientated | KBR | PIP | CLOSE | 23/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | None | M-05 | 01/12/2025 | VALV-54230096 | 0324C |  | 4.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 26/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 26/11/2025
3 | Gap at handrails to be as per standard details (typical 75mm, max 120 mm) typical punch for Level 3 and Level 5. | Handrail gap is updated | PB | STR | Pending PB Reply | 04/12/2025 | None |  | None | None | STR | None | None | M-05 |  | None | 0325C |  | 12.0000000000000 | 22.0000000000000 | PB - Operation | None |  | None | None | 07/12/2025 | 19/12/2025 | 21/12/2025 | 21/12/2025 | 21/12/2025 | 07/12/2025
3 | Handrail and kickplate to be provided on the cooler side of access platform (typical for all 3 coolers access platform) | Already provided handrails for each access platform | KBR | STR | RE-OPEN | 29/11/2025 | None |  | None | None | STR | None | None | M-05 |  | PLTF_FRP-GRTG-F1 | 0326C | 11/02/2026 | 1.00000000000000 | 38.0000000000000 | PB - Operation | None |  | None | None | 02/12/2025 | 03/12/2025 | 05/12/2025 | 07/12/2025 | 03/12/2025 | 02/12/2025
4 | Pulling post base plate causing tripping hazard in escape route. Evaluate making base plate flush with deck vs. reroute escape route to avoid. Typical for Level 3 & 4. | 27NOV25 - Escape route adjusted to clear the Pulling obstruction | KBR | PIP | CLOSE | 26/11/2025 | PIPER | 10/12/2025 | Item has been implemented in the 3D model (reference model date: 11/December/2025). | None | PIP | None | None | M-05 | 10/12/2025 | PP-M05-4003-10MT-SWL | 0327C |  | 14.0000000000000 | 0 | PB - Operation | None |  | None | None | 29/11/2025 | 13/12/2025 | 15/12/2025 | 15/12/2025 | 14/12/2025 | 30/11/2025
4 | Gap at handrails to be as per standard details (typical 75mm, max 120 mm) | Handrail already adjusted | PB | STR | Pending PB Reply | 17/12/2025 | None |  | None | None | STR | None | None | M-05 |  | OFHR-M05-000148 | 0328C |  | 4.00000000000000 | 17.0000000000000 | PB - Operation | None |  | None | None | 20/12/2025 | 24/12/2025 | 26/12/2025 | 28/12/2025 | 24/12/2025 | 21/12/2025
1 | Check the tapping orientation for sample connection, considering the purpose of sampling | 24Nov25: Sampling Point Tapping orientation is change to Bottom as per the Comment | KBR | PIP | CLOSE | 23/11/2025 | Julius Orzales | 08/01/2026 | None | 08-01-26_KUB7_CLOSE | PIP | None | No piping DCN required | M-05 | 08/01/2026 | ESP-12310457 ESP-12310474 ESP-12310489 ESP-12310507 ESP-12310508 | 0329C |  | 24.0000000000000 | 22.0000000000000 | SEA/KBR | True | 08/01/2026 | True | None | 26/11/2025 | 20/12/2025 | 10/01/2026 | 11/01/2026 | 21/12/2025 | 26/11/2025
1 | Isolation valve to be as close as possible to nozzle to avoid dead leg - make fitting to fitting | 24MOV25- Model updated | KBR | PIP | CLOSE | 23/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | DCN required | M-05 | 01/12/2025 | VALV-12310663 3&quot;-PC-C30N-0331-ET | 0330C |  | 4.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 26/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 26/11/2025
1 | 400mm reservation volume to be modeled for maintenance access to LITs | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | LIT-1231022A/B/C | 0331C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
1 | N8 Utility connection to be modeled | 24NOV25 : Model updated. | KBR | PIP | CLOSE | 23/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05 | 01/12/2025 | V-UC-1231001B-01 | 0332C |  | 4.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 26/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 26/11/2025
1 | Coaming to be modified to reduce tripping hazard | The coaming is updated | KBR | STR | CLOSE | 17/12/2025 | Julius Orzales | 08/01/2026 | None | 08-01-26_KUB7_CLOSE | PIP | None | None | M-05 | 08/01/2026 | None | 0333C |  | 11.0000000000000 | 11.0000000000000 | SEA/KBR | True | 08/01/2026 | True | None | 20/12/2025 | 31/12/2025 | 10/01/2026 | 11/01/2026 | 31/12/2025 | 21/12/2025
1 | Coaming to be updated as marked | The coaming is updated | PB | STR | Pending PB Reply | 29/11/2025 | None |  | None | None | STR | None | None | M-05 |  | None | 0334C |  | 1.00000000000000 | 38.0000000000000 | PB - Operation | None |  | None | None | 02/12/2025 | 03/12/2025 | 05/12/2025 | 07/12/2025 | 03/12/2025 | 02/12/2025
1 | Valve to be modelled as DBB (typical for all scrubbers) | 24DEC25 : DBB valve updated in all the Scrubber sampling Lines | KBR | PIP | RE-OPEN | 23/12/2025 | None |  | None | None | PIP | None | NO PIPING DCN required | M-05 |  | VALV-12310021 | 0335C | 11/01/2026 | 0 | 15.0000000000000 | PB - Operation | None |  | None | None | 26/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025
1 | LG vent and drain connections to be modeled (typ. For all train) | 24NOV25 : Model updated to show LG vent and Drain connection. | KBR | PIP | RE-OPEN | 23/11/2025 | None |  | None | None | PIP | None | None | M-05 |  | LG-1231024B | 0336C | 26/01/2026 | 24.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 26/11/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 26/11/2025
1 | Support member to be trimmed to suit (typ) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | SP-M05-34231 | 0337C | 12/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | FOs to be modelled | 15Dec25: FO1231034A/B/C Already Modeled. FO-1231043A/B/C is not availble in M05, However other FO tags. in this Module are already Modeled. | KBR | PIP | Pending PB Reply | 14/12/2025 | None |  | None | 09-01-26_KUB7_RE-OPEN_There are FO-1231043A/B/C models, but the tags 1231044A/B/C are duplicated. | PIP | None | No piping DCN required | M-05 |  | FO-1231034A FO-1231034C FO-1231043A FO-1231043B FO-1231043C | 0338C |  | 4.00000000000000 | 21.0000000000000 | PB - Operation | None | 09/01/2026 | False | None | 17/12/2025 | 21/12/2025 | 23/12/2025 | 23/12/2025 | 21/12/2025 | 17/12/2025
1 | Pipe support pad not on top of steel, stiffeners not modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | SP-M05-45051 | 0339C | 12/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | The Operational Drain should be below the LG tie-in, to permit the drain of the maximum fluid from the pipe. | 15Dec25 - Model updated as per the DR90 comment | KBR | PIP | RE-OPEN | 14/12/2025 | None |  | None | None | PIP | None | None | M-05 |  | 2"-PC-F3N-2746-PP | 0340C | 13/01/2026 | 4.00000000000000 | 20.0000000000000 | PB - Operation | None |  | None | None | 17/12/2025 | 21/12/2025 | 23/12/2025 | 23/12/2025 | 21/12/2025 | 17/12/2025
1 | Personnel protection to be modelled for these lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | 2&quot;-DFC-F3N-1833-PP 2&quot;-DFC-F3N-1836-PP 2&quot;-DFC-F3N-1837-PP 2&quot;-PC-F3N-2746-PP 3&quot;-DFC-F3N-1832-PP | 0341C | 13/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Access requirement to instruments on compressor skid to be confirmed with vendor - access blocked by issued piping. Check if instrument arrangement can be relocated. | 20DEC25 - Access to the Instrument Panel is available | KBR | MECH | Pending PB Reply | 19/12/2025 | None |  | None | None | MECH | None | 29Dec2025_Cleared. Instrument rack turned by 180 degrees. Access no longer obstructed. | M-05 |  | E1A4774680_A-transmitter rack _ panel 4&quot;-W-B10-3165-NI | 0342C | 12/02/2026 | 9.00000000000000 | 11.0000000000000 | PB - Operation | None |  | None | None | 22/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 22/12/2025
1 | Vent to be added to piping if no vent is provided on vendor nozzle side. To confirm with Siemens | 20DEC25- Vent Added | KBR | PIP | Pending PB Reply | 19/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | DCN required | M-05 |  | 4"-W-B10-3169-NI | 0343C |  | 3.00000000000000 | 17.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 22/12/2025 | 25/12/2025 | 11/01/2026 | 11/01/2026 | 25/12/2025 | 22/12/2025
1 | 1. Vorecon drain valve to be modelled on piping 2. Vorecon drain tapping to be moved to Aft side of Vorecon tank (to be confirmed with Vendor that aft tapping should be used) | 24NOV25-Model Updated | KBR | PIP | CLOSE | 23/11/2025 | PIPER |  | Agree to close - Pending Seatrium Reply | None | PIP | None | No piping DCN required | M-05 | 01/12/2025 | 2"-DFC-B9-XXXX-NI | 0344C |  | 4.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 26/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 26/11/2025
1 | 1. Trunnion and pipe reinforcement pads overlapping to be fixed 2. Line stop on trunnion to be checked | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | SP-M05-32859 | 0345C | 14/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Vent to be added as marked for filling purpose - to be checked with process (typical for all three trains) | 28NOV25 : Vent connection added | KBR | PIP | Pending PB Reply | 27/11/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | No piping DCN required | M-05 |  | W-3177 | 0346C |  | 20.0000000000000 | 22.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 30/11/2025 | 20/12/2025 | 11/01/2026 | 11/01/2026 | 21/12/2025 | 30/11/2025
1 | Spectacle blind to be modelled | 24Nov25: Spectacle Blind Removed in AFC P&ID. | KBR | PIP | CLOSE | 23/11/2025 | PIPER | 01/12/2025 | Agreed between PB Operation, Piping, and SEATRIUM | None | PIP | None | No piping DCN required | M-05 | 01/12/2025 | ESP-12310548 2&quot;-DFC-B9-1992-NI | 0347C |  | 4.00000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 26/11/2025 | 30/11/2025 | 02/12/2025 | 02/12/2025 | 30/11/2025 | 26/11/2025
1 | Line to be connected to the header, typical for all 3 trains | 09JAN26 : Line no. 4"-DFC-B9-0190-NI connected to the Main Header. | KBR | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PIP | None | None | M-05 |  | 4"-DFC-B9-0190-NI | 0348C | 14/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
1 | Spec blind to be deleted, does not exist on P&ID | 04DEC25 - Spectale Blind Deleted. | KBR | PIP | Pending PB Reply | 03/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | No piping DCN required | M-05 |  | 2"-PC-E16N-2587-NI | 0349C |  | 14.0000000000000 | 22.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 06/12/2025 | 20/12/2025 | 11/01/2026 | 11/01/2026 | 21/12/2025 | 07/12/2025
2 | Check the slope requirements for this line. P&ID indicates a slope toward the production header which may not be met. Ref. I-DE-3010.2S-1231-944-S2N-001 | 24Dec25 : As discussed with KBR Process Low point Drain is provided. | KBR | PIP | Pending PB Reply | 23/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | no piping DCN required | M-05 |  | 4"-PC-C16N-0310-NI | 0350C |  | 2.00000000000000 | 14.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 26/12/2025 | 28/12/2025 | 11/01/2026 | 11/01/2026 | 28/12/2025 | 28/12/2025
2 | Personnel protection to be provided on this line | 22Dec25- PP updated as per the P&ID | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | DCN required | M-05 |  | 8"-PC-E3N-0160-NI | 0351C |  | 1.00000000000000 | 17.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 24/12/2025 | 25/12/2025 | 11/01/2026 | 11/01/2026 | 25/12/2025 | 24/12/2025
2 | Tapping sequence not as per P&ID - to be checked with process. Typical for all 3 trains | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | PC-0587 | 0352C | 25/01/2026 |  |  | SEA/KBR | None |  | None | None
2 | FO modelled as spec blind to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | PC-0587 | 0353C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Check the free draining requirement for this line P&amp;ID I-DE-3010.2S-1231-944-S2N-002 | Noted, as the exchanger is located at higher elevation, free draining seems not possible. Piping to provide PUN markup to remove free draining requirement. | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M-05 |  | 20"-PC-E30N-0342-NI | 0354C |  | -1.00000000000000 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
3 | Drains to be provided downstream of both the check valves, to confirm with Process. Typ. for all trains. P&amp;ID I-DE-3010.2S-1231-944-S2N-002 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | 20"-PC-E30N-0342-NI | 0355C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
3 | PDIT to be moved further away from strainer | 04DEC2025-PDIT Tapping is shifted further away from the T-strainer. | KBR | PIP | Pending PB Reply | 04/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | No piping DCN required | M-05 |  | 24"-PC-C12N-0573-NI | 0356C |  | 13.0000000000000 | 22.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 07/12/2025 | 20/12/2025 | 11/01/2026 | 11/01/2026 | 21/12/2025 | 07/12/2025
3 | Instrument tappings and valves to be modeled for Venturi flowmeter | 24DEC25- Instrument Tappings Modeled. | KBR | PIP | Pending PB Reply | 23/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | no piping DCN required | M-05 |  | 24"-PC-C12N-0573-NI | 0357C | 23/12/2025 | 6.00000000000000 | 10.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 26/12/2025 | 01/01/2026 | 11/01/2026 | 11/01/2026 | 01/01/2026 | 28/12/2025
3 | I-DE-3010.2S-1231-944-S2N-015 note 78 stating "THE CONNECTIONS OF SDV-1231058A/C-2 SHALL BE LOCATED IN THE LOWER GENERATRIX OF THE PIPING." to be removed or updated as horizontal connection is agreed. Typical for all trains. | None | KBR | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-05 |  | 2"-PC-E3N-0353-NI | 0358C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Provide confirmation from vendor that total length of vent between oil mist eliminator and safe vent location is acceptable considering pressure drop. P&ID I-DE-3010.2S-1231-944-S2N-018 note to be updated accordingly after vendor confirmation. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | 6"-OL-B3-0118-NI | 0359C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure extinguisher operating space is clear of the coaming | 04-12-25: Safety equipment shifted to avoid coaming clash. | KBR | PIP | Pending Seatrium Reply | 03/12/2025 | None |  | None | None | PIP | None | None | M-04 |  | Z-5428433 | 0360C |  | 35.0000000000000 |  | PB - Operation | None |  | None | None | 06/12/2025 |  |  |  |  | 07/12/2025
1 | Valve at safety shower to be modelled (typical for all safety showers in M04) | 12-12-25: Safety shower model updated. | KBR | PIP | Pending Seatrium Reply | 11/12/2025 | None |  | None | None | SAF | None | None | M-04 |  | Z-5434334 | 0361C |  | 27.0000000000000 |  | PB - Operation | None |  | None | None | 14/12/2025 |  |  |  |  | 14/12/2025
2 | Marginally exceding maximum distance between hydrant and locker box - to be reviewed. Ref. TQF-P84P85-YCT-BE-HUL-SAF-0064 | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | Z-H-5423020 H-5423020 | 0362C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Instrument stand to be relocated away from safety shower entrance | None | KBR | CSE | OPEN | 27/11/2025 | None |  | None | None | CSE | None | None | M-04 |  | SPI-M04-206 | 0363C | 29/01/2026 | 41.0000000000000 |  | PB - Operation | None |  | None | None | 30/11/2025 |  |  |  |  | 30/11/2025
4 | Hydrant operating volume to be clear of obstruction from coaming | 04-12-25: Coaming and drain pit shifted FWD to avoid hydrant volume clash. | KBR | PIP | Pending Seatrium Reply | 03/12/2025 | None |  | None | None | PIP | None | None | M-04 |  | H-5423189 | 0364C |  | 35.0000000000000 |  | PB - Operation | None |  | None | None | 06/12/2025 |  |  |  |  | 07/12/2025
4 | Handling volume through hydrant to be updated | 04-12-25: Handling volume model update. | KBR | PIP | Pending PB Reply | 03/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 26Dec2025_Cleared. | M-04 |  | H-5423189 | 0365C | 23/01/2026 | 22.0000000000000 | 14.0000000000000 | PB - Operation | True | 07/01/2026 | True | None | 06/12/2025 | 28/12/2025 | 09/01/2026 | 11/01/2026 | 28/12/2025 | 07/12/2025
1 | Instrument air supply piping to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | 2&quot;-IA-B3-1002-NI 1&quot;-IA-B3-1003-NI 1&quot;-IA-B3-1028-NI | 0366C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Closed drain tie-in to be connected. Handling volume to be modified to avoid interference with drain line | 19-12-25: Model updated. | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | 09-01-26_B1YR_CLOSE | PIP | None | No piping DCN required | M-04 |  | 2"-DFC-B9-1823-NI | 0367C |  | 4.00000000000000 | 17.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 21/12/2025 | 25/12/2025 | 11/01/2026 | 11/01/2026 | 25/12/2025 | 21/12/2025
2 | Bypass line routing to be completed | 31-12-25: Bypass line routing updated. | KBR | PIP | Pending PB Reply | 30/12/2025 | None |  | None | 09-01-26_B1YR_CLOSE | PIP | None | no piping dcn required | M-04 |  | 2"-P-E6N-8351-NI | 0368C |  | 2.00000000000000 | 7.00000000000000 | PB - Operation | True | 09/01/2026 | True | None | 02/01/2026 | 04/01/2026 | 11/01/2026 | 11/01/2026 | 04/01/2026 | 04/01/2026
2 | Drain to be relocated in line with P&ID. Length of drain to be shortened. (typical for all M04 drip legs) | 05-01-26: Drain model updated. | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | B1YR - WORKING | PIP | None | no piping dcn required | M-04 |  | None | 0369C |  | 1.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
2 | Line size to be updated after receiving revised vendor PID | 10-12-25: Piping size updated 4" as per latest vendor PID REV-E. | KBR | PIP | Pending PB Reply | 09/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-04 |  | P-8030 P-8130 P-8230 | 0370C |  | 8.00000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 12/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 14/12/2025
2 | AIT valves to be updated in Instrument catalogue and shown in model | None | KBR | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-04 |  | None | 0371C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Pipe routing to header to be completed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | 2"-DFC-B9N-8009-NI | 0372C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Drain and vent piping from drip leg to be connected | 11-12-25: Model updated Non permeate line drain to drip leg and drip leg vent to Non permeate feed line are connected. | KBR | PIP | Pending PB Reply | 10/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-04 |  | 1&quot;-P-E6N-8240-NI 1&quot;-P-E6N-8140-NI 1&quot;-P-E6N-8040-NI 20&quot;-P-E6N-8277-NI 10&quot;-P-E6N-8237-NI | 0373C |  | 7.00000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 13/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 14/12/2025
2 | Drain connections to be modeled - typical for all trains | 31-12-25: Drain model updated. | KBR | PIP | Pending PB Reply |  | None |  | None | None | PIP | None | no piping dcn required | M-04 |  | None | 0374C |  |  | 6.00000000000000 | PB - Operation | None |  | None | None |  | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026
2 | High point vent to be modeled | 04-12-25: HPV model updated. | KBR | PIP | Pending PB Reply | 03/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-04 |  | 12"-P-E6N-8023-NI | 0375C |  | 14.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 06/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 07/12/2025
3 | PSV inlet lines to be updated with transvere direction slope 0.5%, AFT to FWD 2.5% | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | None | 0376C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Piping to be connected | 10-12-25: Model updated. | KBR | PIP | Pending PB Reply | 09/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-04 |  | None | 0377C |  | 8.00000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 12/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 14/12/2025
3 | Drain connection to be modeled - typical for all threee trains | 12-12-25: Drain updated. please refer attached snap. 31-12-25: Draing shifted to lowest point near valve. | KBR | PIP | Pending PB Reply | 30/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M-04 |  | None | 0378C |  | 3.00000000000000 | 5.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 05/01/2026 | 07/01/2026 | 07/01/2026 | 05/01/2026 | 04/01/2026
3 | Vent discharge to be minimum 3m above deck | 31-12-25: Vent lines model updated terminated 3m from level-4. | KBR | PIP | Pending PB Reply | 30/12/2025 | None |  | None | None | PIP | None | no piping DCN required | M-04 |  | 2&quot;-F-B10-8010-NI 2&quot;-F-B10-8014-NI 2&quot;-F-B10-8018-NI | 0379C |  | 2.00000000000000 | 6.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | FIT tag numbers to be corrected | 10-12-25: Piping model updated with FIT tags. Clash to be resolved by INST team. 08-01-26: INST. panel is relocated. | KBR | CSE | OPEN | 07/01/2026 | None |  | None | None | CSE | None | None | M-04 |  | None | 0380C | 29/01/2026 | 0 |  | PB - Operation | None |  | None | None | 10/01/2026 |  |  |  |  | 11/01/2026
3 | SDV to be moved portside to provide adequate clearance from instrument connection | 31-12-25: SDV shifted and panel orientation changed, clearance available. | KBR | PIP | Pending PB Reply | 30/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M-04 |  | None | 0381C |  | 3.00000000000000 | 5.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 05/01/2026 | 07/01/2026 | 07/01/2026 | 05/01/2026 | 04/01/2026
4 | TIT-1231048 to be modeled | 04-12-25: TIT-1231048 model updated. | KBR | PIP | Pending PB Reply | 03/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-04 |  | None | 0382C |  | 14.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 06/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 07/12/2025
4 | BDV inlet lines to be connected | 10-12-25: Model updated. Please refer latest snap. 31-12-25: Piping modified. Please refer attached snap. | KBR | PIP | RE-OPEN | 30/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M-04 |  | 4"-P-E6N-8281-NI | 0383C |  | 2.00000000000000 | 6.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
4 | Sampling piping to be modeled | 10-12-25: Sampling piping model updated. 31-12-25: Valve shifted near to process line tapping. | KBR | PIP | Pending PB Reply | 30/12/2025 | None |  | None | None | PIP | None | nonpiping DCN REQUIRED | M-04 |  | None | 0384C |  | -13.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 04/01/2026
4 | Spectacle blind to be updated | 04-12-25: Spectacle blind updated in model. | KBR | PIP | Pending PB Reply | 03/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-04 |  | None | 0385C |  | 14.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 06/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 07/12/2025
3 | 4"-PC-C3N-0306-NI to change to 4"-PC-C16N-0286-PP after the VALV-12311158 | 04dec25 - Model updated as per the comment | KBR | PIP | Pending PB Reply | 03/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | DCN required | M-05 |  | 4&quot;-PC-C3N-0306-NI 4&quot;-PC-C16N-0286-PP VALV-12311158 | 0386C |  | 14.0000000000000 | 22.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 06/12/2025 | 20/12/2025 | 11/01/2026 | 11/01/2026 | 21/12/2025 | 07/12/2025
3 | Support location and valve location to swap position - check valves to be closer together | 25NOV25: Model updated as per the comment | KBR | PIP | Pending PB Reply | 24/11/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | No piping DCN required | M-05 |  | None | 0387C |  | 23.0000000000000 | 22.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 27/11/2025 | 20/12/2025 | 11/01/2026 | 11/01/2026 | 21/12/2025 | 27/11/2025
3 | Valve arrangement to be updated to provide accessibility | 10Jan26 : Valve accessibility Provided and model updated | KBR | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PIP | None | None | M-05 |  | None | 0388C | 18/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
3 | Confirm with process the location of PSEs considering the minimum distance requirement on P&ID and update P&ID note. (typ. for all coolers) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | None | 0389C | 18/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Pipe sleeve inside coaming to be selected as sealed type as per piping practices - total sleeve height 250mm (catalogue to be updated). Typical for all coolers in Level 3. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | None | 0390C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Check the requirement for drain between SDV and check valve with Process | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | VALV-12310010 PC-0730 | 0391C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
3 | FO to be modeled | 04DEC25- FO Added and Model updated. | KBR | PIP | Pending PB Reply | 03/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | No piping DCN required | M-05 |  | None | 0392C |  | 14.0000000000000 | 22.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 06/12/2025 | 20/12/2025 | 11/01/2026 | 11/01/2026 | 21/12/2025 | 07/12/2025
3 | Pup piece to be deleted and valve welded directly to sockolet | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | VALV-12310779 VALV-12311080 VALV-54120400 VALV-54120404 VALV-12310983 | 0393C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
None | CCTV (height-3m) and JB to be relocated together 90 degree (west side) and speaker to east side as per mark-up. Gas detectors (F&G) to move-up to adjust with the CCTV relocation | 07-01- CCTV and JB has been relocated as well as speaker is moved to east side as per mark up | KBR | TEL | RE-OPEN | 06/01/2026 | None |  | None | None | TEL | None | None | M13 |  | CAM-5514071 AST-CH4-M13-101-013 | 10126C | 28/01/2026 | 1.00000000000000 |  | PB - Engineering | None |  | None | None | 09/01/2026 |  |  |  |  | 11/01/2026
None | Power Cable ladder to be adjusted to improve the power cable bending radius. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13 |  | TT-M13-L-E-TRAY-10003 | 10127C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
None | If nearby Structure is permanent, Speaker to be relocated to it. If not leave as it is. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13 |  | COR-5518314A COR-5518314B COR-5518315A COR-5518315B | 10128C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Relocate the speaker to the edge as per mark up | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13 |  | COR-5518311A | 10129C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the F&G equipment to the edge to avoid speaker | None | KBR | TEL | OPEN |  | None |  | None | None | SAF | None | None | M13 |  | AST-CH4-M13-101-011 | 10130C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the equipment for better cabling | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13 |  | COR-55183168 | 10131C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Move the speaker inside the platform | The speaker has been moved as per the markup. | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | 09.01.2026_U4EW_PB operation agrees with the solution. | TEL | None | None | M13 |  | SPP-M13-00068 | 10132C | 28/01/2026 | 3.00000000000000 | 0 | PB - Engineering | True | 09/01/2026 | True | None | 08/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
None | Move the beacon inside the platform | The Beacon has been moved as per the snapshot. | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | S09.01.2026_U4EW_ In the last 3D document provided to PB operation team, the SPP-M13-00139 wasn´t found in the 3D model and the selection three. Also wasn´t the equipament below the support. | TEL | None | None | M13 |  | SPP-M13-00139 | 10133C | 28/01/2026 | 3.00000000000000 | 0 | PB - Engineering | True | 08/01/2026 | False | None | 08/01/2026 | 11/01/2026 | 10/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
None | Move the speaker inside the platform | The speaker has been moved inside the platform as per the snapshot. | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | 09.01.2026_U4EW_PB operation team agrees with the solution. | TEL | None | None | M13 |  | SPP-M13-00088 | 10134C | 28/01/2026 | 3.00000000000000 | 0 | SEA/KBR | True | 09/01/2026 | True | None | 08/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
None | Move the speaker inside the platform | The speaker has been moved inside the platform as per the snapshot. | KBR | TEL | RE-OPEN | 05/01/2026 | None |  | None | None | TEL | None | None | M13 |  | SPP-M13-00085 | 10135C | 28/01/2026 | 2.00000000000000 |  | SEA/KBR | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | Combine the BLE with the speaker pole | The BLE is combined with the speaker pole. | KBR | TEL | RE-OPEN | 05/01/2026 | None |  | None | None | TEL | None | None | M13 |  | BLE-5511270 | 10136C | 28/01/2026 | 2.00000000000000 |  | PB - Engineering | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | Combine the BLE with the speaker pole | The BLE is combined with the speaker pole. | KBR | TEL | RE-OPEN | 05/01/2026 | None |  | None | None | TEL | None | None | M13 |  | BLE-5511271 | 10137C | 28/01/2026 | 2.00000000000000 |  | PB - Engineering | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | CCTV (height-3m) and JB to be relocated together 90 degree (west side) and speaker to east side as per mark-up. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | CAM-5514070 | 10138C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Reduce the tray as per mark up | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | TT-M12-L-E-TRAY-00001 TT-M12-L-E-TRAY-00002 | 10139C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Reduce the tray as per mark up | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | TT-M12-S-B-TRAY-00001 | 10140C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the speaker and extend the support | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | COR-5518289A | 10141C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate the speaker | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | COR-5518289B | 10142C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Check the beacon location based on study and adjust the beacon elevation | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | LSE-5518036A | 10143C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Speaker to be relocated as per mark-up. | Speaker is relocated as per markup | KBR | TEL | Pending PB Reply | 04/01/2026 | None |  | None | None | TEL | None | None | M12 |  | COR-5518499A | 10144C | 28/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Engineering | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
None | Speaker to be relocated as per mark-up. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | COR-5518294B | 10145C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Speaker to be relocated as per mark-up. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | COR-5518298A | 10146C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Secondary trays are missing for Telecom equipment. General for M12. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | PA-5517036 | 10147C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Speaker to be relocated as per mark-up. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M12 |  | COR-5518298B | 10148C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Beacon to be relocated so that can be seen from corridor | Beacon is moved as per markup | KBR | TEL | RE-OPEN | 04/01/2026 | None |  | None | None | TEL | None | None | M12 |  | SPP-M12-00067 | 10149C | 28/01/2026 | 3.00000000000000 |  | PB - Engineering | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
None | Secondary trays are missing for Telecom equipment. General for M13. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M13 |  | General | 10150C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Guard rail design to suit the accessibility for the GTG junction box. (See possibility of removing the guard rail, structural discipline to advise.), If this can be remove, the same should be evaluate for M13B and M13 as well. | Guard rail updated | KBR | STR | RE-OPEN | 28/12/2025 | None |  | None | None | STR | None | None | M12 |  | Handrail Element-7-2788 Handrail Element-7-2762 | 10151C | 18/01/2026 | 0 | 10.0000000000000 | PB - Operation | None |  | None | None | 31/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 31/12/2025
None | Adjust HV tray to AFT side (as much as possible) and align to MCT location and GTG terminal box. Proper cable bending to be ensured in the proposed close-out. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M12 |  | ET-M12-H-TRAY-05000-TRAY-0023 | 10152C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Resolve overlapping of valve and cable tray. | Valve is outside of the cable tray now. | KBR | PIP | Pending PB Reply | 23/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M12 |  | Blind Flange-6460 | 10153C |  | 0 | 15.0000000000000 | PB - Engineering | None |  | None | None | 26/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025
None | Adjust pipe location to ensure lighting is not obstructed. | The Light Fixture location is updated to avoid pipe obstrcution | PB | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 04-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M12 |  | LEM-344-01-M12-002 | 10154C |  | 16.0000000000000 | 4.00000000000000 | PB - Engineering | None |  | None | None | 21/12/2025 | 06/01/2026 | 08/01/2026 | 08/01/2026 | 06/01/2026 | 21/12/2025
None | Speaker/lighting to adjust, ensuring both cable entries are not obstructed. | Light Fixture relocated to have better cable termination space | SEA | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 04-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M12 |  | LEM-344-01-M12-003 | 10155C |  | 16.0000000000000 | 4.00000000000000 | SEA/KBR | True |  | None | None | 21/12/2025 | 06/01/2026 |  |  | 06/01/2026 | 21/12/2025
None | JB or safety box to be adjusted, cable entry to JB (bottom) shall not be obstructed. | JB Mounting Height is increased and minimum cable entry distance is maintained. | SEA | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 04-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M12 |  | CXE-L-M12-304 | 10156C |  | 16.0000000000000 | 4.00000000000000 | SEA/KBR | True |  | None | None | 21/12/2025 | 06/01/2026 |  |  | 06/01/2026 | 21/12/2025
None | Move light fixture inside guard rail. | The Light Fixture location is updated. | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 04-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M12 |  | LEM-344-01-M12-004 | 10157C |  | 16.0000000000000 | 4.00000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 06/01/2026 |  |  | 06/01/2026 | 21/12/2025
None | Lighting to be checked if can be mounted on the pipe support. JB and piping below to be modified to avoid obstruction on cable entries to the JB. | The Light Fixture attached with pipe support, Lighting JB's and its trays are updated. | PB Ops | ELE | RE-OPEN | 18/12/2025 | None |  | None | None | ELE | None | None | M12 |  | CXE-L-M12-205 LEM-344-02-M12-001 | 10158C |  | 16.0000000000000 | 4.00000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 06/01/2026 | 08/01/2026 | 08/01/2026 | 06/01/2026 | 21/12/2025
None | Relocate light fixture away from pipe/flange below. | Light Fixture moved from handrail and mounted in the nearby structure. | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M12 |  | LEM-344-02-M12-002 | 10159C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Adjust floodlight/tray, rotation/movement of floodlight should not be obstructed by the tray location. Both model to be adjusted accordingly. | light fixture relocated to avoid obsrction from the cable tray | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M12 |  | LNO-222-04-M12-001 | 10160C |  | 2.00000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 21/12/2025
None | Shift small bore pipes away from lighting location to resolve lighting accessibility/maintainability issues. | 1-1/2"-F-B3-1755-NI routing has been modified. | KBR | PIP | RE-OPEN | 23/12/2025 | None |  | None | None | PIP | None | no piping DCN required | M12 |  | LNO-222-07-M12-001 | 10161C | 22/01/2026 | 0 | 15.0000000000000 | PB - Operation | None |  | None | None | 26/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025
None | Shift small bore pipes away from lighting location to resolve lighting accessibility/maintainability issues. | Piping has been shifted away from lighting. | KBR | PIP | Pending PB Reply | 23/12/2025 | None |  | None | None | PIP | None | no piping DCN required | M12 |  | LNO-222-05-M12-006 | 10162C |  | 0 | 15.0000000000000 | PB - Operation | None |  | None | None | 26/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025
None | Re-arrange JB on same column, one on top of the other, ensuring no obstruction to cable entries to JB. | We have updated the tray route to accomodate the cables to respective JB's. | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 04-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M12 |  | CXE-L-M12-201 CXE-L-M12-302 | 10163C |  | 16.0000000000000 | 4.00000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 06/01/2026 |  |  | 06/01/2026 | 21/12/2025
None | Shift JBs up, approximately 1.7m mounting height, tray to be adjusted accordingly. | We have updated the JB's and Tray locations (1500mm)., due to Pipe support obstruction. | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 04-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M12 |  | CXE-L-M12-202 CXE-L-M12-307 | 10164C |  | 16.0000000000000 | 4.00000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 06/01/2026 |  |  | 06/01/2026 | 21/12/2025
None | Rotate JB to provide access to the valve behind. | Jb orientation updated. | PB Ops | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M12 |  | CXN-L-M12-007 | 10165C |  | 9.00000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 14/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 14/12/2025
None | Modify tray and locate approximately 300mm below the JB. | Modified cable tray and re-located approximately 300mm below the JB. | PB Ops | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M12 |  | SPS-M12-010 | 10166C |  | 9.00000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 14/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 14/12/2025
None | Shift JB to opposite side of column. | The Lighting JB Location is updated. | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 04-JAN-2026 SEA REMARKS: SEE KBR ACTION COMMENT) NOTE: ENSURE THAT THE CABLE TRAY FOR JB IS PROPERLY CONNECTED UNTIL THE CABLE TERMINATION POINT. | M12 |  | CXE-L-M12-317 | 10167C |  | 16.0000000000000 | 4.00000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 06/01/2026 |  |  | 06/01/2026 | 21/12/2025
None | Shift JB up, mounting height approximately 1.7m at same column/position. | Lighting JB location updated. | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 04-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M12 |  | CXE-L-M12-309 | 10168C |  | 16.0000000000000 | 4.00000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 06/01/2026 |  |  | 06/01/2026 | 21/12/2025
None | Re-orient JB to ensure accessibility (at same area). | Lighting JB location updated. | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 04-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M12 |  | CXE-L-M12-311 | 10169C |  | 16.0000000000000 | 4.00000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 06/01/2026 |  |  | 06/01/2026 | 21/12/2025
None | Re-evaluate the HV tray and MCT configuration below the GTG phase terminal box. | None | KBR | ELE | OPEN |  | None |  | None | None | ELE | None | None | M12 |  | ET-M12-H-TRAY-05001-TRAY-0222 | 10170C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | To provide the addition of cable trays for each JB at a distance of approximately 300mm | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M12 |  | Refer to Snapshot 2 | 10171C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | To provide trimmer for JB supports | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M12 |  | SPI-M12-201 | 10172C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | To relocate the cable tray penetration | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M12 |  | I-M12-S-PEN-202 | 10173C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Cable tray model should be moved to M-16 Hierarchy | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M12 |  | IT-M12-S-I-TRAY-01012 IT-M12-S-I-TRAY-01008 | 10174C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | To check the cable bending radius and standardization of Tele JB cable trays installation. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M11 |  | IT-M11-S-A-TRAY-00001 | 10175C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | To clear the JB opening/maintenace space | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M11 |  | CCD-5514113 | 10176C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Secondary trays are missing for Telecom equipment. General for M11. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M11 |  | General | 10177C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | To relocate the BLE | BLE is relocated as per study mapping | KBR | TEL | RE-OPEN | 04/01/2026 | None |  | None | None | TEL | None | None | M11 |  | BLE-5511224 | 10178C | 28/01/2026 | 0 | 3.00000000000000 | PB - Engineering | None |  | None | None | 07/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 07/01/2026
Level 3 | Move speaker to inside of platform | Speaker relocated as per markup | KBR | TEL | RE-OPEN | 04/01/2026 | None |  | None | None | TEL | None | None | M11 |  | SPP-M11-00050 | 10179C | 28/01/2026 | 3.00000000000000 |  | PB - Engineering | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
Level 3 | Move the equipment to inside the platform | POB is moved inside the platform as per markup | KBR | TEL | Pending PB Reply | 04/01/2026 | None |  | None | None | TEL | None | None | M11 |  | SPP_M11-00075 | 10180C | 28/01/2026 | 0 | 3.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 07/01/2026
Level 3 | Move the equipment to inside the platform | The speaker has been moved inside the platform as per the markup | KBR | TEL | Pending PB Reply | 04/01/2026 | None |  | None | None | TEL | None | None | M11 |  | COR-5518285B | 10181C | 28/01/2026 | 0 | 3.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 07/01/2026
Level 1 | To update cable tray penetration as per the vendor drawing | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | I-M11-S-MCT-001 I-M11-S-MCT-002 | 10182C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | To add the vertical cable tray | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | JBC-1422-002 JBC-1422-001 JBC-1422-006 JBC-1422-007 | 10183C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Cable tray penetration to be placed to have enough space for bolting to FRP grating | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | I-M11-S-PEN-207 I-M11-S-PEN-208 | 10184C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Evaluate rotating panel PN-5520111 so that rear has permanent platform access, please make penetration to match the MCT in panel after rotation | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | PN-5520111 | 10185C | 29/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | To provide support for bending radius cable tray as per the standard specification | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | IT-M11-S-I-TRAY-01027 | 10186C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | KBR tie-in point sould match with vendor tie-in point for equipment: B-1251001A/B/C | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | B-1251001A/B/C | 10187C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1M | 2 FIT to relocate to allow access to handwheel | 2 FIT are relocated. | KBR | CSE | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | INST | None | None | M11 |  | FIT-1251003C FIT-1251004C | 10188C | 29/01/2026 | -1.00000000000000 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
General | Modify penetration to follow structural guidelines. Typical for all FRP grating | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | I-M11-S-PEN-216 (General) | 10189C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Trays shall be modelled showing complete connectivity. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | General | 10190C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Transmitter is far from tapping. One of the following solutions needs to be adopted to bring the transmitter closer to the Tapping point: a) the position of transmitter needs to be reevaluated b) Integral mounted transmitter is to be evaluated. c) diaphragm seal needs to be considered | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | PDIT-1251012A, SPI-M11-256 PDIT-1251012B, SPI-M11-275 PIT-1251004A, SPI-M11-258 PIT-1251002 | 10191C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
General | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all Instruments, JB and valves M11. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M11 |  | General | 10192C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Relocate instrument nearby tapping point | The instrument is moved to nearest the tapping point. | KBR | CSE | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | INST | None | None | M11 |  | T-02-PIT-1251024C | 10193C | 29/01/2026 | -1.00000000000000 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
None | Transmitter is far from tapping. One of the following solutions needs to be adopted to bring the transmitter closer to the Tapping point: a) the position of transmitter needs to be reevaluated b) Integral mounted transmitter is to be evaluated. c) diaphragm seal needs to be considered | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M12 |  | PIT-5147018E PIT-5147018F PIT-5147024E PIT-5147024F PIT-5147830F FIT-5147804F PIT-5147830E FIT-5147804E PIT-5147012F PIT-5147014E PIT-5125001 PIT-5147012E PIT-5147011F PIT-5147011E PIT-5147014F PIT-5125003 PIT-5147008E PIT-5147008F FIT-5125004E FIT-5125004F PDIT-5147010E PDIT-5147010F | 10194C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
General | Modify penetration to follow structural guidelines. Typical for all FRP grating. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M12 |  | General | 10195C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Trays shall be modelled showing complete connectivity. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M12 |  | General | 10196C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Modify the firewater pipe & fusible plug tubing to clear filter maintenance. | None | PB Ops | PIP | OPEN |  | None |  | None | None | INST | None | None | M11 |  | 1"-FW-B7-1558-NI | 10197C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Lighting fixture to adjust location and move towards front side of panel. | Light fixture Moved Towards Front of the panel | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M11 |  | LEM-343-01-M11-004 | 10198C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
Level 1 | JB/lighting to be checked if falling inside material handling volume. Revise model (JB or handling route space reserve) accordingly. | Light fixture & Junction box relocted to avoid material handling volume. | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M11 |  | CXN-L-M11-052 LNO-221-09-M11-007 | 10199C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
Level 1 | Extend tray to bottom area of the JB. | Electrical Tray has been extended | PB Ops | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M11 |  | CXE-L-M11-303 | 10200C |  | 20.0000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 03/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 03/12/2025
None | Pipe to relocate and avoid escape route volume reserve. | None | PB Ops | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | DA-0003 | 10201C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Adjust/relocate/rotate tray support in front of the floodlight, to avoid obstructing light throw from floodlight. | light fixture moved to web of the column and to avoid obstruction from cable tray support | SEA | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M11 |  | LES-308-04-M11-002 | 10202C |  | 4.00000000000000 | 16.0000000000000 | SEA/KBR | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
Level 1 | Adjust/relocate/rotate tray support in front of the floodlight, to avoid obstructing light throw from floodlight. | Flood light fixture relocated to avoid cable tray obstruction | PB | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 06-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M11 |  | LNO-221-06-M11-002 | 10203C |  | 12.0000000000000 | 2.00000000000000 | PB - Engineering | None |  | None | None | 27/12/2025 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 28/12/2025
Level 2 | Slightly adjust light fixture to AFT side mounted on same column, just enough space for welding to be maintained. | Light Fixture has been updated (Moved to AFT side) | PB Ops | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M11 |  | LES-308-06-M11-006 | 10204C |  | 20.0000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 03/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 03/12/2025
Level 2 | Adjust floodlight location to a position where there is no obstruction. | Lighting fixture location is updated beased on updated Lighting Calculation and presnt postion is not having any obsturction | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M11 |  | LNO-221-07-M11-001 | 10205C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
None | Lower the lighting fixture elevation to avoid large bore pipe as obstruction. | lighting fixture elevation changed to avoid large bore pipe obstruction. | PB Ops | ELE | RE-OPEN | 18/12/2025 | None |  | None | None | ELE | None | None | M11 |  | MNO-221-09-M11-009 | 10206C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 21/12/2025
Level 2M | Relocate JB/lighting to accessible location. | Lighting JB relocated nearest column to have better access | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M11 |  | CXE-L-M11-336 | 10207C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Vendor to model missing branch sub-tray. Clamping model to be corrected. | Awaiting a response from Vendor Veolia | SEA | MECH | OPEN |  | None |  | None | None | VEOLIA | None | None | M11 |  | LNO-221-14-M11-001 | 10208C | 18/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Vendor light fixture position to be updated based on mark-up. Floodlight JB to be adjusted and ensure its accessibility. | Awaiting a response from Vendor Veolia | PB | MECH | RE-OPEN | 14/12/2025 | None |  | None | None | ELE | None | None | M11 |  | CXN-L-M11-050 | 10209C | 18/02/2026 | 6.00000000000000 | 19.0000000000000 | PB - Engineering | None |  | None | None | 17/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 17/12/2025
None | Relocate lighting to avoid overlap with handling volume. Evaluate best position for this lighting fixture. | The light fixture has been removed, and the required lux level is achieved using the remaining fixtures. | PB Ops | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 06-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M11 |  | LEM-342-06-M11-003 | 10210C |  | 12.0000000000000 | 2.00000000000000 | PB - Operation | True |  | None | None | 27/12/2025 | 08/01/2026 |  |  | 08/01/2026 | 28/12/2025
Level 1M | Mount JB away from escape/access way, but same column. | Lighting JB Relocated to avoid clash with access route | PB Ops | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 06-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M11 |  | CXE-L-M11-312 | 10211C |  | 12.0000000000000 | 2.00000000000000 | PB - Operation | True |  | None | None | 27/12/2025 | 08/01/2026 |  |  | 08/01/2026 | 28/12/2025
Level 1 | Move tray behind JB, ensure JB is not blocked for access. | Lighting JB (CXN-L-M11-010) relocated to have better access | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M11 |  | CXE-L-M11-010 | 10212C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Add vertical trays to ensure cable is properly supported. | Updated both panel vertical tray and properly supported in the panles. | PB Ops | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 06-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: KBR ELEC PROVIDED THE VERTICAL TRAY, THEY NEED TO ENSURE THE PROPER CONNECTIVITY OF TRAYS FOR SMOOTH CABLE TRANSITION. KBR MUST ENSURE THAT ALL EIT ITEMS ARE CLASHED FREE PRIOR TO THE ISSUANCE OF DELIVERABLES. | M11 |  | CXN-L-M11-421 CXN-L-M11-422 | 10213C |  | 12.0000000000000 | 2.00000000000000 | PB - Operation | True |  | None | None | 27/12/2025 | 08/01/2026 |  |  | 08/01/2026 | 28/12/2025
None | Evaluate lighting panel and big bore pipe location. There should be no pipe/flange close or on top of the lighting panel. | None | PB | PIP | OPEN |  | None |  | None | None | ELE | None | None | M11 |  | PCC-5263011B | 10214C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate/lift JB location to avoid obstructing access to pipe/flange behind. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M11 |  | CXE-L-M11-316 CXN-L-M11-031 | 10215C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Cable ladder to be adjusted as per mark-up snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | IT-M02-L-E-TRAY-00004 IT-M02-S-A-TRAY-00003 | 10216C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Modify the cable ladder to have proper bending radius at JB termination area | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | TT-M02-L-E-TRAY-10004 TT-M02-S-B-TRAY-00004 | 10217C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Relocate the cctv to marked area at 3 meters. Relocate lighting to 3.5 meters as per operations recommendation. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | CAM-5514005 LES-296-01-M02-001 | 10218C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Relocate the cctv to marked area at 3 meters. Relocate lighting to 3.5 meters as per operations recommendation. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | CAM-5514005 LES-296-01-M02-001 | 10219C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Provide proper bend for cable termination. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | TT-M02-S-A-TRAY-00007 | 10220C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Adjust the access point to edge of the structure and proper the cable trays. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | PA-5517004 | 10221C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Shift the light to edge of the structure on the left as marked to avoid blocking the cabling for access point | light fixture relocated to have better access for cable termination | SEA | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M-02 |  | SPL-M02-00012 | 10222C |  | 5.00000000000000 |  | SEA/KBR | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
General | Secondary trays are missing for Telecom equipment. General for M02. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | General | 10223C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Shift the CCD box to front side of cctv. | The CCD box has been shifted to the front side of the CCTV. | KBR | TEL | Pending PB Reply | 06/01/2026 | None |  | None | None | TEL | None | None | M-02 |  | CCD-5514103 | 10224C | 28/01/2026 | 2.00000000000000 | -1.00000000000000 | SEA/KBR | None |  | None | None | 09/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
Level 4 | Relocate speaker to avoid blocking the RIO panel | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | COR-5518034B | 10225C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Check if these penetrations are required. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | T-M02-S-PEN-201 T-M02-S-PEN-301 | 10226C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Equipment coaming to be removed on the penetration area. Typical for 3 skids. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | SS-M02-0002827 | 10227C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
General | To provide the addition of cable trays for each JB at a distance of approximately 300mm. Typical comment for all JBs When cables transition from behind the junction box (JB) to the front cable ladder, ensure that support members are arranged so they do not obstruct the cable route. Typical comment for all JBs | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | General | 10228C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
General | Modify penetration to follow structural guidelines. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | General | 10229C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | KBR to model and incorporate the necessary supports in accordance with the standard KBR typical drawings for all 90 deg Bends. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | IT-M02-S-I-TRAY-01005-TRAY-0106 | 10230C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Utilise column mounted type of installation for single JB | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | JBIF-1412-006 | 10231C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Electrical avoid separate penetration near RIO panel location | Electrical separate penetration has been removed. | SEA | ELE | Pending PB Reply | 05/12/2025 | None |  | None | None | ELE | None | 15-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-02 |  | E-M02-L-PEN-405 | 10232C |  | 9.00000000000000 | 24.0000000000000 | SEA/KBR | True |  | None | None | 08/12/2025 | 17/12/2025 |  |  | 17/12/2025 | 08/12/2025
None | Vendor RIO MCT steel penetration should be in line. Typical for all 3 trains. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | PN-UC-1254001C-02 | 10233C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Update missing cable tray supports | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | TS-M02-AUTO-TRAY | 10234C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Clarify why the Tubing Flange Adaptor is not modelled. If these flange adaptors are only available in SPI for MTO extraction, please confirm how space is reserved in the 3D model for such flanges and how alignment between the Flange Adaptor and the piping interface flange is ensured. This is Typical comment, applicable to all such cases. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | FIT-1254027A-1 | 10235C | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Level Gauges Vent and drain valves to be modelled | None | SEA | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | LG-1254011A | 10236C | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | 4 tags of Gas Chromotograph Instrument Cable tray is not modelled | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | PN-AIT-1254003A | 10237C | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Transmitter is far from tapping. One of the following solutions needs to be adopted to bring the transmitter closer to the Tapping point: a) the position of transmitter needs to be reevaluated b) Integral mounted transmitter is to be evaluated. c) diaphragm seal needs to be considered Case by case stantion support to be lowered less than 800mm. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | PIT-1254087 PIT-1254060A/B/C PIT-1254061A PIT-1254012A_013A PIT-1254068A PIT-1254055A PIT-1254071B PIT-1254006B PIT-1254007B PIT-1254009B PIT-1254008B PIT-1254078B PIT-1254101B PIT-1254012B_013B PIT-1254072B PIT-1254006C_007C PIT-1254009C PIT-1254008C and TIT-1254021C PIT-1254078C_PIT-1254101C_TIT-1254049C PIT-1254072C PIT-1254012C_013C PIT-1254122B PIT-1254068A PIT-1254055A PIT-1254071C PIT-1254055A PIT-1254071A PIT-1254006A_007A PIT-1254080C PIT-1254081C_PIT-1254067C PIT-1254082C | 10238C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
General | Provide cable tray supports for all main instrumentation cable trays | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | General | 10239C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Provide Tray for long capillaries | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | PDIT-1254005A | 10240C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
General | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all Instruments, JB and valves M02. Also the Tray which running close to the deck is should be checked and routed above the coaming height. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | General | 10241C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
General | Model flushing ring for capillary type level transmitters | None | PB Ops | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | LIT-1254020A LIT-1254022A LIT-1254020B LIT-1254022B LIT-1254020C LIT-1254022C LIT-1254007A LIT-1254008A LIT-1254007B LIT-1254008B LIT-1254007C LIT-1254008C | 10242C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
General | Vendor model to align with tie-in tray from topside. Typical for all 3 skids | Awaiting info from Vendor Siemens | SE | MECH | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | EC-M02-L-N-TRAY-20005 (General) | 10243C | 17/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Penetration minimum gap from nearby beam to be observed based on structural typical standard. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | E-M02-L-PEN-211 | 10244C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Check penetration below package if required. If not required, based on structural profile below the package, delete them. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-02 |  | TS-M02-AUTO-PEN | 10245C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Update model showing combined penetration for electrical and instrument cables. Relevant structural beams to be updated to suit the penetrations from E&I. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | I-M02-S-PEN-408 | 10246C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Provide adequate access facility/structures for the terminal box (typical comment for 3 packages at level-1). | Awaiting a response from Vendor Siemens. | PB Ops | MECH | OPEN |  | None |  | None | None | Vendor | None | None | M-02 |  | None | 10247C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate the vendor JB to an accessible location. | Awaiting a response from Vendor Siemens. | PB | MECH | OPEN |  | None |  | None | None | Vendor | None | None | M-02 |  | None | 10248C | 17/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Lighting JB and instrument (stand) are too close. Adjust location of instrument away from lighting JB. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | CXE-L-M02-353 | 10249C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | JB is blocked for access, relocate electrical/ instrument tray away from front side of JB. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | CXE-L-M02-352 | 10250C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Extend/adjust floodlight support away from steel column. | OK, floodlight has been re-located | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LNO-209-01-M02-003 LNO-209-01-M02-005 | 10251C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Bring tray closer to JB, ensuring proper cable support. Distance between tray and JB cable entry point should be around approximately 300mm. | Tray relocated closer to the JB and updated with proper cable support. The distance between the cable tray and the JB cable entry point is maintained at 300 mm. | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M-02 |  | CXE-L-M02-207 | 10252C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
Level 2 | Tapping points (PIT-1254063A) should not be obstructed. Relocate JB at opposite side of same column. | JB relocated to provide better access for Instrument | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M-02 |  | CXN-L-M02-015 | 10253C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
Level 2 | Check mounting method of lighting, ensure proper mounting on available steel structures. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LNO-209-06-M02-005 | 10254C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Relocate tray (elevate or move away from light fitting) to avoid obstruction to light access. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LEM-318-03-M02-006 | 10255C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Relocate lighting fixture away from beacon. Ensure that the beacon is easily visible to personnel during emergency scenario. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LEM-319-03-M02-003 | 10256C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Adjust instrument tray to unblock floodlight illumination throw to task area. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LES-296-04-M02-001 | 10257C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Small bore pipes to adjust upward away from floodlight. Ensure pipe support for small bore lines are not too close to floodlight also. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LNO-209-09-M02-004 | 10258C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Move the Telecom Cable ladder to have enough space for installing the Hold down Clamp | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05 |  | TT-M05-S-B-TRAY-00003 | 10259C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level1 | Update the cable tray routing based on the actual cable size and cable bending radius | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05 |  | None | 10260C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
General | Secondary trays are missing for Telecom equipment. General for M05 | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05 |  | General | 10261C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Adjust the speaker to edge for better cabling | The speaker has been adjusted to the edge for better cabling | SEA | TEL | Pending PB Reply | 23/12/2025 | None |  | None | None | TEL | None | None | M-05 |  | SPP-M05-00018 | 10262C |  | 12.0000000000000 | 3.00000000000000 | SEA/KBR | None |  | None | None | 26/12/2025 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 28/12/2025
Level 1 | Relocate the speaker and adjust the access point. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05 |  | SPP-M05-00024 | 10263C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Trim the tray up to the lighting | The tray is Trimmed. close the point | PB | ELE | CLOSE | 05/12/2025 | Julius Orzales | 08/01/2026 | None | 08.01.2025-NA53- close | ELE | None | 15-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-05 | 08/01/2026 | EC-M05-L-E-TRAY-20535 | 10264C |  | 9.00000000000000 | 25.0000000000000 | PB - Engineering | True | 08/01/2026 | True | None | 08/12/2025 | 17/12/2025 | 10/01/2026 | 11/01/2026 | 17/12/2025 | 08/12/2025
Level 2 | Relocate the speaker for accessbility | The speaker has been relocated as per accessibility | PB | TEL | Pending PB Reply | 23/12/2025 | None |  | None | None | TEL | None | None | M-05 |  | COR-5518055B | 10265C |  | 12.0000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 26/12/2025 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 28/12/2025
Level 2 | Adjust the safety volume to avoid the speaker | None | PB | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | COR-5518057B | 10266C | 01/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Relocate the speaker to the column | Speaker is recolated to the column as per mark up | KBR | TEL | RE-OPEN | 04/01/2026 | None |  | None | None | TEL | None | None | M-05 |  | COR-5518057A | 10267C | 28/01/2026 | 3.00000000000000 |  | SEA/KBR | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
Level 4 | CCTV need to relocate to 3 meters for better viewing as per operation team's recommendation and lighting need to relocate. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05 |  | CAM-5514014 | 10268C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | CCTV need to relocate for better viewing as per operation team's recommendation and lighting need to relocate | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-05 |  | LNO-211-11-M05-005 | 10269C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Adjust the speaker to edge for better cabling | The speaker has been adjusted to the edge for better cabling. | PB | TEL | Pending PB Reply | 23/12/2025 | None |  | None | None | TEL | None | None | M-05 |  | SPP-M05-00048 | 10270C |  | 12.0000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 26/12/2025 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 28/12/2025
None | Move the equipment to inside the platform | The equipment has been moved inside the platform | PB Ops | TEL | Pending PB Reply | 23/12/2025 | None |  | None | None | TEL | None | None | M-05 |  | None | 10271C |  | 12.0000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 26/12/2025 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 28/12/2025
Level 1 | Topside module tray and vendor tray bottom should be aligned and higher than coaming height | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | IT-M05-S-I-TRAY-01001-TRAY-0103 | 10272C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | E&I penetration trays rear side should be removed. Update as per mark up. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | I-M05-S-PEN-101 | 10273C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Electrical to removed the coaming plate. ICSS panel MCT and structural coaming should be aligned | 05/12/25 Electrical Response: Electrical separate penetration has been removed. | KBR | ELE | RE-OPEN | 04/12/2025 | None |  | None | None | ELE | None | None | M-05 |  | E-M05-L-PEN-213 I-M05-S-PEN-223 | 10274C | 29/01/2026 | 15.0000000000000 | 19.0000000000000 | PB - Operation | None |  | None | None | 07/12/2025 | 22/12/2025 | 24/12/2025 | 24/12/2025 | 22/12/2025 | 07/12/2025
None | Connectivity required | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | IT-M05-S-I-TRAY-01001-TRAY-0104 IT-M05-S-I-TRAY-01019-TRAY-0002 | 10275C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Vendor MCT to aligned with Topside coaming | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | I-M05-S-PEN-214 | 10276C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
General | Provide cable tray tee joint and connect the trays. Typical | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | General | 10277C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Trays shall be modelled showing complete connectivity (Typ). | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | IT-M05-S-S-TRAY-04008 | 10278C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Lower down the cable ladder to have space for cable bending radius below JB | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | IT-M05-S-S-TRAY-05001-TRAY-0102 | 10279C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | KBR to model and incorporate the necessary supports in accordance with the standard KBR typical drawings for all 90 deg Bends(Typ). | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | IT-M05-S-S-TRAY-04002-TRAY-0206 | 10280C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Cable tray to be provided from the main Structural beam instead of the present support arrangement | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | ISPT-M05-04031 | 10281C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Re-orientate the transmitters to have access for tapping point. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | LIT-1231020A LIT-1231022A | 10282C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Relocate the marked transmitters away from the SDV. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | LIT-1231020B LIT-1231022B | 10283C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Flow element upstream and downstream need to recheck and update. follow up with piping. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | FE-1231035A | 10284C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
None | Tray to be modelled for capillary tubing | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | PIT-1231072B | 10285C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Ensure positioner location is accessable to operator. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | LV-1231022A | 10286C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Tray not to be routed behind ladder | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | IC-M05-S-I-TRAY-01015 | 10287C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Piping /Instrument to ensure vent and drain connection. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | LG-1231021A | 10288C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Instrument tray & penetration to be modell ed for Analyzer. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | PN-AIT-1231009 | 10289C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
General | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. Penetrations to be model as per structure guidelines.. This requirement applies to all Instruments, JB and valves M05. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | General | 10290C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Instrument to relocate in accessible area | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | None | 10291C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Evaluate and change the instrument type to capillary diaphragm and install the transmitter nearby. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | PIT-1231065A PIT-1231065B PIT-1231065C | 10292C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | This transmitter is far from tapping. One of the following solutions needs to be adopted to bring the transmitter closer to the Tapping point: a) the position of transmitter needs to be reevaluated b) Integral mounted transmitter is to be evaluated. c) diaphragm seal needs to be considered | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | PIT-1231065C PIT-1231086C PDIT-1231056A PIT-1231050A PIT-1231052A PIT-1231085A PDIT-1231056B PIT-1231050B PIT-1231052B PIT-1231085B PIT-1231061A PIT-1231034 PIT-1231061B PIT-1231065A PIT-1231086A PIT-1231086B PDIT-1231073B PIT-1231061C PIT-1231065C PIT-1231086A PIT-1231086B PIT-1231086C PIT-1231098A PIT-1231098B PIT-1231098C | 10293C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Move flow transmitter to near. Exceptionally, these transmitters may be installed at a height between 2.0 and 2.4 meters. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-05 |  | FIT-1231078A FIT-1231078B FIT-1231078C | 10294C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Adjust/shift light fitting slightly to right, away from stairway area for easier and safer access and maintenance. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LEM-318-04-M02-006 | 10295C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
General | Ensure that all sub-cable trays are properly terminated and connected to the bottom of each JB. All lighting fixtures shall be connected using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all lights and JB within Module M02. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | General | 10296C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 5 | Pole-mounted lighting fixtures (5 nos.) around platform periphery to be evaluated and verified, proposed to be shifted inside the platform. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LEM-318-05-M02-002 LEM-318-05-M02-003 LEM-319-05-M02-002 LEM-319-05-M02-003 LEM-319-05-M02-004 | 10297C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Shift floodlight/JB along with support assembly where JB is easily accessed in consideration of the guardrail profile. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LES-296-06-M02-001 LNO-209-12-M02-005 LES-296-06-M02-005 | 10298C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Floodlight too close to valve, shift floodlight away from the valve and its access/handling space. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LES-296-06-M02-006 | 10299C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Relocate floodlight to avoid blocking access to instrument JB. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LNO-209-13-M02-001 | 10300C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Relocate pole mounted light to unblock the access to valve. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LNO-209-13-M02-003 | 10301C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Shift floodlight to marked location, away from nearby valve. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-02 |  | LNO-209-13-M02-004 | 10302C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Show the cable bending radius to the last MCT frame close to the beam to see whether the cable will touch the beam. If it touches, the penetration is to be changed to 8*3. KBR to check. | HV Cable is modelled last MCT frame and verified & there is no touch the beam for this cable. | SEA | ELE | RE-OPEN | 30/11/2025 | Welton | 08/01/2026 | 09/01/26- UR7U-The electrical cable is very close to the beam, which could cause damage to the cable's insulation due to the risk of contact with the beam. | 08.01.2025-RTWG-RE-OPEN-The electrical cable is very close to the beam, which could cause damage to the cable's insulation due to the risk of contact with the beam. | ELE | None | 15-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-05 |  | E-M05-H-MCT-003 | 10303C |  | 14.0000000000000 | 24.0000000000000 | SEA/KBR | True | 08/01/2026 | False | None | 03/12/2025 | 17/12/2025 | 10/01/2026 | 11/01/2026 | 17/12/2025 | 03/12/2025
None | Provide access platform for the terminal box (UC-1231001A/B/C). | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | UC-1231001A/B/C | 10304C | 29/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Alignment of electrical tray interfacing with RTU panel to be fully checked, ensure tie-in interface alignment. Typical comment to all RTU panels | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | PN-UC-1231001A-02 | 10305C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Check tray provision from vendor. If vendor do not provide the tray, topside tray to be extended complete with proper support. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | PN-AIT-1231009 | 10306C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Re-orient JBs and shift away from current position to avoid access issues. | JB relocated to have better access | PB Ops | ELE | RE-OPEN | 05/12/2025 | Welton | 08/01/2026 | 09/01/26 - UR7U - JB remains obstructed for maintenance. | 08.01.2025 -NA53- RE-OPEN -JB remains obstructed for maintenance. | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-05 |  | CXN-L-M05-006 | 10307C |  | 14.0000000000000 | 19.0000000000000 | PB - Operation | True | 08/01/2026 | False | None | 08/12/2025 | 22/12/2025 | 10/01/2026 | 11/01/2026 | 22/12/2025 | 08/12/2025
Level 1 | Evaluate positions of the 3 lights, as there are maintenance issues foreseen with all 3 lights in 1 column/position. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LEM-322-02-M05-005 | 10308C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Evaluate positions of lighting and camera. Observe clearance between 2 equipment so as not to degrade image captured by camera. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LEM-323-02-M05-003 | 10309C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Move lighting fixture away from tapping points. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LEM-323-02-M05-004 PC-2560-N7C | 10310C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Handling volume to be updated in model. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LES-298-01-M05-004 | 10311C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Floodlight to shift to outer face of the column flange for better accessibility. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LES-298-02-M05-003 | 10312C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Small bore pipe to shift away from front side of the floodlight. | 10Jan2026 - Small bore piping shifted away from the Flood Light. | PB Ops | PIP | Pending Seatrium Reply | 09/01/2026 | None |  | None | None | PIP | None | None | M-05 |  | LNO-211-02-M05-003 | 10313C | 28/01/2026 | -1.00000000000000 |  | PB - Operation | None |  | None | None | 12/01/2026 |  |  |  |  | 12/01/2026
Level 1 | Floodlight position to consider mounting on pipe support to ensure that it is not obstructed. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LNO-211-03-M05-004 | 10314C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Adjust light to AFT side of column (same position and orientation) to increase accessibility to equipment. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LES-298-03-M05-001(Snapshot1) LEM-322-53-M05-002 (Snapshot2) | 10315C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Shift the floodlight lower as large bore pipe impedes illumination based on current position. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LES-298-03-M05-002 | 10316C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Re-orient/move tray away from floodlight projection of light to task area. | Tray is Re-located to avoid obstrction to the light | PB Ops | ELE | Pending PB Reply | 05/12/2025 | None |  | None | 09.01.2025-NA53 -Close. | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-05 |  | LNO-211-06-M05-002 | 10317C |  | 14.0000000000000 | 20.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 08/12/2025 | 22/12/2025 | 11/01/2026 | 11/01/2026 | 22/12/2025 | 08/12/2025
Level 2 | JB front side should not be obstructed by tray, revise tray model to ensure accessibility of the JB. | Tray is Re-located. Resovled this issue | PB Ops | ELE | Pending PB Reply | 05/12/2025 | None |  | None | 09.01.2025-NA53- Close | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-05 |  | CXN-L-M05-018 | 10318C |  | 14.0000000000000 | 20.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 08/12/2025 | 22/12/2025 | 11/01/2026 | 11/01/2026 | 22/12/2025 | 08/12/2025
Level 1 | Relocate piping away from JB to provide 800mm clearance | None | SEA | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 10319C | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Adjust the speaker to edge as per mark up | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-04 |  | COR-5518038A | 10320C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Relocate the F&G equipment to the edge to avoid speaker | None | KBR | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | AST-M04-101-C02-013 | 10321C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Trim the tray and align with JB. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-04 |  | TT-M04-S-A-TRAY-00003 TT-M04-S-B-TRAY-00003 | 10322C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Relocate the Speaker to column mount | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-04 |  | COR-5518043A | 10323C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Check and relocate the Access point as per markup. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-04 |  | PA-5517002 | 10324C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Relocate the BLE | BLE has been relocated as per mark up | KBR | TEL | Pending PB Reply | 06/01/2026 | None |  | None | None | TEL | None | None | M-04 |  | BLE-5511052 | 10325C | 28/01/2026 | 2.00000000000000 | 0 | PB - Engineering | None |  | None | None | 09/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
Level 2 | Move speaker nearer to the edge | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-04 |  | SPP-M04-00022 | 10326C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 3 | Relocate the BLE | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-04 |  | BLE-5511054 BLE-5511055 | 10327C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 6 | Modify equipment support to avoid structure beam | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-04 |  | SPP-M04-00059 | 10328C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 6 | Relocate the BLE to the marked location | The BLE has been relocated to the marked location | KBR | TEL | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | TEL | None | None | M-04 |  | BLE-5511062 | 10329C | 28/01/2026 | 0 |  | PB - Engineering | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
Level 6 | Relocate the BLE to the marked location | The BLE has been relocated to the marked location | KBR | TEL | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | TEL | None | None | M-04 |  | BLE-5511063 | 10330C | 28/01/2026 | 0 |  | PB - Engineering | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
General | Secondary trays are missing for Telecom equipment. General for M04. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-04 |  | General | 10331C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
None | To confirm vendor cable tray tie in location for UC-UT-1238001A/B | Awaiting a response from Vendor MAYEKAWA | None | MECH | OPEN |  | None |  | None | None | Vendor | None | None | M-04 |  | None | 10332C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
General | To provide the trimmers for Junction Boxes support. Typical | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | General | 10333C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
General | Vendor MCT to aligned with Topside coaming | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | General | 10334C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | To relocate the analyser panel or junction boxes to have the maintenance access | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | PN-MIT-1235801 | 10335C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Vendor to provoide the cable tray tie in | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | IT-M04-S-I-TRAY-01026 | 10336C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Capillary tubing tray and related penetration is missing. KBR should model the tubing (if more than 2.5m) and cable penetrations separately, as agreed as per LL. General for M04 | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | LIT-1235801C LIT-1235802C | 10337C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all Instruments, JB and valves M04. Cable Penetration to be modelled and that has to follow as per structure guideline. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | None | 10338C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | KBR to model and incorporate the necessary supports in accordance with the standard KBR typical drawings for all 90 deg Bends. | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | IT-M04-S-I-TRAY-01001 | 10339C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Model tapping point and flushing ring for capillary type level transmitters and. Typical comment for M04 | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | PDIT-1235820 LIT-1234804 LIT-1235801A LIT-1235801B LIT-1235801C LIT-1235802A LIT-1235802B LIT-1235802C LIT-1235805 | 10340C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Evaluate the instrument tubing whether can be routed on the same deck level, where practicle. I | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | None | 10341C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Model flushing ring for capillary type level transmitters. Typical comment for M04 | None | KBR | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | None | 10342C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | This transmitter is far from tapping. One of the following solutions needs to be adopted to bring the transmitter closer to the Tapping point: a) the position of transmitter needs to be reevaluated b) Integral mounted transmitter is to be evaluated. c) diaphragm seal needs to be considered (PB to provide the list of transmitter impacted) | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | (PB to provide the list of transmitter impacted) | 10343C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Ensure that all sub-cable trays are properly terminated and connected to the bottom of each JB. All lighting fixtures shall be connected using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all lights and JB within Module M05. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | CXE-L-M05-366 | 10344C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Clear tray below light fitting for access space to equipment. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LEM-322-06-M05-004 | 10345C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Adjust support length of JB, provide sufficient clearance between JB and valve/tray. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | CXE-L-M05-320 | 10346C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Adequate clearance between speaker and light to be observed. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | LNO-212-11-M05-001 | 10347C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Adjust floodlight as per guard rail profile. Ensure JB to be accessible. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | CXN-L-M05-064 LNO-211-15-M05-004 LNO-211-17-M05-003 | 10348C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Space for installing cables at MCT to be checked and addressed. Proper spacing to be provided. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-04 |  | E-M04-M-MCT-002-TRAY-0031 | 10349C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Check cable entry space between socket and JB. Ensure cable is able to terminate and is properly supported. | cable entry space between the socket and the junction box (JB) has been modified. | SEA | ELE | Pending PB Reply | 05/12/2025 | None |  | None | None | ELE | None | 15-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-04 |  | SKN-M04-423 | 10350C |  | 9.00000000000000 | 24.0000000000000 | SEA/KBR | True |  | None | None | 08/12/2025 | 17/12/2025 |  |  | 17/12/2025 | 08/12/2025
None | Analyzer panel location needs to be finalized so that the electrical cable trays, penetrations, and supports can be modeled. GA & penetration to be finalized by Vendor. | Electrical response : cable tray provided for Analyzer panel | SEA | CSE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED (CABLE TRAY/SUPPORT) AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-04 |  | ET-M04-L-N-TRAY-2000 | 10351C | 29/01/2026 | 8.00000000000000 | 19.0000000000000 | SEA/KBR | True |  | None | None | 14/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 14/12/2025
None | Not enough space for terminal box maintenance. Resolve access issue. To be resolve/advise by Vendor | Awaiting a response from Vendor MAYEKAWA | PB Ops | MECH | OPEN |  | None |  | None | None | MECH | None | None | M-04 |  | SRF1 | 10352C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
None | Offloading Meter skid Tie-in to be confirmed and to align with Vendor | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-04 |  | - | 10353C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | JB to face opposite side for easy access. Tray model to suit and shall not block the front side of JB. | JB face opposite side modelled as per comment | PB Ops | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | ELE | None | 15-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-04 |  | None | 10354C |  | 14.0000000000000 | 24.0000000000000 | PB - Operation | True |  | None | None | 03/12/2025 | 17/12/2025 |  |  | 17/12/2025 | 03/12/2025
None | Telecom tray to adjust, light fitting to adjust accordingly, ensure cable entry is not blocked, ensure light support can be welded to the column. | Telecom tray adjusted and enough clearance provided for light fixture support welding | PB Ops | ELE | RE-OPEN | 18/12/2025 | None |  | None | None | ELE | None | None | M-04 |  | LEM-321-02-M04-004 | 10355C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 21/12/2025
None | Floodlight to relocate and mount on web part of column for better illumination coverage. | Flood light has been moved to Web location as per the comment | PB Ops | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | ELE | None | 15-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-04 |  | LNO-210-03-M04-005 | 10356C |  | 14.0000000000000 | 24.0000000000000 | PB - Operation | True |  | None | None | 03/12/2025 | 17/12/2025 |  |  | 17/12/2025 | 03/12/2025
None | Model lighting sub-tray. | Sub trays modelled as per comments | PB Ops | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M-04 |  | LNO-210-04-M04-009 LNO-210-05-M04-008 LNO-210-06-M04-004 LNO-210-08-M04-001 LNO-210-07-M04-002 LEM-321-06-M04-003 LNO-210-13-M04-002 LNO-210-13-M04-003 | 10357C |  | 19.0000000000000 | 19.0000000000000 | PB - Operation | True |  | None | None | 03/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 03/12/2025
None | Change lighting installation type to clear the issue with handling volume, related lighting sub-tray to suit. | As per updated calculation Light fixture is removed, this location is luminated by nearby light fixture. | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-04 |  | LNO-210-09-M04-007 | 10358C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
None | Check purpose of extension platform. Check if light can shift to inside the guard rail. | Platform Extended for Drop zone, hence light fixture is removed from this location | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-04 |  | LNO-210-09-M04-007 | 10359C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
PLLIN | Mechanical handling equipment to be checked - interfering with telecoms tie-in. | None | None | HAND | OPEN |  | None |  | None | None | TEL | None | None | INT |  | TPT-TC-PLLI-S-B-TRAY-50775 | 0394C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
MDK | Support to be checked for welding accessibility as per structural guideline. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | INT |  | TSPT-M13-01014 | 0395C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
MDK | CIMC cable tray to align with topside tie-in point | None | None | CIMC | OPEN |  | None |  | None | None | TEL | None | None | INT |  | TPT-TC-PLLI-S-A-TRAY-51354 | 0396C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | KBR to align the cable trays based on ABB tie-in | None | None | EIT | OPEN |  | None |  | None | None | CSE | None | None | INT |  | IT-M17-S-S-TRAY-00028 IT-M17-S-S-TRAY-00029 | 0397C |  |  |  | SEA/KBR | None |  | None | None
1 | KBR to explain why the agreed safety system has been changed to instrument, and ABB to take action accordingly | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | INT |  | IT-M13R-S-S-TRAY-00037 | 0398C |  |  |  | SEA/KBR | None |  | None | None
1 | Electrical and Instrument cable trays to have combined tray supports | None | KBR | ELE | OPEN |  | None |  | None | None | CSE | None | None | INT |  | ESPT-M09D-20042 ISPT-M09D-01001 | 0400C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | IT-054, 055, KBR to evaluate the tubings and cable ladders to be connected below the battery limit to connect between topside Equipment's. This Tie-in may not require considering the above point. | None | KBR | CSE | OPEN |  | None |  | None | None | CSE | None | None | INT |  | None | 0401C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | IT-056 - There is Missing Tie-in between Topside RIO to LQ for Network cables. KBR/CIMC to evaluate to use the existing Tie-in IT-012, 013 | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | INT |  | None | 0402C |  |  |  | SEA/KBR | None |  | None | None
1 | Provide tray support and tray dropper to be adjusted | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | INT |  | IT-M07B-S-I-TRAY-00501 | 0403C |  |  |  | SEA/KBR | None |  | None | None
1 | ET-108 Cable tray support to be provided | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | INT |  | ET-M13-L-E-TRAY-01011 | 0404C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
MDK | M05 - KBR piping to adjust piping to align with interface location | KBR Piping Updated to match interface location with CIMC | KBR | PIP | Pending PB Reply | 20/11/2025 | None |  | None | None | PIP | None | No piping DCN required | INT |  | TP-5336-0588 | 0405C |  | 27.0000000000000 | 22.0000000000000 | SEA/KBR | None |  | None | None | 23/11/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 23/11/2025
MAIN | CIMC duplicate piping to be deleted | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | 4"-DFC-B9-0206-NI | 0406C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
MDK | M13B - KBR piping to adjust piping to align with Tie-in list coordinates | KBR Piping Updated to align with Tie-in list Co-ordinates and matched with CIMC Interface location | KBR | PIP | Pending PB Reply | 20/11/2025 | None |  | None | None | PIP | None | No piping DCN required | INT |  | 10&quot;-DA-B9-2357-NI TP-5336-0070 | 0407C |  | 27.0000000000000 | 21.0000000000000 | SEA/KBR | None |  | None | None | 23/11/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 23/11/2025
MDK | M05B - TP number to be assigned to line in model | TP Number Assigned at Interface Location | KBR | PIP | Pending PB Reply | 20/11/2025 | None |  | None | None | PIP | None | No piping DCN required | INT |  | 3"-PC-C3N-2781-NI | 0408C |  | 27.0000000000000 | 21.0000000000000 | SEA/KBR | None |  | None | None | 23/11/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 23/11/2025
MDK | Tie -in numbers to be assigned to piping | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | INT |  | "TP-5336-0012 TP-5336-0013 TP-5336-0015 TP-5336-0017 TP-5336-0018 TP-5336-0161 TP-5336-0004 TP-5336-0129 TP-5336-0011 TP-5336-0157 TP-5336-0154 TP-5336-0750 TP-5111-0002 TP-5336-0098 TP-5336-0063 TP-5336-0795 TP-5336-0097 TP-5336-0023 TP-5336-0027 TP-5134-0405 TP-5134-0406 TP-5336-0146 TP-5336-0064 TP-5336-0147 TP-5336-0066 TP-5336-0067 TP-5336-0023 TP-5134-0405 TP-5134-0406 TP-5241-0178 TP-5115-0322 TP-5134-0005 TP-5135-0482 TP-5134-0401 | 0409C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
MDK | M15 - Flange to be provided at inlet of siphon | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | INT |  | DA-1095 | 0410C | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
MAIN | M15 - Space to be provided for rodding - 1m by 1m volume | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | INT |  | DA-1095 | 0411C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
MDK | M09 - Hookup spool to be provided on topside piping | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | INT |  | DA-3187 | 0412C | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
MDK | CIMC to align the piping as per tie-in list coordinates | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | TP-5241-0178 | 0413C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
MDK | Mismatch on tie-ins from CIMC. CIMC to align with the tie-in list coordinates | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | BG-0193 BG-0748 TP-5241-0739 TP-5241-0037 | 0414C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
MDK | Size mismatch - CIMC to match the line size | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | TP-5336-0024 TP-5336-0112 TP-5336-0026 TP-5336-0744 | 0415C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
MDK | CIMC to align the piping as per tie-in list coordinates | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | TP-5122-0456 | 0416C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
MDK | M16 - piping to be aligned as per tie-in list coordinates and blind flange deleted | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | INT |  | TP-5122-0001 | 0417C | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
PLLIN | Chemical Injection valve modelling, instrument PIT modelling and access volumes to be completed, valves to be accessible. VDS input to be provided by KBR | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | INT |  | None | 0418C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
PLLIN | TUTU hook-up to be checked - currently modelled as piping but tubing connection to be studied if required. | None | None | CSE | OPEN |  | None |  | None | None | PRO | None | None | INT |  | 1&quot;-CNI-J12-2088-NI 1&quot;-CNI-J12-2089-NI TUTU-PLATE-6-SLOT | 0419C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
PLLIN | CIMC Subsea HPU tubing to be routed to follow KBR interface point | None | None | CIMC | OPEN |  | None |  | None | None | CSE | None | None | INT |  | TUTU-PLATE-37-SLOT-TUBING IT-M09A-T-TRAY-00501 | 0420C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
PLLIN | Gap to be provided between pipe and tundish | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | 4"-DA-B9-1386-NI | 0421C | 26/02/2026 |  |  | PB - Engineering | None |  | None | None
PLLIN | Seatrium to check with KBR to understand the interpretation of P&ID I-DE-3010.2S-1210-944-S2N-014 Note 10. Currently check valve is located 180 m from the slots (worst case) | None | None | SEA | OPEN |  | None |  | None | None | PRO | None | None | INT |  | None | 0422C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
PLLIN | Contents of slot number to be in line with tubing rack number | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | TUTU-CNI-PIPE-RACK-slot25-COPY | 0423C | 26/02/2026 |  |  | PB - Operation | None |  | None | None
PLLIN | Seatrium to check whether the coaming for safety showers and chemical injection tubing rack should be combined or not | None | None | SEA | OPEN |  | None |  | None | None | SAF | None | None | INT |  | None | 0424C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
PLLIN | Slot 12 to be updated as per latest P&ID with more hydraulic tubing than chemical injection tubing | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | None | 0425C | 26/02/2026 |  |  | PB - Operation | None |  | None | None
PLLIN | CIMC to complete the tubing connections to the respective tubing racks | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | None | 0426C | 26/02/2026 |  |  | PB - Operation | None |  | None | None
PLLIN | CIMC to complete the tubing penetrations on the SDV platform | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | None | 0427C | 26/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Seatrium to liaise with CIMC to ensure connectivity to CIMC valves XV-5111001A/B/C/D, SDV-5336501 | None | None | CIMC | OPEN |  | None |  | None | None | PIP | None | None | INT |  | XV-5111001A/B/C/D SDV-5336501 | 0428C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Update the Valve tag as per PID VALV-51390020, VALV-51390021, VALV-51390022, VALV-51390023 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | INT |  | VALV-51390020 VALV-51390021 VALV-51390022 VALV-51390023 | 0429C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | KBR to complete the routing of tubing between Topside RIO Panels and Topside valves | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | INT |  | PN-UH-5139009-02 | 0430C | 15/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | Pipe supports to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | INT |  | 4&quot;-H-B3-0132-NI 4&quot;-H-B3-0138-NI 3&quot;-H-B3-0140-NI 4&quot;-H-B3-0146-NI 4&quot;-H-B3-0147-NI 4&quot;-H-B3-0148-NI 4&quot;-H-B3-0149-NI 3&quot;-H-B3-0127-NI 3&quot;-H-B3-0134-NI 3&quot;-H-B3-0152-NI 2&quot;-H-B3-0142-NI 3&quot;-H-B3-0146-NI | 0431C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Penetrations to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | INT |  | 4&quot;-H-B3-0132-NI 4&quot;-H-B3-0138-NI 3&quot;-H-B3-0140-NI 4&quot;-H-B3-0146-NI 4&quot;-H-B3-0147-NI 4&quot;-H-B3-0148-NI 4&quot;-H-B3-0149-NI 3&quot;-H-B3-0127-NI 3&quot;-H-B3-0134-NI 3&quot;-H-B3-0152-NI 2&quot;-H-B3-0142-NI 3&quot;-H-B3-0146-NI | 0432C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Seatrium to follow up on the drainage systems for HPU extended platform | None | None | SEA | OPEN |  | None |  | None | None | PIP | None | None | INT |  | None | 0433C | 26/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Seatrium to follow up with CIMC for 86 tubing/piping connections to the SDVs on SDV platform | None | None | SEA | OPEN |  | None |  | None | None | PIP | None | None | INT |  | None | 0434C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | KBR to update the XV location in the P&ID as this valve is located at Main Deck, not M10A. Seatrium shall discuss with KBR for tie-in point vs. Panels configuration. Seatrium and PB prefers this tie-in point (in principle for all main deck valves) to be located at Panel PN-UH-5139009-02 | None | KBR | CSE | OPEN |  | None |  | None | None | PIP | None | None | INT |  | XV-5133046 | 0435C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | Tubing penetrations to be updated from MCT type to coaming type with fire sealant | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | INT |  | I-M09A-S-MCT-004 | 0436C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Safety Equipment supports to be modelled - Typical punch for all EEBD and fire lockers in M09 MDK | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | INT |  | Z-H-5423247 Z-5434790 Z-H-5423239 Z-5434791 Z-5434793 | 0437C | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | TS-MDK - Safety equipment reserve volume to be modeled (typical for all fire extinguishers) | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | INT |  | Z-54285034 Z-54285035 Z-54281036 | 0438C | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | Tag number to be updated as per Safety Plan drawing | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | INT |  | H-5423245 Z-H-5423245 | 0439C | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | Slot 12 - CIMC to study to ensure adequate access to the safety shower | None | None | CIMC | OPEN |  | None |  | None | None | SAF | None | None | INT |  | Z-5430504-C3 | 0440C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | CIMC to complete the piping connections to the safety showers | None | None | CIMC | OPEN |  | None |  | None | None | SAF | None | None | INT |  | Z-5430504-C1 Z-5430504-C2 Z-5430504-C3 Z-5430504-C4 | 0441C | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Material handling volume size to be reduced as per hatch size | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | INT |  | None | 0442C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Seatrium to resolve the clashes due to SDV valves configuration change with KBR and CIMC | None | None | SEA | OPEN |  | None |  | None | None | PIP | None | None | INT |  | SDV-1210001A/B/C/D/E/F/G/H/J | 0443C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Beam clamp, pipe support and cable tray arrangement to be modified to avoid interference | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | INT |  | SDV-1210008K VALVE STUDY-0019 | 0444C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | The sling of the spool movement modeling to be updated to avoid interference with KBR pipe supports and cable trays (typical punch A-F SDV Valves) | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | INT |  | None | 0445C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | KBR to show the material handling path for the manual valves which needs to be removed prior to flexible riser removable spool handling | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | INT |  | VALV-12101972 | 0446C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Layout configuration showing real loads vs. deck loads to be provided for M09 Level 1. Seatrium has restricted the use of rollerskates previously for 10T weight valve. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | INT |  | None | 0447C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Turn radius to be modelled | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | INT |  | None | 0448C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Detailing below M17/M13B/M13 infill plate, brackets to be completed | None | None | ABB | OPEN |  | None |  | None | None | STR | None | None | INT |  | None | 0449C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | Evaluate the requirement for coaming and drainage for HPU DISTRIBUTION RACK | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M11 |  | PN-UH-5139011 | 0450C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Supply and return piping to be modelled for HPU DISTRIBUTION RACK | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | PN-UH-5139004 | 0451C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Evaluate the requirement for coaming and drainage for HPU DISTRIBUTION RACK | None | None | PRO | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | PN-UH-5139004 | 0452C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Supply and return piping to be modelled for HPU DISTRIBUTION RACK | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | PN-UH-5139005 | 0453C | 21/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Evaluate the requirement for coaming and drainage for HPU DISTRIBUTION RACK | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | PN-UH-5139005 | 0454C | 25/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Piping between HPU DISTRIBUTION RACK and valves to be modelled. Piping Tie-ins to be verified. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | PN-UH-5139007A | 0455C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Evaluate the requirement for coaming and drainage for HPU DISTRIBUTION RACK | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | PN-UH-5139007A | 0456C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Supply and return piping to be modelled for HPU DISTRIBUTION RACK | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PN-UH-5139010B | 0457C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Evaluate the requirement for coaming and drainage for HPU DISTRIBUTION RACK | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PN-UH-5139010B | 0458C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Tapping to be taken as close as possible from inlet as per P&ID Note 39 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | 8"-PC-E16N-2793-NI | 0459C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Location of sampling panel to be confirmed with Process considering distance from branch take-off | Location of sampling panel is not a concern to Process. However, Piping to ensure that the isolation valve to the sampling panel is located closure to the take off header. | None | PRO | RE-OPEN | 08/01/2026 | None |  | None | None | PIP | None | no dcn required | M10A/C |  | ESP-12230408 ESP-12230418 | 0460C |  | 0 | 0 | PB - Operation | None |  | None | None | 11/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
2 | To evaluate making structural member removable to allow for spectacle blind removal. | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | ESP-12230040 / 12230042 / 12230140 | 0461C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | Evaluate the location of sample box close to sample point | M-10A Sample box moved close to sample point. For M10C already sample box in same level | None | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | NO Piping DCN required | M10A/C |  | SC-FIT-1223056A | 0462C |  | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
2 | All first drain valves of the vessel shall be connected directly on the vessel nozzle - to avoid dead leg. The valves are not requently operated. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | VALV-12232500 VALV-12230119 VALV-12230272 VALV-12230274 VALV-12232502 | 0463C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | First block valve to be close to nozzle, UC connection to be in horizontal. Access to valve by scaffolding is acceptable. | First block valve moved close to nozzle, UC connection modeled in horizontal. | KBR | PIP | RE-OPEN | 18/12/2025 | None |  | None | None | PIP | None | None | M10A/C |  | VALV-12230043 VALV-12230038 | 0464C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 21/12/2025
2 | Valve and spectacle blind to be located as close as possible to nozzle as it is not frequently operated. PB Operations agrees to change valve to category 3. | Valve and spectacle blind movedo as closed possible to nozzle. | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M10A/C |  | VALV-12230334 | 0465C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 21/12/2025
2 | Equipment sample collection box to be inside the equipment coaming | Equipment sample collection box now in inside the equipment coaming | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | DCN piping not required | M10A/C |  | SG-1223001A/B TO-1223001/2-A/B | 0466C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
3 | Valves to be updated as double block type as per AFC | Valves are updated to double block type. | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | No Piping DCN required | M10A/C |  | VALV-12230276 VALV-12230277 VALV-12230278 VALV-12230279 VALV-12230280 VALV-12230312 VALV-12230313 | 0467C |  | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
2 | DA-1884 Connected drain box to be located aft position of the Support fixed saddle. Check with process on connecting to 10" header from another drain box. | DA-1884 Connected drain box modified to aft position | KBR | PIP | RE-OPEN | 18/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M10A/C |  | M10A-L2-DB3-002 | 0468C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
2 | Operation volume to be added for DBB | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | VALV-12230294 VALV-12230038 VALV-12230302 | 0469C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Removal of plate from top (with ergonomic access) during operation to be evaluated - spool removal not acceptable. Reserve volume to be modeled considering spindle operation. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | FE-1223053A/B | 0470C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Platform elevation to be raised considering height of spindle - PB Operation accepts 2m head room. | Modelled 2300mm Head room volume for M10A&C | KBR | STR | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10A/C |  | FE-1223053A/B | 0471C | 31/12/2025 | 0 | 6.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
4 | Coaming to be updated to include SDV and piping. Drainbox to move toward Aft position accordingly with coaming modification | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | OFLD-M10A-0094708 | 0472C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Sampling point connection to be relocated to marked position to meet P&ID note 52 requirement | Sampling point connection relocated to marked position | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M10A/C |  | PC-0211 | 0473C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
4 | Process to evaluate the SDV & Check valve arrangement considering I-DE-3010.2S-1223-944-S2N-003 P Note 38. Note to be deleted if not necessary | Due to limitations in layout, a bleed connection is already provided between SDV and check valve. Hence, Note 38 can be removed. Piping to raise PUN. | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M10A/C |  | PC-0211 SDV-1223051A Check Valve VSL-2-12501 | 0474C |  | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
5 | Check with Process if line can be connected to HP header as like the PSV outlet. Ref. I-DE-3010.2S-1223-944-S2N-009 | Retain as it is (connected to LP) | None | PRO | Pending PB Reply | 08/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10A/C |  | F-0720 | 0475C |  | 0 | 0 | PB - Operation | None |  | None | None | 11/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
1 | Drain connection to be modifed to provide clearance | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | VALV-12230282 VALV-12230222 | 0476C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | High point vent to be modeled | High point vent modeled. Not applicable for M10C | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10A/C |  | PC-0498 | 0477C |  | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
1 | Horizontal orientation required for cleaning in place - Hose (note 31) | Drain orentation changed to horizontal | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M10A/C |  | VALV-12230289 VALV-12230290 | 0478C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
1 | NOTE 56 OF I-DE-3010.2S-1223-944-S2N-003 to be updated by process as per vendor requirements. (3D) | I-DE-3010.2S-1223-944-S2N-003 | None | PRO | OPEN |  | None |  | None | None | PRO | None | None | M10A/C |  | ESP-12238001 | 0479C |  |  |  | PB - Operation | None |  | None | None
4 | Junstion box to be relocated, to clear the drain accessibility | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | JBI-1421-105 | 0480C |  |  |  | PB - Operation | None |  | None | None
4 | Light fixture and instrument stands to relocate to clear utility connections VALV-12232514 & VALV-12232516 | Electrical Response : light fixture Removed and lux level achieved with Flood light | None | ELE | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | LNO-218-16-M10A-004 PDG-1223007C PIT-1223036B PIT-1223036C | 0481C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Flange OD mismatch to be fixed | Model updated properly | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | No piping dcn required | M10A/C |  | 12"-PC-B16N-0260-PP | 0482C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
3 | Model penetration sleeve | Sleeve penetration modelled | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | No piping dcn required | M10A/C |  | PC-0257 | 0483C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
4 | PIT tapping can be taken in horizontal. Access reserve volume around instrument to be modeled. TIT to be cleared of interence with cable tray. | PIT tapping taken in horizontal. Access reserve volume around instrument modeled. TIT cleared with cable tray. | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | no piping DCN required | M10A/C |  | PC-0259 | 0484C |  | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
4 | PIT for the degassers should be directly on vessel top, PB agrees that valves can be category 3. 600mm reserve space for access required (permanent access not required). | PIT for the degassers directly mouinted on vessel top | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | Piping DCN REQUIRED | M10A/C |  | VALV-12230619 VALV-12230618 VALV-12230448 VALV-12230541 | 0485C |  | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
2 | Model a reserve volume for spectacle blind removal | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | ESP-12230303 ESP-12230182 | 0486C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Ensure lines terminate within tundish | lines are terminated within tundish | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M10A/C |  | DA-3399/3400/3401/3402 | 0487C |  | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
2 | First closed drain block valve to be installed at the vessel TO-1223001/2-A/B. Second block valve to be located close to first block valve. PB Operations agrees to change valve to category 3. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | VALV-12232484 VALV-12230500 VALV-12230502 VALV-12232454 VALV-12232455 VALV-12232456 VALV-12232457 VALV-12232492 VALV-12230701 VALV-12230705 VALV-12232460 VALV-12232461 VALV-12232462 VALV-12232463 VALV-12230498 VALV-12231651 | 0488C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Isolation valve need to be kept as close as possible to nozzle. PC-2319-N4A,PC-2342-N4A. Typical for TO-1223001/2-A/B | Isolation valve kept closed to the nozzle | KBR | PIP | RE-OPEN | 21/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M10A/C |  | VALV-12230523 VALV-12230496 VALV-12230699 VALV-12230661 | 0489C | 23/01/2026 | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
2 | Evaluate moving sample collection point to the marked location to meet the 4m distance requirement | Sample collection point moved to the marked location. | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M10A/C |  | ESP-12230434 | 0490C |  | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
2 | Valve to be modelled for CIP-12230034, CIP-12230009 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | PC-2694 PCW-0017 | 0491C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Hydrotest vent point to be flanged. | Hydrotest vent point changed to flange. | KBR | PIP | Pending PB Reply | 05/01/2026 | None |  | None | None | PIP | None | DCN required | M10A/C |  | PC-0850 | 0492C | 23/01/2026 | 1.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
4 | Remove the coaming plate, only penetration sleeve with 150mm height with watertight fire seal is sufficient as confirmed by PB - confirm with Safety | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | PC-0395 PC-0238 | 0493C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Emergency stop button height to be reduced and rotated toward escape route to provide accessibility | Awaiting KSB vendor response. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M10A/C |  | B-1223001A/B | 0494C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Water and air piping to be connected with Equipment TP | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | IA-1178 W-3646 W-3647 | 0495C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Category 1 valves to be within the height limit for ergonomics | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | VALV-12230399 VALV-12232467 | 0496C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | PIT tappings to be taken at 3 or 9 o'clock position for dirty service. Also acceptable to have elbows in horizontal plane. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | PIT-1223059A/B PIT-1223057A/B PIT-1223062 | 0497C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment coaming to be updated to cover drain | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | B-1223001A/B | 0498C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Low point drain to be provided after check valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | VALV-12230428 | 0499C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain valves to be updated to horizontal position for clean in place connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | VALV-1223420/421/630/631 | 0500C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Please provide details on the chromatography panels for module M-04. It is necessary to define and include the electrical power supply and instrumentation points. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | SPCS-1235003-01 SPCS-1235003-02 SPCS-1235003-03 SPCS-1235003-04 SPCS-1235003-05 SPCS-1235003-06 SPCS-1235003-07 SPCS-1235003-08 SPCS-1235003-09 SPCS-1235003-10 SPCS-1235003-11 SPCS-1235003-12 SPCS-1235003-13 SPCS-1235003-14 SPCS-1235003-15 | 10360C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | The piping needs to be supplemented. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | T-01-SPCS-1235003-02 T-01-SPCS-1235003-10 T-01-SPCS-1235003-11 T-01-SPCS-1235003-12 T-01-SPCS-1235003-01 T-01-SPCS-1235003-04 T-01-SPCS-1235003-05 T-01-SPCS-1235003-06 T-01-SPCS-1235003-07 T-01-SPCS-1235003-08 T-01-SPCS-1235003-09 T-01-SPCS-1235003-13 T-01-SPCS-1235003-14 T-01-SPCS-1235003-15 T-01-SPCS-1235003-3 | 10361C | 15/02/2026 |  |  | PB - Operation | None |  | None | None
None | Panel installed in a location difficult to access for maintenance, without access to the instruments and side connections. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | SPCS-1235003-8 | 10362C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Painels location needs to be finalized so that the electrical cable trays, penetrations and supports can be modeled | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-04 |  | PN-AIT-1235804A PN-AIT-1235804B PN-AIT-1235804C | 10363C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Tappoint connection point is needed to link the orifice plate taps to the flow transmitter. | 04-12-25: FIT tapping connections model updated. | KBR | PIP | Pending PB Reply | 03/12/2025 | None |  | None | None | PIP | None | No piping DCN required | M-04 |  | FE-1235808A/B/C - FE-1235811A/B/C | 10364C |  | 14.0000000000000 | 21.0000000000000 | PB - Operation | None |  | None | None | 06/12/2025 | 20/12/2025 | 22/12/2025 | 22/12/2025 | 21/12/2025 | 07/12/2025
None | Tapping point very close to the panels (SPCS-1235003-9 and SPCS-1235003-1). | 09-01-26: SPCS-1235003-9/1 panel is relocated. | KBR | CSE | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | INST | None | None | M-04 |  | FE-1235809C | 10365C | 26/02/2026 | -1.00000000000000 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
None | Motor access to be checked with Skid Vendor | Awaiting a response from vendor PERONI | PB Ops | MECH | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | MOTOPUMPA_PXCA40_11 | 10366C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
None | CCTV and fire hydrant to be adjusted as per snapshot | 06-01-CCTV has been adjusted as per the snapshot by Telecom. Fire hydrant action needs to be taken | KBR | PIP | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M10A |  | I-DE-3010.10-5423-944-S2N-165 | 10367C | 28/01/2026 | 3.00000000000000 | -1.00000000000000 | SEA/KBR | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
None | Accessability to be ensured for the speaker. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10A |  | COR-5518189B | 10368C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | CCTV to be relocated as per snapshot. Pipe blockage due to CCTV installation height is accepted by PB. | CCTV has been relocated as per the screenshot. | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M10A |  | CAM-5514046 | 10369C | 28/01/2026 | 3.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
None | Flarme detectors to be relocated as per snapshot, because of cabling issue. | 17/12/25 - Flame detectors is a F&G devices handle by Safety & not CSE. | PB | CSE | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | SPI-M10A-118 | 10370C |  |  |  | PB - Engineering | None |  | None | None
None | Spearker to slightly relocated, possibility to attach to the pipe support to be explored. Flarme detectors to be relocated as per snapshot | 06-01-The speaker has been slightly relocated. Pipe support mounting and Flame detectors relocation pending as per snapshot. | KBR | PIP | RE-OPEN | 05/01/2026 | None |  | None | None | TEL | None | None | M10A |  | I-DE-3010.2S-5124-944-S2N-003 & UST-M10A-102-004 | 10371C | 28/01/2026 | 2.00000000000000 |  | PB - Engineering | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | CCTV to be relocated as per snapshot. | CCTV has been relocated as per snapshot | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M10A |  | CAM-5514048 | 10372C | 28/01/2026 | 3.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
None | Beacon support to be extended. | Beacon support is extended as per comment | KBR | TEL | Pending Seatrium Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M10A |  | BLE-5511177, BLE-5511180, BLE-5511184 | 10373C | 28/01/2026 | 2.00000000000000 |  | SEA/KBR | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | Electrical cable tray to be modified to provide access to the equipment on the beam. Refer to snapshot | Electrical cable tray modified to provide better access to the equipment on the beam. | PB | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M10A |  | EC-M10A-L-E-TRAY-40561 | 10374C |  | 5.00000000000000 |  | PB - Engineering | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | CCTV to be relocated as per snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10A |  | None | 10375C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
None | Spearker to slightly relocated,to avoid the cable blocking the lighting. Refer to snapshot. | Speaker is slightly relocated as per snapshot | KBR | TEL | RE-OPEN | 05/01/2026 | None |  | None | None | TEL | None | None | M10A |  | COR-5518203A | 10376C | 28/01/2026 | 2.00000000000000 |  | PB - Operation | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | Speaker to be relocated as per mark-up. | Speaker has been relocated as per screen shot | KBR | TEL | RE-OPEN | 05/01/2026 | None |  | None | None | TEL | None | None | M10A |  | SPP-M10A-00059 | 10377C | 28/01/2026 | 2.00000000000000 |  | PB - Engineering | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | Telecom Secondary trays, Penetrations and Supports are missing for Telecom equipment. General for M10A/C | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10A |  | General | 10378C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Speaker to be relocated as per mark-up. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10A |  | COR-5518209B | 10379C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | CCTV to be relocated as per snapshot | CCTV thas been relocated as per snapshot | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M10C |  | CAM-5514060 | 10380C | 28/01/2026 | 3.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
None | Flarme detectors to be relocated as per snapshot, because of cabling issue. | 17/12/25 - Flame detectors is a F&G devices to be handle by Safety & not CSE. | PB | CSE | OPEN |  | None |  | None | None | SAF | None | None | M10C |  | SPI-M10C-102-023 | 10381C |  |  |  | PB - Engineering | None |  | None | None
None | CCTV to be relocated as per mark-up, where the Spearker located. Speaker to be relocated nearby/on the column. | CCTV has been relocated as per the markup. The speaker has also been relocated. | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M10C |  | CAM-5514062 | 10382C | 28/01/2026 | 3.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
None | CCTV to be relocated as per mark-up, Floodlight height to be adjusted. | None | KBR | TEL | OPEN |  | None |  | None | None | ELE | None | None | M10C |  | CAM-5514063, SPL-M10C-00338 | 10383C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | CCTV to be relocated as per mark-up, Floodlight location to be adjusted. | None | KBR | TEL | OPEN |  | None |  | None | None | ELE | None | None | M10C |  | CAM-5514064, SPL-M10C-00427 | 10384C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
None | Speaker and light to be slightly shifted for the cables bending and termination as per mark-up | Speaker and light has been adjusted as per comment | KBR | TEL | Pending Seatrium Reply | 05/01/2026 | None |  | None | None | ELE | None | None | M10C |  | SPL-M10C-00414 | 10385C | 28/01/2026 | 2.00000000000000 |  | PB - Operation | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | Ensure sufficient space is provided to access the MCT for installation purposes. A stool-type foundation shall be provided to maintain a 250–300 mm clearance between the existing structural foundation and the vendor-supplied foundation. This clearance is required to allow proper access to the MCT for cable pulling and for tightening the MCT during the integration phase. (Applicable for A &amp; B Package) | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | ug2389388zmk001_01 | 10386C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Provision of tray shall be considered below terminal box / package skid. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | B-1223001A/B - PRE-OIL DEHYDRATOR RECIRCULATION WATER PUMP | 10387C | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
None | The emergency push button shall be relocated and rotated 90º. (Vendor Package) | Awaiting KSB vendor response. | PB | MECH | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | B-1223001A - PRE-OIL DEHYDRATOR RECIRCULATION WATER PUMP | 10388C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | The instrument/electrical cable tray (IT-M10A-S-I-TRAY-01033 & EC-M10A-L-N-TRAY-00112) shall be relocated to provide access to terminal box. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | B-1223001A - PRE-OIL DEHYDRATOR RECIRCULATION WATER PUMP | 10389C | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Adjust/shift air filter box to ensure access to it not blocked by structural column. | Awaiting KSB vendor response. | PB | MECH | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | B-1223001A - PRE-OIL DEHYDRATOR RECIRCULATION WATER PUMP | 10390C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Lighting JB to be shifted away from access space for the air filter box door opening | Lighting Junction Box relocated. | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10391C | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate cable tray away from access space to air filter box. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | EC-M10A-L-N-TRAY-00115 | 10392C | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Vendor terminal box to be shifted and ensure accessibility to it is unblocked by pipe support. (by vendor) | Awaiting KSB vendor response. | PB Ops | MECH | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | B-1223023A/B, B-1223003A/B - OIL TRANSFER PUMP | 10393C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | Adequate cable termination space below terminal box to be provided. (by vendor). Motor terminal box to be elevated and small cable tray to be included. | Awaiting KSB vendor response. | PB Ops | MECH | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | M-B-1223002 A and B | 10394C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | Update MCT model using size with 300mm height from deck level to top of MCT. | MCT has been updated using size with 300mm height from deck level to top of MCT. | SEA | ELE | Pending PB Reply | 05/12/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10A |  | E-M10A-M-MCT-007 | 10395C |  | 14.0000000000000 | 19.0000000000000 | SEA/KBR | True |  | None | None | 08/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 08/12/2025
None | Provide tray supports, as required. | Tray supports are provided | PB Ops | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10A |  | ET-M10A-L-N-TRAY-10014-TRAY-0101 | 10396C |  | 8.00000000000000 | 19.0000000000000 | PB - Operation | True |  | None | None | 14/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 14/12/2025
None | Pipe routing to be modified to avoid the HV cable tray | None | SEA | PIP | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10397C | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Adjust location of lighting panel to clear the access way for terminal box. Trays to be relocated too, to ensure accessibility of terminal box. | Proper and clear accessibility of terminal box lighting Panel & Tray have been relocated. | PB | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10C |  | M-B-1223001D, PCC-5263210A and cable trays ET-M10C-L-E-TRAY-10007, EC-M10C-L-N-TRAY-00103 | 10398C |  | 20.0000000000000 | 18.0000000000000 | PB - Engineering | None |  | None | None | 03/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 03/12/2025
None | Emergency push button shall be relocated, to create space for access. | Awaiting KSB vendor response. | PB | MECH | OPEN |  | None |  | None | None | ELE | None | None | M10C |  | M-B-1223001D | 10399C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | The cable tray IT-M10C-S-I-TRAY-01019 shall be relocated. | None | PB | CSE | OPEN |  | None |  | None | None | INST | None | None | M10C |  | M-B-1223001D - The cable tray IT-M10C-S-I-TRAY-01019 | 10400C |  |  |  | PB - Engineering | None |  | None | None
None | The auxiliary terminal box (Air filter - EXPO ML 571) of the M-B-1223001C shall be relocated (Obstruction by Structure Column). (by vendor) | Awaiting KSB vendor response. | PB | MECH | OPEN |  | None |  | None | None | ELE | None | None | M10C |  | None | 10401C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Electrical/instrument trays to be relocated to ensure it is not blocking any access for auxilliary boxes from package. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10C |  | None | 10402C | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Vendor tray to be revised to accommodate electrical cables. Sufficient termination space below terminal box to be provided. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10C |  | B-1223002C/D | 10403C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Ensure sufficient space is provided to access the MCT for installation purposes. A stool-type foundation shall be provided to maintain a 250–300 mm clearance between the existing structural foundation and the vendor-supplied foundation. This clearance is required to allow proper access to the MCT for cable pulling and for tightening the MCT during the integration phase. (to apply to M10C related equipment) | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10C |  | None | 10404C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Bring tray at rear side of JB, to unblock font JB access (typical). | Lighting Tray Re-routed to provide better access to JB | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M10A |  | CXN-L-M10A-057 | 10405C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | JB to be relocated nearby with 1.3m. case by case Change mounting height of lighting JB to 1.8m. PB agreed for height upto 1.8m. | Lighting JB elevated as per PB agreed height upto 1.8m. | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M10A |  | CXE-L-M10A-207 | 10406C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Re-arrange JBs to improve accessibility of equipment. PB agreed for height upto 1.8m | Lighting JB Relocated / Re arranged to improve accessibility of equipment. | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M10A |  | CXE-L-M10A-307 CXE-L-M10A-303 | 10407C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Relocate JB to a more accessible location. | Lighting JB Relocated to have better access | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M10A |  | CXN-L-M10A-010 | 10408C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Relocate JB to a more accessible location. | Lighting JB Relocated to have better access | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M10A |  | CXN-L-M10A-009 | 10409C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Relocate JB as per snapshot | CXN-L-M10A-023,CXN-L-M10A-024,CXN-L-M10A-030 Junction box relocated as per comments | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | CXN-L-M10A-023 CXN-L-M10A-024 CXN-L-M10A-030 | 10410C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Electrical panel/box to be shifted away from tubing tapping point. | Pipe value flange has been relocated and shifted away from tubing tapping is point. | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M10A |  | CX-TO-1223001A-B | 10411C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Relocate JB to a more accessible location. Refer to the snapshots | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | CXE-L-M10A-337 CXN-L-M10A-049 | 10412C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Ensure that all sub-cable trays are properly terminated and connected to the bottom of each JB. All lighting fixtures shall be connected using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all lights and JB within Module M10A/C | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10413C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Lighting and Instrument cable support to be relocated slightly to avoid the lighting close proximity to the structure. | Instrument support slighty relcolated down side | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10414C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Lighting to be shifted/reoriented to avoid the pipe (Currently close to the pipe) | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10415C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Floodlight to be considered same as what was done in M10C. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10416C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | No glanding space. Extend support arm to create space for glanding. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10417C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate lighting fixture and change mounting type to beam mounted. | Light fixture ounted on beam | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10418C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Cable ladder to move right to have better bending radius. | 24-12-25 : Cable Ladder is moved to right for sufficient bending radius towards JB. 08-01-26 : Please refer close out Snapshot 2 for more clarification on the cable ladder shifted to the right. | PB Ops | CSE | Pending PB Reply |  | U5D6 | 04/01/2026 | [U5D6 -05/JAN/2026] Closeout snapshot does not show the cable ladder shifted to the right. It is in the same position as before. | None | INST | None | 28-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) 10-JAN-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10A |  | None | 10419C |  |  | -1.00000000000000 | PB - Operation | None |  | None | None |  | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026
None | Cable ladder support to be included | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M10A |  | None | 10420C |  |  |  | SEA/KBR | None |  | None | None
None | The RIO Panel Platform needs an explanation of how it will be bolted to the RIO foundation or to the main/secondary structural beams. Also the Coaming around RIO Panel has to be removed as per agreed TQF | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-10A/C |  | PN-5520110C-01 | 10421C |  |  |  | SEA/KBR | None |  | None | None
1 | Pulling post inside gutter to be relocated | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | PP-M11-1001-10MT PP-M11-1001-10MT | 20001C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Cable tray to be relocated away from equipment panel cover swing open direction | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-11 |  | B-1251002A/B/C | 20002C | 15/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Handing path width should be 1000mm for pump handling. Add corner radius in the handling path. Update the 2D drawing as per latest 3D model. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | B-1251001A | 20003C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Speakers to be relocated from handling volume. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-11 |  | COR-5518268B | 20004C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 Mezz | Only handling obstruction volume to be provideed under the bracing for stacker operation space during valve handling. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | PV-1251001 | 20005C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 Mezz | Padeyes 2d drawing to be updated inline with 3D model | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | XV-1251005 XV-1251003C | 20006C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 Mezz | Pipe to shift away from hatch volume. Pipe should use nearby structure as shield. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-11 |  | None | 20007C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Model handling path between the 2 exchangers | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | None | 20008C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 and 2Mezz | General comment: Check for pulling post or any other pulling device to reach the loading area of this 15.1t valve | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | VALV-12510060 VALV-12510296 - 15.1 Ton VALV-12510370 - 11.2 Ton VALV-12510371 - 11.2 Ton | 20009C | 21/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Application for both exchanger. Davit for cover to be modelled. Lifting points for cover and bundle to be shown and model the lifting and pulling lugs. 3D model for shell and tube exchanger to be updated, showing the tunion and davit and liftings points. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | P-1251001A/B | 20010C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Padeyes located in M12 for pulling the exchanger to be moved further towards AFT aside. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | P-1251001A/B | 20011C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Handling path and volume to be model for exchanger handling | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | P-1251001A/B | 20012C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Telecom item and stanchion post to be relocated away from handling volume. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-11 |  | P-1251001A/B | 20013C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Safety shower to relocate away from dropzone lifting | Safety shower has been shifted away with the piping at more than 300mm away from the dropzone. | KBR | PIP | Pending Seatrium Reply | 23/12/2025 | None |  | None | None | SAF | None | None | M12 |  | P-1251001A/B | 20014C |  | 15.0000000000000 |  | PB - Operation | None |  | None | None | 26/12/2025 |  |  |  |  | 28/12/2025
1 | Handling of whole heat exchanger to be studied and reserved the handling volume. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | P-1251001A/B | 20015C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Cable tray, lighting, jb to be relocated away from east side of column for heat exchanger handling. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-11 |  | P-1251001A/B | 20016C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Removable handrail, requires kickplate and socket to be removable as well during maintenance of heat exchanger bundle to avoid clash with bottom nozzle. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-11 |  | P-1251001A/B | 20017C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
2 Mezz | Handrail to be provided as removable type, following the STR standard, each piece to be max 2.1m length per removable handrails. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-11 |  | None | 20018C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Telecom equipment Tag No: TS-M11-TELE-EQP to be relocated to clear clash with handling path | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-11 |  | None | 20019C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Update the lifting volume including coming out from the starboard handrail | None | None | HAND | OPEN |  | None |  | None | None | CSE | None | None | M-11 |  | None | 20020C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Cable tray to relocation away for valve removal | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-11 |  | LV-1251002-1 | 20021C | 15/02/2026 |  |  | PB - Operation | None |  | None | None
above level 4 | PSV weight to be clarified. If weight is more than 40kg, handling to be provided for PSV handling | None | None | HAND | OPEN |  | None |  | None | None | PIP | None | None | M-11 |  | PSV-1251003A/B | 20022C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | General comment for 3 compressors: Pipe clashing with monorail handling volume to be removable type by adding flanges. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | UC-1254001A/B/C | 20023C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Telecom fixture clash with handling path, shift the fixture LSE-5518001B/SPP-M02-00059 | None | KBR | TEL | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | UC-1254001A/B/C | 20024C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 | General comment for 3 compressors: Heat exchanger end plate shall be completely pull out till end of the bolt. Removable spool is required and should be small enough to easily remove. Cable tray to reroute as well to avoid clash. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | UC-1254001A/B/C | 20025C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Maintenance space for plate heat exchanger clashing with column. Handling to provide lifting beam for end plate complete removal. Lights/instrument to be relocated if is clashing. | None | None | ELE | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | UC-1254001A/B/C | 20026C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | To check with vendor if there is sufficient space for Heat exchanger maintenance when the handrail kick plate is limiting the End plate from coming out fully. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-02/M-05 |  | UC-1254001A/B/C UC-1231001A/B/C | 20027C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | KBR to provide philosophy on mechanical handling for internal part of the scrubber. (Typical for all scrubber) | Please check this document I-PR-3010.2S-1200-540-HM9-001 | None | MECH | Pending PB Reply | 06/01/2026 | None |  | None | None | CSE | None | None | M-02 |  | V-UC-1254001C-01 | 20028C | 29/01/2026 | 1.00000000000000 |  | PB - Operation | None |  | None | None | 09/01/2026 |  |  |  |  | 11/01/2026
2 | Shift the padeye on to the secondary beam | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | SDV-1254021A-1 | 20029C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Valve handling to be checked. If handling by using roller platform, provided temporary pulling post / using existing pipe support if it can withstand the load. | None | None | HAND | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | VALV-12540302 | 20030C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Handling to be re-checked , Valve catalogue updated post DR60 Tag closure.Valve Tag number : XV-1254042A,XV-1254041A, XV-1254042B ,XV-1254041B ,XV-1254041C | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | XV-1254042A XV-1254041A XV-1254042B XV-1254041B XV-1254041C | 20031C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Add Handling volumes on interconnection from M-02 to M-05B | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | None | 20032C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Padeye direction to rotate towards handling swing direction. | None | None | HAND | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | PE-M-02-2005 PE-M-02-2006 | 20033C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Breakup spool to be provided at the mark up locations for sprinkler lines (6 locations) | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | None | 20034C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Add missing Handling path obstructions volume. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | None | 20035C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Instrument item need to be relocated to clear the obstruction from the valve handling. | 17/12/25 - F&G devices is a Safety item and need to be resolve by Safety | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | AST-CO2-M02-401-008 SPI-M02-416 | 20036C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Relocate the speaker from the drop zone. Relocate the light fixture away from thedrop zone -too close to crane operation. | None | KBR | TEL | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | LEM-319-04-M02-001 SPP-M02-00047 | 20037C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Show handling volume at in field area. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | None | 20038C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
5 | To relocate the flood light to handle the valve along port side. Relocate the cable tray to clear valve handling. | None | None | ELE | OPEN |  | None |  | None | None | TEL | None | None | M-02 |  | FV-1254004C | 20039C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Speaker to be relocated to clear clash with terminal box handling. | None | KBR | TEL | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | COR-5518051B | 20040C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 | removable spool to be provide. Typical for all the compressor. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-05 |  | 1&quot;-OL-B3-0119-NI 1&quot;-OL-B3-0139-NI 1&quot;-OL-B3-0142-NI | 20041C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 | General comment for 3 compressors: Heat exchanger end plate shall be completely pull out till end of the bolt. Removable spool is required and should be small enough to easily remove. Cable tray to reroute as well to avoid clash also there is a plate there which need to recheck if it is clashing with heat exchanger maintenance. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | ELE | None | None | M-05 |  | UC-1231001A/B/C | 20042C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | KBR to provide the sufficient space for plate heat exchanger maintenance and removal. (Typical for all other compressor) | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-05 |  | UC-1231001A/B/C | 20043C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipe routing to be shifted away or pipe flange to be provided for rotor handling. | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M-05 |  | UC-1231001C 1&quot;-FW-B7-1726-NI | 20044C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipe to be relocated to clear clash with valve handling volume. | None | None | PIP | OPEN |  | None |  | None | None | TEL | None | None | M-05 |  | 1&quot;-FW-B7-2072-NI SDV-1231058C-1 | 20045C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
2 | KBR to model the turning radius volume. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05 |  | SDV-1231058C-1 | 20046C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
3, 4 | Lifting lug to be modelled as per GA for the suction and discharge cooler heat exchanger. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | P-UC-1231001A/B/C-01 P-UC-1231001A/B/C-02 | 20047C | 01/02/2026 |  |  | PB - Operation | None |  | None | None
3 | General comment for all 3 exchanger: provide removable flange for the sprinkler line as per the markup. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | P-UC-1231001A/B/C-02 | 20048C | 02/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Valve Handling to be done once final valve weight and catalogue is updated.( both valves) | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05 |  | 16"-PC-E30N-2757-NI (XV-1231011A) 16"-PC-E30N-2758-NI (XV-1231011B) | 20049C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Padeye need to be oriented inline with handling direction | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05 |  | VALV-12310561 | 20050C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Missing Handling paths to be modelled. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05 |  | None | 20051C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Provide additional padeye and handling by swing transfer along FWD side as the space is less infront of the valve. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05 |  | VALV-12310590 | 20052C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Handling path need to be remove inline with 2D drawing. As in no handling path required on the bridge interconnection due to both module have their own drop zone area. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05 |  | None | 20053C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Model swing volume big enough for the Actuator Valve | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-04 |  | UC-UT-1238001A/B | 20054C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Movement of deck trolley with biggest item or flow meter in lie down position to be shown at this corner turning out. Show there is sufficient handling path width. | Movement of Manual trolley with Largest Flow meter in M10B has been simulated. No clash was observed in the route. | KBR | HAND | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | HAND | None | None | M-04 |  | None | 20055C | 30/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
2 | Handling transport route to be model in M-04 instead in M-06 | MH Handling volume has been placed in M04 model | KBR | HAND | Pending PB Reply |  | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M-04 |  | None | 20056C | 09/01/2026 |  | 10.0000000000000 | PB - Operation | True | 07/01/2026 | True | None |  | 01/01/2026 | 09/01/2026 | 11/01/2026 | 01/01/2026
2 | Handling volume to be modelled and the light to be relocated away from handling volume. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-04 |  | FE-1235812A | 20057C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
2 | MH volume to be added to reserve the volume for actuator removal, check the possibility of relocating the JB or change to removable support. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-04 |  | SDV-1235806A | 20058C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
2 | MH need to simulate the movement of actuator till main handling route. | The movement of Atuator has ben simulated | KBR | HAND | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | HAND | None | None | M-04 |  | None | 20059C | 30/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
2 | MH volume to be reduced to fit the purpose of handling. Cable tray to be routed behind the valve. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-04 |  | IC-M04-S-S-TRAY-02003-TRAY-0001 | 20060C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Structure to provide removable handrail on the aft side for valve handling | None | None | STR | OPEN | 22/12/2025 | None |  | None | None | HAND | None | None | M-04 |  | None | 20061C | 28/01/2026 | 16.0000000000000 |  | PB - Operation | None |  | None | None | 25/12/2025 |  |  |  |  | 25/12/2025
3 | Lifting points on valve to be define. Handling path width to be checked with reference to valve orientation placed on deck trolley/transport equipment. | FV-1235808A to be handled by scaffolding the lifting points will be Flange Bolt holes. additionalslings to be tied to acuator to avoid overturnig. handling path is suficient considerig the width of valve. VALV-12358102 will ve handled by Aframe as the valve is comparatively lesser height with 600mm plus headroom to lift the vave | KBR | HAND | Pending Seatrium Reply | 09/01/2026 | None |  | None | None | HAND | None | None | M-04 |  | FV-1235808A VALV-12358102 | 20062C | 30/01/2026 | 0 |  | PB - Operation | None |  | None | None | 12/01/2026 |  |  |  |  | 12/01/2026
3 | Relocate the instrument away from flow element handling. | 09-01-26: Instruments relocated. | KBR | CSE | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | CSE | None | None | M-04 |  | FE-1235808B | 20063C | 10/02/2026 | -1.00000000000000 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
3 | Piping & Tubing to add more flanges in the line for ease of removal, also the pipe supports to be of removable type. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | None | 20064C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Provide handling volume to block the path for equipment movement. Instrument to relocated away from handling path. | MH as modeled the Handling volume | KBR | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-04 |  | None | 20065C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Move all the EIT items close together and place them close to the column. Reason is because there is a drop zone and items will be swing around. | None | None | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-04 |  | None | 20066C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | MH swing Volume to be modelled | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-04 |  | None | 20067C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | FGS JB opening to face outwards as current facing inwards do not have much space. | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-04 |  | None | 20068C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Handling space infront of valve to be clear from obstruction. Fire extinguisher support to be removable type, cable trays, tubing and pole to be relocated away from handling volume. | None | KBR | SAF | OPEN |  | None |  | None | None | HAND | None | None | M-04 |  | Z-5428052 | 20069C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Position the A-frame for more width for the valve landing | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-04 |  | BDV-1231047 | 20070C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Turn radius to be added for biggest valve with deck trolley | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-04 |  | VALV-12310093 BDV-1231047 | 20071C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Drop zone volume to be model in. Instrument and lighting to be relocated to avoid getting mashed by crane lifting activity. | None | None | EIT | OPEN |  | None |  | None | None | ELE | None | None | M-04 |  | SPI-M04-444 LNO-210-14-M04-002 SPI-M04-431 | 20072C |  |  |  | PB - Operation | None |  | None | None
1 | M-10A-20073C -1.Details of pump transporting on Roller skates to be provided.2. Pump COG and Lifting points informations required.3.Pump craddle support information to be provided considering the shape of the pump. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10A |  | B-5133001A/B/C | 20073C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Flange to be added for removable pipe. Current flanges provided not sufficient, pipe is too big for placing on transport route. Pipe supports on these removable pipes looks welded onto the pipes, and beams supports to flange for removable. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A |  | B-5133001A/B/C | 20074C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Obstruction volume height to match with pump handling/transportation volume and consider with cradle height | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A |  | B-5133001A/B/C | 20075C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Break up flange to be provided for sprinkler line at the mark up location. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A |  | B-5133001A/B/C | 20076C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Pulling post to be added fro pump transportation. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10A |  | B-5133001A/B/C | 20077C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Typical comment for all modules: The location of the Removable coaming to be shown in 2D Drawing. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A/Gen |  | B-5133001A/B/C | 20078C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipie support to be shifted to clear clash with monorail trolley hoist volume. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A |  | B-5133001A/B/C | 20079C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Breakout flange to be added for motor handling. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A |  | B-5133001B | 20080C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Break up flange to be provided. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A |  | B-5133001B | 20081C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Instrument cable tray to be shifted for terminal box access. Push button to shift closer to motor. | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-10A/M-10C |  | B-1223001B B-1223001D | 20082C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Move the instrumentation items closer to skid B along Fort side as close as possible, where the column along the handling path closest obstruction | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-10A |  | PDA-M10A-E-01 HSH-5424505A-1 HSS-M10A-101-L001 | 20083C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Pump handling Simulation and turning radius to be provided. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10A |  | B-1223001B | 20084C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Skid A and C Terminal Box handling using Beam clamp to be modelled. | Beam clamps have been added to the model to facilitate handling of the Skid A and C terminal boxes. | PB | HAND | Pending PB Reply | 14/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared, 1MT lifting beam & beam clamps added for both skids. | M-10A |  | B-5133001A/C | 20085C | 26/12/2025 | 15.0000000000000 | 10.0000000000000 | PB - Operation | True | 07/01/2026 | True | None | 17/12/2025 | 01/01/2026 | 09/01/2026 | 11/01/2026 | 01/01/2026 | 17/12/2025
1 | 1.Sprinkler line to be shifted to clear the handling clash. 2. Provide removable flange for the sprinkler line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A |  | B-5133002AB | 20086C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Beam clamp to be modelled. | Beam clamps have been added to the model to facilitate handling. | PB | HAND | Pending PB Reply | 14/12/2025 | None |  | None | 07.01.2025_B0RG_RE-OPEN_It is necessary to provide break flanges at deluge lines or fill the obstruction volume to be detected on clash report | HAND | None | 30Dec2025_Cleared. | M-10A |  | B-5133002A | 20087C | 26/12/2025 | 15.0000000000000 | 10.0000000000000 | PB - Operation | True | 07/01/2026 | False | None | 17/12/2025 | 01/01/2026 | 09/01/2026 | 11/01/2026 | 01/01/2026 | 17/12/2025
1 | A-frame to be model for valve handling and also for lifting across the coaming. Handling to ensure there is no clashes with the lighting and telcom items on the nearby STR columns. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10A |  | HV-1223045A/B | 20088C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1mezz | Beam Clamp to be modelled for VALV-51330041. check to relocate CAM-5514047 camera towards starboard side. | MH 05/01/2026:Beam clamp has beem modelled . telecom has to relocate the camera | KBR | TEL | OPEN | 04/01/2026 | None |  | None | None | HAND | None | None | M-10A |  | VALV-51330041 | 20090C | 09/02/2026 | 3.00000000000000 |  | PB - Operation | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
1mezz | 1.A-Frame to be modelled for handling the valve. 2.Handling path to be show in 2D. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10A |  | XV-5133012A | 20091C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1mezz | Turn radius to be added. | Turn radius has been added. | PB | HAND | Pending PB Reply | 21/12/2025 | None |  | None | 07.01.2025_B0RG_RE-OPEN_Turn radius floor should be connected with the last one. Now, the model is missing the big handling path floor. | HAND | None | 30Dec2025_Cleared. | M-10A |  | None | 20092C | 26/12/2025 | 8.00000000000000 | 10.0000000000000 | PB - Operation | True | 09/01/2026 | False | None | 24/12/2025 | 01/01/2026 | 11/01/2026 | 11/01/2026 | 01/01/2026 | 24/12/2025
2 | Valve handling to be modelled in | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10A/M-10C |  | SDV-1223012A SDV-1223012B | 20093C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1mezz | Handrail at 1mezz to be made removable type | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-10A/M-10C |  | OFHR-M10C-0000012 OFHR-M10C-0000060 | 20094C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Handling obstruction volume to be modelled. | MH 0/01/2026: OBST Volume has been modelled TRAY (ELE)to be re-routed . | KBR | ELE | OPEN | 04/01/2026 | None |  | None | None | HAND | None | None | M-10A/M-10C |  | TF-TO-1223001B-A/B TF-TO-1223002B-A/B | 20095C | 05/02/2026 | 3.00000000000000 |  | PB - Operation | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
3 | Cable tray to be shifted to clear handling obstruction. | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-10A/M-10C |  | TF-TO-1223001B-A TF-TO-1223002B-B | 20096C |  |  |  | PB - Operation | None |  | None | None
3 | 1.Spool handling to be modelled.2. Cut opening for handling access to have coaming and grating ( Check with safety if acceptable). 3.JB to be shifted.4. Beam clamp to be modelled at level 2. 5. platform to be made removable type. 6. Handling transport route to be connected to main handling path. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10A/M-10C |  | FE-1223053A FE-1223053B SDV-1223051A SDV-1223051B | 20097C | 21/01/2026 |  |  | PB - Operation | None |  | None | None
3 | 1.provide turning radius. 2.check to extend the handling path. | Turning radius and handling path is provided as per the requirement. | KBR | HAND | RE-OPEN |  | None |  | None | None | HAND | None | None | M-10A |  | SDV-5133006 | 20098C | 26/12/2025 |  | 2.00000000000000 | PB - Operation | None |  | None | None |  | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026
4 | Removable flange to be provided for sprinkler lines. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A/M-10C |  | P-1223001A/B/C P-1223001D/E/F | 20099C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1.Pipe lines to be shifted to clear handling clash. 2 light fixture to be shifted to clear handlig clash (too close /clashing). | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-10A/M-10C |  | P-1223001A/B/C P-1223001D/E/F | 20100C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Multiple pulling post with smaller SWL can be used. KBR to ensure proposal for pulling post will meet the minimum pulling length. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10A/M-10C |  | P-1223001A/B/C P-1223001D/E/F | 20101C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Cable tray to be relocated. Too close to bundle pulling rope. | Cable tray Relocated. | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-10A |  | P-1223001A/B/C | 20102C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1.Handling obstruction volume for bundle to be modelled. 2.instrumentation item to be clear of bundle obstruction. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10A |  | P-1223001A/B/C | 20103C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Scaffolding volume to be updated including a person standing infront of the manhole. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A/M-10C |  | P-1223001A/B/C P-1223001D/E/F | 20104C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
4 | A-frame to be modelled. | A-Frame has been modeled for both M10A/M10C. | PB | HAND | Pending PB Reply | 23/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M-10A/M-10C |  | SDV-1223051A SDV-1223051B | 20105C | 26/12/2025 | 6.00000000000000 | 10.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 26/12/2025 | 01/01/2026 | 11/01/2026 | 11/01/2026 | 01/01/2026 | 28/12/2025
5 | Light fixture to be shifted to clear clash with wrench clearance volume for flange bolt removal.(shift away from valve) | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-10A |  | LNO-218-24-M10A-002 | 20106C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1mezz | Beam clamp clash to be cleared (Check to handle using A-Frame) | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10C |  | SDV-1223038B | 20107C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1mezz | Beam clamp clash to be cleared (Check to handle using A-Frame) | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10C |  | SDV-1223066 | 20108C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1mezz | Beam clamp clash to be cleared (Check to handle using A-Frame) | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10C |  | LV-1223044B | 20109C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1mezz | Piping to clear clash with Handling volume (Turning radius) 6"-FL-B7-1903-NI , 6"-FL-B7-1904-NI . | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10C |  | 6&quot;-FL-B7-1904-NI 6&quot;-FL-B7-1903-NI | 20110C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Handling path clash to be cleared. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10C |  | ESP-12230480 | 20111C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
3 | 1. Handling to be provided for Spacer/Spool. 2. Provide removable beams to get space for spacer handling. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10C |  | ESP-12230282 ESP-12230126 | 20112C | 21/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Piping to relocate away from handling route | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10C |  | 2"-PC-B30N-1026-PP | 20113C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Lighting to orientate 90 degree | Light Fixture Type changed as per comment | None | ELE | RE-OPEN | 05/12/2025 | None |  | None | None | ELE | None | None | M-10C |  | LNO-220-19-M10C-004 | 20114C |  | 15.0000000000000 | 18.0000000000000 | PB - Operation | None |  | None | None | 08/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 08/12/2025
5 | Lighting to relocate away from drop zone | Light fixture Relocated. | None | ELE | RE-OPEN | 05/12/2025 | None |  | None | None | ELE | None | None | M-10C |  | LEM-341-08-M10C-003 | 20115C |  | 15.0000000000000 | 18.0000000000000 | PB - Operation | None |  | None | None | 08/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 08/12/2025
1 | Provide spool removal flange. | removable flanges provided | None | PIP | Pending PB Reply | 07/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M-10B |  | PC-0271>10"-PC-E16N-0271-HC | 20116C |  | 0 | 0 | PB - Operation | None |  | None | None | 10/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
1 | Handling path clash to be cleared. (Check the final location Z-5428247 and clear clash). | MH: Handling path clash has been resolved | KBR | HAND | Pending PB Reply | 04/01/2026 | None |  | None | 09.01.25_B0RG_CLOSE | HAND | None | 9Jan2026_Cleared. | M-10B |  | Z-5428247 | 20117C | 09/02/2026 | 4.00000000000000 | 0 | PB - Operation | True | 09/01/2026 | True | None | 07/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 07/01/2026
1 | Exchanger maintenance obstruction volumes to be modelled. | Exchanger maintenance obstruction volumes available in model.need to swith on operation volume. | None | PIP | Pending PB Reply | 07/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M-10B |  | P-5331001A/B/C | 20118C | 02/01/2026 | 0 | 0 | PB - Operation | None |  | None | None | 10/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
1 | Removable skid coaming is not required at this location (No MH requirements) Check and delete it. | Removable coaming deleted | KBR | STR | Pending PB Reply | 06/01/2026 | None |  | None | None | STR | None | None | M-10B |  | None | 20119C | 11/01/2026 | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
1 | Handling to clear clash with piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10B |  | VALV-53310328 | 20120C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | 1.Instrument Air tubing shall be shifted away from Escape route and Access route (SDV-5331041). 2.SDV-5331041 valve Access and Handling path to be added. | Tube routing has been modified via below the floor. | KBR | CSE | Pending Seatrium Reply | 04/01/2026 | None |  | None | None | CSE | None | None | M-10B |  | SDV-5331041 IC-M10B-S-I-TRAY-01024 , IC-M10B-S-S-TRAY-01001 | 20121C | 30/01/2026 | 3.00000000000000 |  | PB - Operation | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
1 Mezz | 1.Delete the lifting beam. 2.Cable tray to be relocated clashing with handling volume (IC-M10B-S-S-TRAY-01053 , IC-M10B-S-I-TRAY-01109-TRAY-0005 ) | None | KBR | HAND | OPEN |  | None |  | None | None | STR | None | None | M-10B |  | IC-M10B-S-S-TRAY-01053 , IC-M10B-S-I-TRAY-01109-TRAY-0005 | 20122C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
1 Mezz | Add obstruction volume for A-Frame movement (special case). | MH: OBST volume for A-frame has been modelled | KBR | HAND | Pending PB Reply | 04/01/2026 | None |  | None | 09.01.25_B0RG_CLOSE | HAND | None | 9Jan2026_Cleared. | M-10B |  | XV-5331052B XV-5331052C | 20123C | 09/02/2026 | 4.00000000000000 | 0 | PB - Operation | True | 09/01/2026 | True | None | 07/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 07/01/2026
1 Mezz | 1. Valve handling to be studied. 2. Shift the lift up to clear handling path. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10B |  | TV-5331003 | 20124C | 21/01/2026 |  |  | PB - Operation | None |  | None | None
1 Mezz | Clear Handling path and turning radius clash. | None | None | PIP | OPEN |  | None |  | None | None | CSE | None | None | M-10B |  | None | 20125C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 Mezz | Provide removable handrail at mark up location. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10B |  | None | 20126C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
2 | 1. Valve handling to be re-studied (LV-5331007). 2. Valve transportation volumes to be modelled (simulation). 3. Check the final valve height. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10B |  | LV-5331007 | 20127C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Flow meter transportation to be modelled in vertical position.(typical same method can be followed for others) | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10B |  | CRUDE OIL WELL SERVICE METERING SKID | 20128C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Instrument tubing & penetration to be shifted to clear handling clash. | None | None | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-10B |  | FV-5133041-1 | 20129C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
2 | 1.Provide removable flange at mark up location. potential clash during handling. 2. provide scaffolding volume for the Port side filter also. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10B |  | Z-1212001 | 20130C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
2 | 1.Check with vendor the dimension of the turbine meter and whether it has to be handled as a whole or in parts. 2.transportation of the turbine meter to be provided. | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-10B |  | Z-1212001 | 20131C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | 1. Clear the area for bundle handling (PDA-M10B-E-10 ,AST-CH4-M10B-301-001,PN-1223139-2,LNO-219-13-M10B-003,UST-M10B-301-009,COR-5518229A ) | None | None | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-10B |  | PDA-M10B-E-10 , AST-CH4-M10B-301-001, PN-1223139-2 LNO-219-13-M10B-003 UST-M10B-301-009 COR-5518229A ) | 20132C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handling path obstruction volume to be modelled. | Handling path obstruction volume has been updated in the model. | PB | HAND | Pending PB Reply | 21/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M-10B |  | None | 20133C | 26/12/2025 | 8.00000000000000 | 10.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 24/12/2025 | 01/01/2026 | 11/01/2026 | 11/01/2026 | 01/01/2026 | 24/12/2025
3 | Handling path clash to be cleared. | Handling path clashes has been resolved | KBR | HAND | Pending PB Reply | 04/01/2026 | None |  | None | 09.01.25_B0RG_RE-OPEN_Please to align floor and volume | HAND | None | 9Jan2026_Cleared. | M-10B |  | None | 20134C | 21/01/2026 | 4.00000000000000 | 0 | PB - Operation | True | 09/01/2026 | False | None | 07/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 07/01/2026
3 | Handling path obstruction volume to be modelled. | Handling path volume has been modelled | KBR | HAND | Pending PB Reply | 04/01/2026 | None |  | None | 09.01.25_B0RG_CLOSE | HAND | None | 9Jan2026_Cleared. | M-10B |  | None | 20135C | 09/02/2026 | 4.00000000000000 | 0 | PB - Operation | True | 09/01/2026 | True | None | 07/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 07/01/2026
3 | Handling path clash to be cleared. | Handling path clashes has been resolved | KBR | HAND | Pending Seatrium Reply | 04/01/2026 | None |  | None | None | HAND | None | None | M-10B |  | None | 20136C | 09/02/2026 | 3.00000000000000 |  | PB - Operation | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
3 | 1. Provide removable flange for the sprinkler lines in mark up locations. 2. Clear electrical cable tray clash with | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10B |  | None | 20137C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
3 | valve handling by using beam clamp , clear cable trey clash using inverted goal post structure (VALV-12230716). | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-10B |  | None | 20138C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
3 | 1. Provide removable flange for sprinkler line as shown in the marked location. 2.shift the instrument away from handling direction (HSS-M10B-301-K001). | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10B |  | None | 20139C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Sampler box to be shifted to clear handling path clash ESP-51330107. | None | None | PIP | OPEN |  | None |  | None | None | CSE | None | None | M-10B |  | ESP-51330107 | 20140C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve handling to be re-studied .handle the valve by using Beam clamp. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10B |  | VALV-12230732 | 20141C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve handling to be shown by using Beam clamp. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-10B |  | VALV-12231506 VALV-12231456 | 20142C | 09/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Handling path obstruction volume to be modelled. | The handling path obstruction volume has been updated in the model. | KBR | HAND | RE-OPEN | 21/12/2025 | None |  | None | None | HAND | None | None | M-10B |  | None | 20143C | 26/12/2025 | 17.0000000000000 |  | PB - Operation | None |  | None | None | 24/12/2025 |  |  |  |  | 24/12/2025
5 | 1.piping to clear handling path obstruction volume. 2. model beam clamp and swing simulation. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10B |  | FV-5133041-2 | 20144C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Shift the light away from the direct Deck crane pick up region. | Light fixture Re located as per comments | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-10B |  | None | 20145C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | relocate JB as it is close to LG. | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-10A/C |  | JBIF-1421-310 | 10422C |  |  |  | SEA/KBR | None |  | None | None
None | MCT is closer to the beam. MCT to be adjusted. | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M10A |  | I-M10A-S-MCT-088 | 10423C |  |  |  | SEA/KBR | None |  | None | None
None | JB need to shift by 200mm to clear the accessability of valve handle. | 10-01-26 : JBC-1421-109 is shifted by 200mm to have sufficient space to access the valve 1"-PC-B16N-1638-HC | PB Ops | CSE | Pending Seatrium Reply |  | None |  | None | None | INST | None | None | M10A |  | JBI-1421-105 SPI-M10A-406 | 10424C |  |  |  | PB - Operation | None |  | None | None
None | To evaluate the package panel cable bending radius and ensure the cable ladder is positioned below the cable glands at the required distance to achieve proper cable bending | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M10A |  | PN-B-5133001A/B/C | 10425C |  |  |  | SEA/KBR | None |  | None | None
None | The cable ladder interface between the vendor and KBR is not connected and must be fixed | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-10A/C |  | B-5133002A\B B-5133001A\B\C | 10426C |  |  |  | SEA/KBR | None |  | None | None
None | Vendor drawing for cable tray should be match with Vendor provided 3D model. (Vendor scope) | Awaiting KSB vendor response. | SEA | MECH | OPEN |  | None |  | None | None | INST | None | None | M10A |  | B-1223003A\B | 10427C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | KBR to model and incorporate the necessary supports in accordance with the standard KBR typical drawings for all 90 deg Bends(Typ). | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-10A/C |  | None | 10428C |  |  |  | SEA/KBR | None |  | None | None
None | The tubing tray penetrations shall be reviewed and revised to ensureto use to the agreed penetration type | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-10A/C |  | IT-M10C-T-I-TRAY-04001 | 10429C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. Penetrations to be model as per structure guidelines.. This requirement applies to all Instruments, JB and valves M10A/C | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M10A |  | None | 10430C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | PIT to be relocated to avoid the capiliary | Instrument is relocated near the tapping to avoid Capiliary tray. | KBR | CSE | CLOSE | 26/12/2025 | U5D6 | 04/01/2026 | [U5D6 - 05/JAN/2026] Instrument is very close to tap. Agreed with proposed solution. | None | INST | None | 28-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) NOTE: KBR MUST ENSURE THAT ALL EIT ITEMS ARE CLASHED FREE PRIOR TO THE ISSUANCE OF DELIVERABLES. | M10A | 04/01/2026 | PIT-1223082A | 10431C | 20/02/2026 | 1.00000000000000 | 8.00000000000000 | PB - Operation | None |  | None | None | 29/12/2025 | 30/12/2025 | 01/01/2026 | 01/01/2026 | 30/12/2025 | 29/12/2025
None | PIT to be relocated to provide the valve handle accessability. | Instrument relocated to give the valve accessibility. | KBR | CSE | Pending PB Reply | 26/12/2025 | None |  | None | None | INST | None | 28-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10A |  | PIT-5533028A | 10432C | 20/02/2026 | 1.00000000000000 | 11.0000000000000 | PB - Operation | True |  | None | None | 29/12/2025 | 30/12/2025 |  |  | 30/12/2025 | 29/12/2025
None | Capillary tubing not to corss over. Field instrument (Transmitter) to be swapped as well. | Tapping point is swapped to match with P&D | KBR | CSE | Pending PB Reply | 26/12/2025 | None |  | None | None | INST | None | 28-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10A |  | None | 10433C | 20/02/2026 | 1.00000000000000 | 11.0000000000000 | PB - Operation | True |  | None | None | 29/12/2025 | 30/12/2025 |  |  | 30/12/2025 | 29/12/2025
None | Check the possibilities to relocate the PDA. | PDA has been relocated. | KBR | CSE | Pending PB Reply | 30/12/2025 | None |  | None | None | INST | None | 07-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10A |  | None | 10434C | 20/02/2026 | 7.00000000000000 | 1.00000000000000 | PB - Operation | True |  | None | None | 02/01/2026 | 09/01/2026 |  |  | 11/01/2026 | 04/01/2026
None | Actuator need to be oriented 90 degree | Actuator has been rotated to 90deg. | KBR | CSE | Pending Seatrium Reply | 04/01/2026 | None |  | None | None | INST | None | None | M10A |  | None | 10435C | 20/02/2026 | 3.00000000000000 |  | SEA/KBR | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
None | Level transmitter Diaphr. Capilary - Provide Flushing ring to allow cleaning and reduce maintenance time. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 - For any flanged process connection in which the instrument is connected through a diaphragm seal, a flushing ring shall be provided to allow cleaning and reduce maintenance time. Flushing ring shall be supplied with vent and drain valves as defined in chapter 19. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M10A |  | LIT-1223016A LIT-1223016B LIT-1223018A LIT-1223018B LIT-1223024A LIT-1223024B LIT-1223026A LIT-1223026B LIT-1223031A LIT-1223031B LIT-1223033A LIT-1223033B | 10436C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | ENERGY ABS. LEVEL TRANSMITTER - Include the level transmitter valves in the 3D model to allow for maintenance. According to manufacturer&#39;s document | None | PB Ops | CSE | OPEN |  | None |  | None | None | HAND | None | None | M10A |  | M10A LIT-1223012A-1 / LIT-1223012A-2 / LIT-1223012A-3 LIT-1223021A-1 / LIT-1223021A-2 / LIT-1223021A-3 LIT-1223028A-1 / LIT-1223028A-2 / LIT-1223028A-3 LIT-1223029A-1 / LIT-1223029A-2 / LIT-1223029A-3 LIT-1223041A-1 / LIT-1223041A-2 / LIT-1223041A-3 M10C LIT-1223012B-1 / LIT-1223012B-2 / LIT-1223012B-3 LIT-1223028B-1 / LIT-1223028B-2 / LIT-1223028B-3 LIT-1223029B-1 / LIT-1223029B-2 / LIT-1223029B-3 LIT-1223041B-1 / LIT-1223041B-2 / LIT-1223041B-3 LIT-1223021B-1 / LIT-1223021B-2 / LIT-1223021B-3 | 10437C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Cable tray to be routed either front or side of the panel. | Tray has been rerouted as per requirement. | KBR | CSE | Pending Seatrium Reply | 01/01/2026 | None |  | None | None | INST | None | None | M10C |  | PN-AIT-1223012 | 10438C | 20/02/2026 | 6.00000000000000 |  | SEA/KBR | None |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
None | Tapping point orientation is not correct. To follow the agreed solution. | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M10C |  | None | 10439C | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Cable tray to be provided for tubing or PIT to relocated closer to the tapping point | Tube tray has been routed | KBR | CSE | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | INST | None | None | M10C |  | None | 10440C | 20/02/2026 | 0 |  | SEA/KBR | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
None | Lighting very close to the flange. Re-evaluate the lighting position and move away from flang | Light fixture relocated s per comment | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10441C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Floodlight too close to pipe, projection of floodlight rotation is obstructed. Relocate (or adjust mounting height) floodlight accordingly. | Light fixture Projection Updated. | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10442C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Floodlight support and pipe support is too close. Adjust floodlight position to create adequate clearance space from pipe support, or mount the floodlight to the pipe support. | Flood Light fixture Moved as per comment | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | None | 10443C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Re-evaluate light position for accessibility. Position the light closer to the cage ladder for better access. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A/C |  | LES-305-06-M10A-005 LES-305-06-M10A-006 LES-305-09-M10A-005 LES-305-09-M10A-004 LES-305-09-M10A-005 LES-307-04-M10C-004 LES-307-04-M10C-005 LES-307-07-M10C-004 LES-307-07-M10C-005 LES-307-07-M10C-006 | 10444C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Light to be relocated to the nearest beam | Ligth fixture reloacted, But cant able to mount in nearest beam, we dont have clear head room clearance. | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | LES-305-07-M10A-003 | 10445C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Too close to the piping. Flood light to be telocated nearby. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | LNO-218-12-M10A-001 | 10446C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Floodlight too close to tray support. Relocate floodlight away from tray support. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | LNO-218-14-M10A-005 | 10447C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Rotate light to focus perpendicular to floor (light fixture to be mounted directly facing floor below). | Light fixture Facing changed as per comment | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | LNO-218-16-M10A-006 | 10448C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | JB to face opposite side, for easier access to equipment during maintenance. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | CXE-L-M10A-228 | 10449C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Change light mounting type and mount to nearby pipe support. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | LNO-218-19-M10A-008 | 10450C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Rotate and re-position the light fixture to naerby beam to avoid cable termination and glanding issues. | Light fixture Relocated as per comment | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | LEM-340-02-M10C-005 | 10451C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Spearker to be relocated to avoid the engine as access area. If applicable, will be relocated based on the study report. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10B |  | COR-5518218B | 10452C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Cable ladder to be modified to avoid the the block from the JB support and coaming. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10B |  | TT-M10B-L-E-TRAY-10002 & TT-M10B-S-B-TRAY-00002 | 10453C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | CCTV to be relocated as per the mark-up snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10B |  | CAM-5514054 | 10454C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Speaker to be relocated as per the mark-up snapshot | Speaker has been relocated as per snapshot | KBR | TEL | RE-OPEN | 05/01/2026 | None |  | None | None | TEL | None | None | M10B |  | COR-5518221B | 10455C | 28/12/2025 | 2.00000000000000 |  | PB - Engineering | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | Speaker support to be extended for better accessability | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10B |  | SPP-M10B-00031 | 10456C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Speaker to be relocated as per the mark-up snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10B |  | COR-5518223B | 10457C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Beacon to be relocated as per mark-up snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10B |  | BLE-5511191 | 10458C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | CCTV to be relocated as per the mark-up snapshot | CCTV has to been re;located as per the mark up | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M10B |  | CAM-5514056 | 10459C | 28/12/2025 | 3.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
None | Speaker pole to be relocated as per mark-up snapshot | Speaker Pole has been relocated as per the markup | KBR | TEL | RE-OPEN | 05/01/2026 | None |  | None | None | TEL | None | None | M10B |  | SPP-M10B-00055 | 10460C | 28/12/2025 | 2.00000000000000 |  | PB - Engineering | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
None | Speaker to be relocated | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10B |  | COR-5518236B | 10461C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Secondary trays are missing for Telecom equipment. General for M10B | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10B |  | CAM-5514058 | 10462C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
None | JB not accessible. JB mounting type to change, front side of JB to face the nearby access way/path. | JB Relocated as per coomment | PB Ops | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10C |  | CXN-L-M10C-232 | 10463C |  | 20.0000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 03/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 03/12/2025
None | Increase arm length of light support to avoid welding problems during support installation. | Light fixture support length increased and provide welding clearance. | SEA | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | TEL | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10C |  | LEM-341-04-M10C-002 | 10464C |  | 20.0000000000000 | 18.0000000000000 | SEA/KBR | None |  | None | None | 03/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 03/12/2025
None | Extend tray to cable termination side of the light fitting. | Cable tray provided up to Light Fixture Termination | PB Ops | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | TEL | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10C |  | LEM-341-05-M10C-006 | 10465C |  | 9.00000000000000 | 18.0000000000000 | PB - Operation | None |  | None | None | 14/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 14/12/2025
None | Problem on JB access. Check the tubing and JB details on how the space can be shared without compromising access to JB. | None | PB Ops | CSE | OPEN |  | None |  | None | None | ELE | None | None | M10C |  | CXN-L-M10C-050 | 10466C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | Move camera down by another 10cm away from floodlight support (as per PB recommendation), for adequate clearance and for maintenance purpose. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M10C |  | CAM-5514063 | 10467C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
None | Floodlight blocked by pipe. Re-position the floodlight to an unblocked location. | Light Fixture relocated as per comments. | PB Ops | ELE | Pending PB Reply | 05/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: KBR ELECTRICAL TO ENSURE TO EXTEND THE CABLE TRAY UNTIL THE FLOOD LIGHT CABLE TERMINATION POINT. | M10C |  | LNO-220-14-M10C-001 | 10468C |  | 15.0000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 08/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 08/12/2025
None | Relocate light to nearby beam, mounting type to be changed. | Light Fixture Relocated and attcahed in the beam | None | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10C |  | LEM-340-07-M10C-001 | 10469C |  | 9.00000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 14/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 14/12/2025
None | Check lighting calculation to verify if LED lights are still required considering floodlights servicing the same area. If required, then relocation of lights is recommended due to space constraints (maintenance). | light fixture Removed and lux level achieved with Flood light | None | ELE | Pending PB Reply | 05/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10C |  | LNO-220-15-M10C-007 LNO-220-15-M10C-008 | 10470C |  | 15.0000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 08/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 08/12/2025
None | JB space issue with valve. Re-position floodlight in nearby location maintaining acceptable illumination at task area. | light fixture relocated to have better JB access | None | ELE | RE-OPEN | 11/12/2025 | None |  | None | None | ELE | None | None | M10C |  | LES-307-12-M10C-002 | 10471C |  | 9.00000000000000 | 18.0000000000000 | PB - Operation | None |  | None | None | 14/12/2025 | 23/12/2025 | 25/12/2025 | 25/12/2025 | 23/12/2025 | 14/12/2025
None | Verify handling movement/activities in the area surrounding the light fixture. Relocate light if it conflicts the expected handling activities in the location. Check any simillar lighting situation in Level 5. | Verified with material handling team. A-Frame movement is not obstructed by the light fixture. | SEA | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10C |  | LNO-220-19-M10C-005 | 10472C |  | 9.00000000000000 | 18.0000000000000 | SEA/KBR | True |  | None | None | 14/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 14/12/2025
None | Relocate pole mounted light to marked location. | Light fixture relocated as per comments | None | ELE | Pending PB Reply | 05/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: KBR TO ENSURE TO PROVIDE PENETRATION FOR LIGHTING CABLE TRAY. | M10C |  | LNO-220-19-M10C-006 | 10473C |  | 15.0000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 08/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 08/12/2025
None | Mount floodlight/JB to nearby pipe support. | Light fixture and Jb mounted Near by column | None | ELE | Pending PB Reply | 05/12/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10C |  | LNO-220-24-M10C-001 | 10474C |  | 15.0000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 08/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 08/12/2025
None | Provide means for MCT access/installation space. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | E-M10B-M-MCT-001(stydy) | 10475C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Vendor model for motor terminal box to be updated based on latest design development. Terminal box shall be aligned with the planned cable entry. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | B-1223004A | 10476C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Vendor to confirm segregations of electrical and instrumentation cables are complied based on requirements. Vendor model to be updated as required. | Awaiting KSB vendor response. | PB | MECH | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | None | 10477C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | HV/MV cable routing with SPD's (and motors) to be checked (below L1). Cable bending radius to be checked and modelled to demonstrate minimum requirement is complied. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | ET-M10B-M-TRAY-05002 ET-M10B-M-TRAY-05005 | 10478C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Vendor model for motor terminal box and vendor cable tray to align with KBR tray to be updated based on latest design information. Terminal box shall be aligned with the planned cable entry. | Awaiting KSB vendor response. | PB | MECH | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | B-5331001A B-5331001C | 10479C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | All model items mounted at the nearby column (with reference to motor terminal box position), obstructing access to the motor terminal box to be relocated. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | CXN-L-M10B-003 | 10480C | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Relocate instrument & tapping point away from maintenance/access space intended for motor terminal box. Comment applicable to motor C & D. | All 3 Instruments are relocated. | KBR | CSE | Pending PB Reply | 26/12/2025 | None |  | None | None | INST | None | 28-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10B |  | PIT-5331025A PIT-5331025B PIT-5331025C | 10481C | 20/02/2026 | 1.00000000000000 | 11.0000000000000 | PB - Operation | True |  | None | None | 29/12/2025 | 30/12/2025 |  |  | 30/12/2025 | 29/12/2025
None | Vendor to update model based on latest information. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | ET-M10B-L-N-TRAY-10002-TRAY-0401 | 10482C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Lighting JB is blocked. JB to relocate to an accessible location. Trays for socket JB to be modelled considering proper bending of cables. | Lighting JB is relocated. Trays for socket JB are modelled proper bending of cables. | PB | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M10B |  | CXN-L-M10B-004 ET-M10B-L-N-TRAY-10016-TRAY-0121 | 10483C |  | 5.00000000000000 |  | PB - Engineering | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Provide adequate space for installation of MCT. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | E-M10B-L-MCT-010-TRAY-0001 | 10484C | 05/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Vendor model for tie-ins (Electrical & Instrument) to match tray tie-ins based on KBR input. Proper MCT installation space to be provided too. | None | SE | CSE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | 3D-CRUDE OIL FISCAL METERING SKID | 10485C |  |  |  | SEA/KBR | None |  | None | None
None | Socket too close to spray point from deluge system. Socket to relocate, possibly combine with other nearby socket in same support. | Socket are relocated with combined support. | PB Ops | ELE | Pending PB Reply | 30/11/2025 | None |  | None | None | ELE | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10B |  | SKN-M11-422 | 10486C |  | 20.0000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 03/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 03/12/2025
None | Ensure that all sub-cable trays are properly terminated and connected to the bottom of each JB. All lighting fixtures shall be connected using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all lights and JB within Module M10B | None | SEA | ELE | OPEN | 30/11/2025 | None |  | None | None | ELE | None | None | M10B |  | SPS-M10B-0502 LES-306-02-M10B-002 CXE-L-M10B-342 LNO-219-15-M10B-008 | 10487C | 05/02/2026 | 38.0000000000000 |  | SEA/KBR | None |  | None | None | 03/12/2025 |  |  |  |  | 03/12/2025
None | Tubing penetration missing. Tubing tray is missing (for more than 2.5m) General punch for M10B. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | PIT-5331016 | 10488C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | 1. For liquid service, the instrument connection should be lower than the tapping point. 2. For gas service, the instrument connection should be higher than the tapping point. These installation requirements shall be implemented in all applicable areas. Where this arrangement cannot be maintained, KBR shall notify PB and obtain confirmation prior to implementation. Typical to all Instruments and Tappings to be check for the Modules M10B | Slope is maintained for all liquid and Gas services as per guidelines. | SEA | CSE | Pending Seatrium Reply | 30/12/2025 | None |  | None | None | CSE | None | None | M10B |  | PIT-1223075 | 10489C | 20/02/2026 | 8.00000000000000 |  | SEA/KBR | None |  | None | None | 02/01/2026 |  |  |  |  | 04/01/2026
None | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves and panels. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all Instruments, JB and valves M10B. Cable Penetration to be modelled and that has to follow as per structure guideline and also when penetration and cable tray Infront of valve should not block the valve maintenance. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | PN-AIT-5331001 | 10490C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Tubing penetrations in the steel and FRP gratings need to be aligned with the structure. Square Penetrations to be use to make the welding easier and also bolting will be easier for FRP Grating | Penetration is changed as per Guidelines. | KBR | CSE | Pending PB Reply | 30/12/2025 | None |  | None | None | CSE | None | 07-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10B |  | None | 10491C | 29/01/2026 | 7.00000000000000 | 1.00000000000000 | SEA/KBR | None |  | None | None | 02/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 04/01/2026
None | Relocate the PDA to avoid the accessway | Since there is no feasible location this PDA is deleted and the valves has been combined with nearest PDA. | KBR | CSE | Pending PB Reply | 26/12/2025 | None |  | None | None | CSE | None | 28-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10B |  | PDA-M10B-NE-04 | 10492C | 20/02/2026 | 1.00000000000000 | 11.0000000000000 | SEA/KBR | None |  | None | None | 29/12/2025 | 30/12/2025 | 01/01/2026 | 01/01/2026 | 30/12/2025 | 29/12/2025
None | Evaluate the possibilithy of rotating the JB by 90 degree to reduce the cable bending. If not possible, can retain the location. | 26-12-25 : JB has been rotated as per comment. | SEA | CSE | Pending PB Reply |  | None |  | None | None | CSE | None | 28-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10B |  | JB1-1421-209 | 10493C |  |  | 11.0000000000000 | SEA/KBR | None |  | None | None |  | 30/12/2025 | 01/01/2026 | 01/01/2026 | 30/12/2025
None | PCS JB is clashing with Handling path and need to check ESP located behind. Equipment to be modified accordingly. | 17-12-25 : Material handling has updated the handling path to clear the clash with JB. | PB Ops | CSE | RE-OPEN |  | None |  | None | None | HAND | None | None | M10B |  | SPI-M10B-115 | 10494C | 20/02/2026 |  | 9.00000000000000 | PB - Operation | None |  | None | None |  | 01/01/2026 | 03/01/2026 | 04/01/2026 | 01/01/2026
None | JB need to relocate as it will affect by valve maintenance. (observation by PB Operation). | 26-12-25 : JBs are relocated to allocate space for valve maintenance. 08-01-26 : distance between MCT and stucture "T" beam is maintained as per standard now. Please refer file "Reply to attached 6" | PB Ops | CSE | Pending PB Reply |  | None |  | None | None | CSE | None | 10-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10B |  | JBIF-1421-203 | 10495C |  |  | -1.00000000000000 | PB - Operation | None |  | None | None |  | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026
None | Need to confirm the obstruction volume of material handling clashing with JB. MH obstruction volume created recently. To be checked for the MH requirement. | 17-12-25 : Clash of JB with MH volume is resolved. MH volume is updated by material handling team to resolve the clash. MH 05/01/2026: OBST Volume clash has been resolved | KBR | HAND | Pending Seatrium Reply | 04/01/2026 | None |  | None | None | HAND | None | None | M10B |  | JBC-1421-219 | 10496C | 02/01/2026 | 4.00000000000000 | -1.00000000000000 | SEA/KBR | None |  | None | None | 07/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 07/01/2026
None | Need to add tee comp. to lay the cable from JB to cable tray | 17-12-25 : Tee component has been added for cable laying from JB to cable tray. | SEA | CSE | Pending PB Reply |  | None |  | None | None | INST | None | 21-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10B |  | JBC-1421-202 | 10497C |  |  | 18.0000000000000 | SEA/KBR | True |  | None | None |  | 23/12/2025 |  |  | 23/12/2025
None | PN-UH-5139010B : Tube tray penetration to be model for HPU Panel. Need to have sufficient distance between cable tray and Tubing tray. electrical cable requirement need to check. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | PN-UH-5139010B(HCR-06)-Rev-B | 10498C |  |  |  | SEA/KBR | None |  | None | None
None | KBR to model and incorporate the necessary supports in accordance with the standard KBR typical drawings for all 90 deg Bends(Typ). | 09-01-26 : Cable Tray Supports are modeled for 90 deg bends. | SEA | CSE | Pending PB Reply |  | None |  | None | None | CSE | None | 10-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: KBR MUST ENSURE THAT ALL EIT ITEMS ARE CLASHED FREE PRIOR TO THE ISSUANCE OF DELIVERABLES. (SEE ATTACHED 8) | M10B |  | IT-M10B-T-TRAY-04004-TRAY-0104 | 10499C |  |  | -1.00000000000000 | SEA/KBR | None |  | None | None |  | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026
None | Need to model tray dropper below vendor JB and need to clarify the scope whether vendor or KBR. | under SEA verification to PB review and approval | SEA | MECH | OPEN |  | None |  | None | None | Arranjo | None | None | M10B |  | None | 10500C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Vendor should model interface cable tray from Vendor JB to instrument on package | under SEA verification to PB review and approval | SEA | MECH | OPEN |  | None |  | None | None | MECH | None | None | M10B |  | RS FL-5331001 | 10501C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Interface cable tray modeled for test seperator pump should be clash free and need to connect to vendor tie-in point. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | B-1223004A\B | 10502C |  |  |  | SEA/KBR | None |  | None | None
None | Need to maintain sufficient distance between HV tray and instrument tray routed for Produced Water Booster Pumps. | Instrument is relocated and tray is rerouted. | KBR | CSE | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | CSE | None | None | M10B |  | IC-M10B-S-I-TRAY-01031 | 10503C |  | -1.00000000000000 |  | SEA/KBR | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
None | Vendor to have a sufficient opening on their panel at deck MCT for cable pulling. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | Z-1212001 /Z-1212002 | 10504C |  |  |  | SEA/KBR | None |  | None | None
None | Cable tray routing need to improve below Metering skid Z-1212002 | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | None | 10505C |  |  |  | SEA/KBR | None |  | None | None
None | Tubing to be modified to avoid the JB | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | T-01-PIT-1223078 | 10506C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | Tubing and Tubing penetration to be modified, to provide required space for welding | Tubing and Tubing penetration is modified as per standard | KBR | CSE | RE-OPEN | 30/12/2025 | None |  | None | None | CSE | None | None | M10B |  | PDA-M10B-NE-09 Copy of I-M10B-T-PEN-239 I-M10B-T-PEN-263 PDA-M10B-E-10 | 10507C | 30/01/2026 | 7.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 04/01/2026
None | Support to be trimmed to 600mm, once PB accepted the proposal through TQF. Typical to updated where required. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | None | 10508C |  |  |  | SEA/KBR | None |  | None | None
None | Transmitter to be relocated to avoid close proximity to valve and handwheel. | Line near the Transmitter is relocated. So that clash is cleared. | KBR | CSE | RE-OPEN | 28/12/2025 | None |  | None | None | CSE | None | None | M10B |  | PIT-5331020B PIT-5331021B | 10509C | 20/02/2026 | 9.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 31/12/2025 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 31/12/2025
None | Relocate the Transmitter beside the penetration, to provide more clearance against deluge pipe. | Both Transmitter has been relocated as per comment. | KBR | CSE | RE-OPEN | 30/12/2025 | None |  | None | None | CSE | None | None | M10B |  | PIT-1223110D PIT-1223110F | 10510C | 20/02/2026 | 7.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 04/01/2026
None | Rearrange tubing tapping point with respect to orifice vendor GA requirement. Elevation difference to be maintained. | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | FIT-1223074-2 | 10511C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | Maintain minimu 50mm between penetrations | Penetration distance is adjusted. | KBR | CSE | RE-OPEN | 30/12/2025 | None |  | None | None | CSE | None | None | M10B |  | I-M10B-S-PEN-316 | 10512C | 30/01/2026 | 10.0000000000000 | -1.00000000000000 | SEA/KBR | None |  | None | None | 02/01/2026 | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026 | 04/01/2026
None | Check the possibility to relocate the instrument to avoid the passage between the equipment. | Instrument is adjusted for the best accessible location. | KBR | CSE | Pending PB Reply | 26/12/2025 | None |  | None | None | CSE | None | 28-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: KBR MUST ENSURE PROPER ALIGNMENT AND SECURE CONNECTION (WITH PROPER FITTINGS) BETWEEN THE CABLE TRAY AND THE MCT. | M10B |  | None | 10513C | 20/02/2026 | 1.00000000000000 | 11.0000000000000 | PB - Operation | None |  | None | None | 29/12/2025 | 30/12/2025 | 01/01/2026 | 01/01/2026 | 30/12/2025 | 29/12/2025
None | Relocate the transmitter as per mark-up, to provide valve maintanence. | Both Transmitter is relocated as per markup. | KBR | CSE | Pending PB Reply | 30/12/2025 | None |  | None | None | CSE | None | 10-JAN-2026 SEA REMARKS: KBR UPDATED AND RELOCATED THE TRANSMITTERS, BUT NOTE: PENETRATIONS FOR TRANSMITTERS NOT FOLLOWING AS PER STRUCTURE STANDARD AND CURRENT LOCATION IS CLASHED WITH PIPE AND COAMING. | M10B |  | PIT-1223109C PIT-1223109B | 10514C | 20/02/2026 | 10.0000000000000 | -1.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026 | 04/01/2026
None | Deluge line and lighting too close. Observe adequate clearance between two items, adjust lighting position to ensure glanding space is not obstructed. | Deluge line moved and having sufficient space for Light fixture glanding | PB Ops | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 06-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10B |  | LEM-338-01-M10B-009 LNO-219-01-M10B-009 | 10515C |  | 12.0000000000000 | 2.00000000000000 | PB - Operation | True |  | None | None | 27/12/2025 | 08/01/2026 |  |  | 08/01/2026 | 28/12/2025
None | Provide missing cable tray/penetration for the light fixture, as required. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | LEM-339-01-M10B-006 LNO-219-02-M10B-002 LEM-339-03-M10B-005 LEM-338-04-M10B-004 LNO-219-14-M10B-004 LES-306-10-M10B-003 LNO-219-16-M10B-008 LNO-219-17-M10B-002 LNO-219-17-M10B-003 LES-306-12-M10B-001 LES-306-12-M10B-002 LES-306-12-M10B-003 LNO-219-19-M10B-001 | 10516C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Check lighting best position to avoid glanding/cabling space issues. Adjust lighting location/rotation accordingly. | Light fixture Updated as per comments. | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | LNO-219-01-M10B-004 | 10517C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | JB location not accessible. Relocate JB for easier access. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | CXN-L-M10B-005 CXE-L-M10B-316 CXN-L-M10B-016 CXN-L-M10B-017 CXE-L-M10B-220 CXE-L-M10B-229 | 10518C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Consider tray relocation to avoid obstructing floodlight coverage. Ensure sub-tray is provided for floodlight. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | LNO-219-02-M10B-005 | 10519C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Access to valve and tapping point blocked. Relocate JB to avoid obstruction of space. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | CXE-L-M10B-319 | 10520C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Re-route instrument sub-tray away from the position of floodlight. | As per comment instrument Tray re routed. | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | IC-M10B-S-I-TRAY-02034 | 10521C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Adjust location of light mounted on structure/support. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | LEM-338-03-M10B-005 LNO-219-10-M10B-004 LEM-339-04-M10B-009 LNO-219-11-M10B-006 LNO-219-14-M10B-004 | 10522C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Instrument tray and floodlight to be adjusted, ensuring floodlight coverage is not blocked. | None | PB Ops | ELE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | LNO-219-08-M10B-005 | 10523C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Adjust light to suit the structural beams available and ensure light is not obstructed by nearby tray. | Light fixture relocated to avoid tray obstruction. | PB Ops | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M10B |  | LEM-338-04-M10B-009 | 10524C |  | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
None | Check lighting calculation to verify if LED lights are able to convert to floodlight due to maintenance concerns from operations team on pole mounted lights in very tight space. | Light Fixture changed as Flood Light as per comments | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | LES-306-09-M10B-001 LNO-219-15- | 10525C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Verify JB model if valid as it is located in inaccessible location and with no trays provided for cable connection. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | CXE-L-M10B-218 CXE-L-M10B-344 | 10526C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Light to be moved slightly to ensure the JB accessability. | light fixture updated to provide better access for JB | PB Ops | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 06-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M10B |  | LES-306-12-M10B-004 LNO-219-19-M10B-005 | 10527C |  | 12.0000000000000 | 2.00000000000000 | PB - Operation | True |  | None | None | 27/12/2025 | 08/01/2026 |  |  | 08/01/2026 | 28/12/2025
None | For all Level 5 lighting fixtures location, to model lighting sub-trays and required penetrations. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | None | 10528C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | Adjust (and rotate 180-degree) instrument stand for transmitters as per markup in tag snaphsot. Lighting location to be retained. | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | SPI-M10B-575 | 10529C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Shift JB to other side of the column, behind the cage ladder. | None | PB Ops | ELE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | CXN-L-M10B-72 | 10530C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
None | M10B - PRESS. TRANSMITTER W/ INDICATOR - DIAPHR Pressure transmitter - Provide Flushing ring to allow cleaning and reduce maintenance time These instruments are classified as capillary diaphragm instruments, therefore they must have a flushing ring to allow for cleaning and calibration. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | PIT-1223021B, PIT-1223023A , PIT-1223023B, PIT-1223073, PIT-1223075, PIT-1223088 PIT-1223110B, PIT-1223112B, PIT-1223112E, PIT-1223112F PIT-1223159, PIT-5133003, PIT-5133013, PIT-5133014, PIT-5133018, PIT-5331004, PIT-5331013, PIT-5331019, PIT-5331020A, PIT-5331020B PIT-5331021A, PIT-5331021B, PIT-5331023A, PIT-5331023B PIT-5331025A, PIT-5331027, PIT-5331028A, PIT-5331028B PIT-5331029, PIT-5331039A | 10531C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | M10B - DIFF. PRESSURE LEVEL TRANSMITTER- DIAPHR Level transmitter - Provide Flushing ring to allow cleaning and reduce maintenance time These instruments are classified as capillary diaphragm instruments, therefore they must have a flushing ring at both tapping points to allow for cleaning and calibration. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | LIT-1223011, LIT-1223038, LIT-5133041, LIT-5133045 LIT-5331002, LIT-5331007, LIT-5331014, LIT-5331015 LIT-5331018A, LIT-5331018B, LIT-5331019A, LIT-5331019B LIT-5331021A, LIT-5331021B, LIT-5331022A, LIT-5331022B | 10532C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | M10A PRESS. TRANSMITTER W/ INDICATOR - DIAPHR Pressure transmitter - Provide Flushing ring to allow cleaning and reduce maintenance time These instruments are classified as capillary diaphragm instruments, therefore they must have a flushing ring to allow for cleaning and calibration. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10A |  | PIT-1223003, PIT-1223054A-1, PIT-1223064A, PIT-1223066A PIT-1223059A, PIT-5133026B, PIT-5133021B, PIT-5133021A PIT-5133028B, PIT-5133001, PIT-5133008, PIT-5133028A PIT-5133029, PIT-5133021C, PIT-5133028C, PIT-5133021C | 10533C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | M10C - DIFF. PRESSURE LEVEL TRANSMITTER- DIAPHR Level transmitter - Provide Flushing ring to allow cleaning and reduce maintenance time These instruments are classified as capillary diaphragm instruments, therefore they must have a flushing ring at both tapping points to allow for cleaning and calibration. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10C |  | LIT-1223016B, LIT-1223018B, LIT-1223024B LIT-1223026B, LIT-1223031B, LIT-1223033B | 10534C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | M10C - PRESS. TRANSMITTER W/ INDICATOR - DIAPHR Pressure transmitter - Provide Flushing ring to allow cleaning and reduce maintenance time These instruments are classified as capillary diaphragm instruments, therefore they must have a flushing ring to allow for cleaning and calibration. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10C |  | PIT-1223029, PIT-1223031B PIT-1223032B, PIT-1223056B PIT-1223069B, PIT-1223072B PIT-1223132 | 10535C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | M10C - These instruments must be visible from their respective control valves, as listed below. 14 THE FLOW INDICATOR SHALL BE CLOSE TO THE MANUAL GLOBE VALVE IN ORDER TO BE VISIBLE TO OPERATOR. | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10C |  | FIT-1223006-2 - VALV-12231800 FIT-1223005-2 - VALV-12231801 FIT-1223007-2 - VALV-12231802 FIT-1223008-2 - VALV-12231803 | 10536C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | M10A - DIFF. PRESSURE LEVEL TRANSMITTER- DIAPHR Level transmitter - Provide Flushing ring to allow cleaning and reduce maintenance time These instruments are classified as capillary diaphragm instruments, therefore they must have a flushing ring at both tapping points to allow for cleaning and calibration. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10A |  | LIT-1223016A LIT-1223018A LIT-1223024A LIT-1223026A LIT-1223031A LIT-1223033A | 10537C | 15/02/2026 |  |  | PB - Operation | None |  | None | None
None | M10A - PRESS. TRANSMITTER W/ INDICATOR - DIAPHR Pressure transmitter - Provide Flushing ring to allow cleaning and reduce maintenance time These instruments are classified as capillary diaphragm instruments, therefore they must have a flushing ring to allow for cleaning and calibration. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 | None | PB Ops | CSE | OPEN |  | None |  | None | None | ELE | None | None | M10A |  | PIT-1223003, PIT-1223054A-1, PIT-1223064A PIT-1223066A, PIT-1223059A, PIT-5133026B PIT-5133021B, PIT-5133021A, PIT-5133028B PIT-5133001, PIT-5133008, PIT-5133028A PIT-5133029, PIT-5133021C, PIT-5133028C PIT-5133021C | 10538C | 15/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | MCT is closer to the beam. MCT to be adjusted to have minimum 50mm. | None | SEA | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09F |  | I-M09F-S-MCT-051 | 10539C |  |  |  | SEA/KBR | None |  | None | None
Level 3 | MCT and cable tray to be aligned | None | SEA | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09F |  | I-M09F-S-MCT-054 I-M09F-S-MCT-082 | 10540C |  |  |  | SEA/KBR | None |  | None | None
Level 4 | To evaluate and confirm with the structure the required distance between structure support and JB support and move the equipment accordingly. | None | SEA | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09F |  | SPI-M09F-404 | 10541C |  |  |  | SEA/KBR | None |  | None | None
None | MCT clash with Structural beam | None | SEA | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09F |  | SPI-M09F-405 | 10542C |  |  |  | SEA/KBR | None |  | None | None
Level 4 | Evaluate the trimmer necessity and if possible to move the JB frame to near structure | None | SEA | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09F |  | SPI-M09F-401 SPI-M09F-301 SPI-M09F-303 | 10543C |  |  |  | SEA/KBR | None |  | None | None
Level 3 | Trimmer for JB support clash with pipe penetration | None | SEA | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09E |  | SPI-M09E-302 | 10544C |  |  |  | SEA/KBR | None |  | None | None
Level 4 | Evaluate the possibility to shift the access way as material handling path to clear clash with JB frame | None | PB | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09E |  | SPI-M09E-401 | 10545C |  |  |  | PB - Engineering | None |  | None | None
None | Evaluate to shift the Safety equipment and keep the gap for MCT to Structure min. 50mm | None | PB | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09E |  | SPI-M09E-402 | 10546C |  |  |  | PB - Engineering | None |  | None | None
None | To confirm with MH whether the "Triangle" junction can be removed | None | PB Ops | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09E |  | SPI-M09E-404 | 10547C |  |  |  | PB - Operation | None |  | None | None
None | Cable tray shall be elevated and provide small piece of cable tray on the bottom of small JB. | None | PB Ops | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09E |  | SPI-M09E-405 | 10548C |  |  |  | PB - Operation | None |  | None | None
Level 3 | Dropper, MCT and incoming tray shall be aligned | None | PB Ops | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09D |  | SPI-M09D-401 | 10549C |  |  |  | PB - Operation | None |  | None | None
None | To evaluate possibility to combine into one JB frame. | None | SEA | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09D |  | SPI-M09D-302 SPI-M09D-303 | 10550C |  |  |  | SEA/KBR | None |  | None | None
None | MCT clash with trimmer for pipe support. To confirm with piping. | None | SEA | CSE | OPEN |  | None |  | None | None | ELE | None | None | M09D |  | SPI-M09D-304 | 10551C |  |  |  | SEA/KBR | None |  | None | None
Level 4 | MCT encroach to MH path. To confirm whether MH can be shifted as Access way. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09D |  | SPI-M09D-403 | 10552C |  |  |  | SEA/KBR | None |  | None | None
None | MCT blocked by trimmer for pipe support and cable tray support. To coordinate with Piping and Electrical to resolve. | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09D |  | SPI-M09D-404 | 10553C |  |  |  | PB - Operation | None |  | None | None
None | Evaluate to shift the JB frame to reduce the number of trimmer. (see punch on M09F) | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09D |  | SPI-M09D-405 | 10554C |  |  |  | SEA/KBR | None |  | None | None
Level 2 | To evaluate for optimising the safety tray size to be 600 width consdiering the number of cable to be laid. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09C |  | IT-M09C-S-S-TRAY-02001 | 10555C |  |  |  | SEA/KBR | None |  | None | None
Level 2 | Keep min 50mm gap between wedge T bar to MCT | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09C |  | SPI-M09C-201 | 10556C |  |  |  | PB - Operation | None |  | None | None
None | To evaluate shifting the tray slightly to the right side then the riser align with MCT | None | PB | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09C |  | SPI-M09C-204 | 10557C |  |  |  | PB - Engineering | None |  | None | None
None | MCT clash with trimmer for pipe support. To confirm with piping. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09C |  | SPI-M09C-303 | 10558C |  |  |  | SEA/KBR | None |  | None | None
None | Shift JB to 100-150mm to the right side to provide more access to the valve | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09C |  | SPI-M09C-404 | 10559C |  |  |  | PB - Operation | None |  | None | None
None | Cable tray dropper is missing | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09B |  | SPI-M09B-202 | 10560C |  |  |  | SEA/KBR | None |  | None | None
None | To be confirm with MH team on th e clash with MH volume and relocate the JB if necessary. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | SPI-M09A-201 SPI-M09A-401 SPI-M09A-402 SPI-M09A-407 | 10561C |  |  |  | SEA/KBR | None |  | None | None
None | To evaluate the reduce the dropper of Safety cable tray considering the cable to be laid | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | TS-M09A-AUTO-EQP-ELEV1-PNL | 10562C |  |  |  | SEA/KBR | None |  | None | None
None | MCT and Vendor cable opening to be aligned | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | None | 10563C |  |  |  | SEA/KBR | None |  | None | None
None | MCT to aligned with the tray tie in pointand vendor to relocate the interface tray | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | PN-UN-5139009-02 PN-UN-5139009-01 PN-1210009_0_SESDV-R1 PN-1210008_A_WCR | 10564C |  |  |  | SEA/KBR | None |  | None | None
None | The RIO Panel Platform needs an explanation of how it will be bolted to the RIO foundation or to the main/secondary structural beams. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | PN-5520109-1 PN-5520109-2 | 10565C |  |  |  | SEA/KBR | None |  | None | None
None | Tubing between HPU control rack to Topside Modules shall be modelled in the Hook up area by KBR same as Cable tray concept | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | None | 10566C | 15/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Tubing between HPU control rack to PDA to be routed. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | None | 10567C | 15/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Block valves are missing in the flow element. All to be modelled. Typical for M09A to F. The block valves for the FITs below are not modeled; these valves are connected directly to the FE (V-CONE FLOW SENSOR). I-DE-3010.2S-1200-944-EP8-074 | None | PB Ops | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A |  | "M09A FE-1210003Q VALV-12108025 VALV-12108026 M09A FE-1210001Q VALV-12108011 VALV-12108012 M09A FE-1210015K VALV-12108039 VALV-12108040 M09B FE-1210001R VALV-12108013 VALV-12108014 M09B FE-1210001S VALV-12108015 VALV-12108016 M09B FE-1210015L VALV-12108041 VALV-12108042 M09B FE-1210015M VALV-12108043 VALV-12108044 M09C FE-1210003S VALV-12108029 VALV-12108030 M09C FE-1210003T VALV-12108031 VALV-12108032 M09C FE-1210015N VALV-12108045 VALV-12108046 M09D FE-1210001T VALV-12108017 VALV-12108018 M09D FE-1210001U VALV-12108019 VALV-12108020 M09D FE-1210001V VALV-12108021 VALV-12108022 M09E FE-1210003U VALV-12108033 VALV-12108034 M09E FE-1210003V VALV-12108035 VALV-12108036 M09E FE-1210003W VALV-12108037 VALV-12108038 M09F FE-1210001W VALV-12108023 VALV-12108024 M09F FE-1210003R VALV-12108027 VALV-12108028 M09F FE-1210015P VALV-12108047 VALV-12108048 M09F FE-1252012 VALV-12528101 VALV-12528102 " | 10568C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
None | Move the Instrument 150MM west side. Min 300mm to be maintained b/w Inst/Tubing to Handwheel (FIT-1210015k-1) For Second snap (FIT-1210015K-1) only tubing to be modified. | Instrument has been moved and tube routing has been modified. | PB Ops | CSE | Pending Seatrium Reply | 01/01/2026 | None |  | None | None | CSE | None | None | M09A |  | FIT-1210015K-1 | 10569C | 20/02/2026 | 6.00000000000000 |  | PB - Operation | None |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
None | Penetration to be relocated to avoid the material handling space. | Penetration has been relocated to avoid the material handling space. | KBR | CSE | Pending Seatrium Reply | 01/01/2026 | None |  | None | None | CSE | None | None | M09A |  | PDA-M09A-NE-02 | 10570C | 30/01/2026 | 6.00000000000000 |  | SEA/KBR | None |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
None | PB request to change flow meter type from Magnetic on high pressure. Flow meters to be modelled Typical for M09A to F | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | FIT-1210005L / FIT-1210005M / FIT-1210005N / FIT-1210005P FIT-1210027R / FIT-1210027S / FIT-1210027T / FIT-1210027U / FIT-1210027V / FIT-1210027W FIT-1210015R / FIT-1210015S / FIT-1210015T / FIT-1210015U / FIT-1210015V / FIT-1210015W FIT-1210005K / FIT-1210015Q | 10571C | 15/02/2026 |  |  | PB - Operation | None |  | None | None
None | Move the instrument 500MM north side. | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | FIT-1244001K-1 | 10572C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | "1 - PRESSURE GAUGE SHALL BE VISIBLE FROM LAUNCHER OR RECEIVER DOOR. Tiypical for M09A to F. M09A | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09A |  | LP-1244002A (PG-1244004K - PG-1244005K) | 10573C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Penetration height to be reduced to 200mm as per standard and clash with structure member to be corrected. | Penetraion Height is modified and clash has been removed. | KBR | CSE | Pending Seatrium Reply | 01/01/2026 | None |  | None | None | CSE | None | None | M09A |  | I-M09A-T-PEN-216 | 10574C | 30/01/2026 | 6.00000000000000 |  | SEA/KBR | None |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
None | Rearrange the tubing behind the FE and Pipe. | Tube routing has been modified beind the FE. | KBR | CSE | Pending Seatrium Reply | 01/01/2026 | None |  | None | None | CSE | None | None | M09B |  | FIT-1210001S-1 FIT-1210001S-2 PIT-1210001S | 10575C | 27/02/2026 | 6.00000000000000 |  | PB - Operation | None |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
None | Move the instrument 300mm towards West | Instrument has been moved as per comment and tube routing has been adjusted. | KBR | CSE | Pending Seatrium Reply | 01/01/2026 | None |  | None | None | CSE | None | None | M09B |  | FIT-1210015L-1 FIT-1210015M-1 | 10576C | 20/02/2026 | 6.00000000000000 |  | PB - Operation | None |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
General | Rearrange the tubing to meet the sloping requirements. | Tube is rearranged to meet the slope. | KBR | CSE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | CSE | None | None | M09B |  | General | 10577C | 27/02/2026 | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
Level 5 | Check the possibility to relocate the PDA | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M09B |  | PDA-M09B-NE-07 | 10578C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Move the sample box to the marked location to provide access in front | the sample box moved to the marked location to provide access in front | KBR | CSE | Pending PB Reply | 21/12/2025 | None |  | None | None | CSE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) NOTE: CURRENT LOCATION OF SAMPLE BOX IS CLASHED WITH PDA-M10A-NE-01, CLASHED TO BE RESOLVE. | M10A/C |  | ESP-12230405 | 0501C | 20/02/2026 | 1.00000000000000 | 16.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 24/12/2025
1 | As per latest GAD, step file to be updated for cooling water lines valve | Awaiting KSB vendor response. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M10A/C |  | B-1223002A/B | 0502C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Add low point drains | low point drains added | KBR | PIP | Pending PB Reply | 05/01/2026 | None |  | None | None | PIP | None | dnc required | M10A/C |  | 3&quot;-PC-B30N-0967-HC 6&quot;-PCW-C16N-0886-HC 6&quot;-PCW-C16N-0251-HC 6&quot;-PCW-C11-0205-PP | 0503C | 23/01/2026 | 1.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
1 | Evaluate placing t-type strainer in 3 o&#39;clock position for maintenance/cleaning. PB Operations agree that access route may be compromised in this case. If kept in vertical, access to be provided. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | None | 0504C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | AIT-1223010 to be updated in ascending flow as per P&ID I-DE-3010.2S-1223-944-S2N-020 note 7, Sampling ESP-12230408 connection to checked with process on its preferential location. Static mixer straight length requirements need to be verified with vendor. | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10A/C |  | ESP-12230408 AIT-1223010 | 0505C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Sampling box to be relocated closer to sample point | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | ESP-12230408 | 0506C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Instrument stands to be relocated clear of cleaning connection | Both Instruments are reocated. | KBR | CSE | Pending PB Reply | 25/12/2025 | None |  | None | None | CSE | None | 28-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10A/C |  | PIT-1223039C PIT-1223039B | 0507C | 20/02/2026 | 2.00000000000000 | 11.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 30/12/2025 | 01/01/2026 | 01/01/2026 | 30/12/2025 | 28/12/2025
1 | Instrument air tie-in to be updated for well service pump | Awaiting a response from vendor PERONI | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M10A/C |  | B-5133001A/B/C | 0508C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain should be within the skid | Awaiting a response from vendor PERONI | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M10A/C |  | B-5133001A/B/C | 0509C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Reserve volume to be modeled for panel access | Awaiting a response from vendor PERONI | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M10A/C |  | B-5133001A | 0510C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve to be located inside coamed area | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | VALV-51330064 | 0511C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain to be inclused in coamed area | Drain line routed to in coamed area | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | no PIPING DCN REQUIRED | M10A/C |  | VALV-51330049 | 0512C |  | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
1 | Evaluate horizontal arrangement of check valve to avoid accumulation of chemical product | Check valve is modelled in horizontal | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | NO PIPING DCN REQUIRED | M10A/C |  | VALV-51330051 | 0513C |  | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
1 | Valves to be updated to DBB as PID & Vent and penetration sleeve to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | VALV-51330604/600 | 0514C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Bolt removal to be verified | Bolt removal modelled and clearance verified | KBR | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | No piping DCN REQUIRED | M10A/C |  | VALV-51330116 VALV-51330117 VALV-51330047 VALV-51330079 VALV-51330250 XV-5133012B XV-5133012A VALV-51330078 VALV-51330033 VALV-51330035 VALV-51330041 | 0515C |  | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
1 | PIT orientation to be checked and confirmed with Instrumentation. | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10A/C |  | PIT-5133026B | 0516C | 16/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Skid drain to be on Aft side of skid | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | None | 0517C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Requirement for plating and coaming vs. grating for liquid hydrocarbon services to be evaluated and confirmed by Safety | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A/C |  | None | 0518C |  |  |  | PB - Engineering | None |  | None | None
None | Outlet piping to be routed with slope to counter vessel trim | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | D-0217 | 0519C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Coaming tripping hazard through escape route to be resolved | Quater cut pipe updated in the escape route | KBR | STR | RE-OPEN | 28/12/2025 | None |  | None | None | STR | None | None | M10A/C |  | None | 0520C | 19/01/2026 | 2.00000000000000 | 8.00000000000000 | PB - Operation | None |  | None | None | 31/12/2025 | 02/01/2026 | 04/01/2026 | 04/01/2026 | 04/01/2026 | 31/12/2025
1 | Coaming tripping hazard through escape route to be resolved | Quater cut pipe added in escape route | KBR | STR | RE-OPEN | 28/12/2025 | None |  | None | None | STR | None | None | M10A/C |  | None | 0521C | 19/01/2026 | 2.00000000000000 | 8.00000000000000 | PB - Operation | None |  | None | None | 31/12/2025 | 02/01/2026 | 04/01/2026 | 04/01/2026 | 04/01/2026 | 31/12/2025
1 | Kickplate is not modelled on steps. PB confirms that kickplate is not required on steps without handrail. | As PB confirms, Kick plate not modelled on step | KBR | STR | Pending PB Reply | 28/12/2025 | None |  | None | None | STR | None | None | M10A/C |  | None | 0522C | 19/01/2026 | 2.00000000000000 | 8.00000000000000 | SEA/KBR | None |  | None | None | 31/12/2025 | 02/01/2026 | 04/01/2026 | 04/01/2026 | 04/01/2026 | 31/12/2025
1 | Pipe support to be relocated behind hydrant. Hydrant operating volume to be clear of interference | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | H-5423073 | 0523C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Operating volume for Extinguishers to be modeled (typical punch for M10A/B) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | None | 0524C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Relocate the equipment between the coamings | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | Z-5428223 | 0525C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | EEBD to face toward Aft | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | Z-5434029 | 0526C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Type 4 locker to be updated as per vendor datasheet (typical for M10A/C) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | Z-H-5423075 | 0527C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Escape route/ coaming plate to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | LEVEL-2-6-3631 TS-M10A-STR-OUTFIT-ELEV2-COAMING | 0528C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Handrail to be modelled (typical for interconnections to M11) | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M10A/C |  | None | 0529C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Penetration sleeve representation to be shown in model | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | None | 0530C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handrail to be provideed between structural bracing and column (typical for M10A/C Level3) | Handrail provided | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | STR | None | None | M10A/C |  | None | 0531C | 19/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
3 | Additional rail to be modelled as per standard detail. Fall arrestor to be modelled. | Fall arrestor and handrail updated | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | STR | None | None | M10A/C |  | None | 0532C | 19/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
4 | Steps and handrails to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | None | 0533C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Coaming plate to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | None | 0534C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Relocate hydrant to avoid interference with coaming | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | Z-5428235 | 0535C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Stepover to be modelled across coaming | As discussed Quater cut pipe modelled in escape route | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | STR | None | None | M10A/C |  | OFLD-M10A-0075902 | 0536C | 19/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
5 | Handrail height to be extended | Handrail updated | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | STR | None | None | M10A/C |  | None | 0537C | 19/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
5 | Missing handrail | Handrail updated | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | STR | None | None | M10A/C |  | None | 0538C | 19/01/2026 | 0 |  | SEA/KBR | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
5 | Kickplate to be extended as per standard detail for stair landings - typical punch for M10A/C | Kick plate updated | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | STR | None | None | M10A/C |  | None | 0539C | 19/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
5 | Lighting fixture is blocking access to hydrant | Light fixture Relocated as per comment | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-10A |  | LNO-218-20-M10A-001 | 0540C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Pipe support to be relocated behind hydrant | Pipe support relocated behind the hydrant | None | PIP | RE-OPEN | 05/01/2026 | None |  | None | None | PIP | None | dcn required | M10A/C |  | SP-M10A-83474 | 0541C | 23/01/2026 | 1.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
5 | Relocate EEBD to clear access for cleaning connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | Z-5434034 | 0542C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Mismatch between top of cage and handrail - to be updated as per standard detail | Ladder updated | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | STR | None | None | M10A/C |  | None | 0543C | 19/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
1 | Evaluate the requirement for handrail and delete if not required | Handrail removed | KBR | STR | Pending PB Reply | 30/12/2025 | None |  | None | None | STR | None | None | M10A/C |  | None | 0544C | 23/12/2025 | 0 | 8.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 02/01/2026 | 04/01/2026 | 04/01/2026 | 04/01/2026 | 04/01/2026
1 | Extinguisher to be relocated to ensure reserve box is clear of coaming | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | Z-5428269 | 0545C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Re-evaluate the location for this equipment ensuring accessibility | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | Z-5428273 | 0546C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | SOPEP KIT to be assigned a tag number and model hierarchy change to Safety Equipment | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A/C |  | None | 0547C |  |  |  | PB - Engineering | None |  | None | None
3 | Handrail to be provided to prevent falling from area under stair | Handrail provided | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | STR | None | None | M10A/C |  | None | 0548C | 23/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
1 | Evaluate the emergency lighting along the escape route | Emergency light fixtures are provided along the escape route | None | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10A/C |  | None | 0549C |  | 8.00000000000000 | 19.0000000000000 | PB - Operation | True |  | None | None | 14/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 14/12/2025
2 | Pipe support to be relocated behind the hydrant | Pipe support relocated behind the hydrant | KBR | PIP | RE-OPEN | 05/01/2026 | None |  | None | None | PIP | None | dcn required | M10A/C |  | None | 0550C | 23/01/2026 | 1.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
3 | Handrail to be updated at marked locations | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M10A/C |  | None | 0551C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | Pipe support to be relocated behind hydrant | Pipe support relocated behind the hydrant | KBR | PIP | RE-OPEN | 05/01/2026 | None |  | None | None | PIP | None | dcn required | M10A/C |  | None | 0552C | 23/01/2026 | 1.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
4 | Stepover to be modelled across coaming | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M10A/C |  | None | 0553C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | Closed drain tie-in to be updated as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | DFC-0030 | 0554C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | All PSV inlet lines freedrain slope to be maintained | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | None | 0555C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | PSV bleed valve to be modelled, block valve tag to be updated. PSV discharge line vent to be updated. | PSV bleed valve modelled, block valve tag updated. PSV discharge line vent updated. | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piing dcn required | M10B |  | F-0518 F-0519 F-0826 | 0556C |  | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
5 | High point vent tapping to be connected | High point vent tapping connected | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | no piing dcn required | M10B |  | F-1981 | 0557C |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
1 | TIT tapping to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | None | 0558C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | ESP tappings to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | ESP-53310217 ESP-12230512 ESP-53310203 ESP-51330106 ESP-12230407 ESP-12230511 ESP-12230521 ESP-51330107 ESP-12230513 ESP-53310223 ESP-53310226 ESP-53310224 ESP-53310221 ESP-53310222 ESP-53310219 ESP-53310225 ESP-53310218 ESP-53310216 ESP-53310206 ESP-53310208 ESP-53310207 ESP-53310214 ESP-53310213 ESP-53310212 ESP-53310211 ESP-53310209 ESP-53310210 ESP-53310215 ESP-53310205 | 0559C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | CIP connection tappings in vertical section - TQF to be raised. CIP line to be modelled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | CIP-53310004 CIP-53310005 CIP-53310006 | 0560C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
5 | CIP tappings to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | CIP-12230020 CIP-12230023 | 0561C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
5 | Vent to be modified to drain - typical for all 6 heat exchangers | Vent modified as drain - typical for all 6 heat exchangers | None | PIP | Pending PB Reply | 07/01/2026 | None |  | None | None | PIP | None | dcn required | M10B |  | HWP-0119 PC-1062 | 0562C | 23/01/2026 | 0 | 0 | PB - Operation | None |  | None | None | 10/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
5 | Bolt removal to be verified | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-12230251 VALV-12230176 XV-1223077 VALV-12232542 VALV-12231746 VALV-12231782 VALV-53310099 VALV-53310643 VALV-12230214 VALV-12230744 HV-1223013B HV-1223005B VALV-12232539 VALV-12230864 VALV-12230961 XV-1223258 VALV-53311134 VALV-53311136 VALV-53311135 VALV-53311137 VALV-53310168 Ball Valve VSL-2-30210 VALV-53311126 VALV-53311128 VALV-53311127 VALV-53311129 VALV-53311140 VALV-53311138 VALV-53311139 VALV-53310148 VALV-53311132 VALV-53311130 VALV-53311131 VALV-53311144 VALV-53311142 VALV-53311143 XV-5331026E VALV-53310204 XV-5331026C VALV-53310163 VALV-53310391 VALV-53310408 XV-5331026D VALV-53310183 XV-5331026A VALV-53310123 XV-5331026B VALV-53310143 | 0563C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Bolt removal volume to be modelled for butterfly valve and bolt removal space to be ensured (typical for M10B butterfly valves) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-12230233 | 0564C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Ensure it is possible to rotate the spectacle blind - rotation volume to be modelled | Spectacle blind - rotation volume is modelled, its possible to rotate | KBR | PIP | RE-OPEN | 01/01/2026 | None |  | None | None | PIP | None | dcn required | M10B |  | ESP-12230043 | 0565C | 23/01/2026 | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | PIT tapping orientation to be checked and updated as per Line List fluid state | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | PIT-1223159 PIT-5331020B PIT-1223109D PIT-5331021A PIT-5331021B PIT-1223109C PIT-1223111D PIT-1223109F PIT-1223111B PIT-1223150 PIT-1223111C PIT-1223023A PIT-1223076 PIT-1223111F PIT-5133014 PIT-1223109A PDIT-1223151 PIT-1223111E PIT-1223109B PIT-1223111A PIT-5331020A PIT-1223109E | 0566C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Check valve bolt removal to be verified | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-12232468 | 0567C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Vent to be modified to drain | Vent modified as drain | KBR | PIP | Pending PB Reply | 07/01/2026 | None |  | None | None | PIP | None | dcn required | M10B |  | VALV-12230877 | 568C | 30/01/2026 | 0 | 0 | PB - Operation | None |  | None | None | 10/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
3 | Block valves to be locate at vessel nozzle. Second block valve may be located close to the first block valve. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | SG-1223002: Utility connections: VALV-12230748, VALV-12230820 Closed drain: VALV-12230756,VALV-12230758, VALV-12230777, VALV-12232508 JETTING WATER SUPPLY CONNECTION and SAND SLURRY OUTLET CONNECTION: VALV-12232351, VALV-12230749, VALV-12232352, VALV-12230754, VALV-12230755, VALV-12232353 | 0569C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Sampling box arrangement to be optimised. Sampling lines to be routed without pocket. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | ESP-12232197/198/199 | 0570C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Reinforcement pad to be modeled | Reinforcement modeled | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | dcn required | M10B |  | SP-M10B-50722 | 0571C | 23/01/2026 | 0 | 6.00000000000000 | SEA/KBR | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | PIT tapping to be horizontal to avoid clogging | PIT-1223073 PIT-1223078 PIT-1223088 PIT-1223090 PIT-1223091 PIT-1223118 horizontal taping updated to avoid clogging | KBR | PIP | Pending Seatrium Reply | 04/01/2026 | None |  | None | None | CSE | None | None | M10B |  | PIT-1223073 PIT-1223078 PIT-1223088 PIT-1223090 PIT-1223091 PIT-1223118 | 0572C | 31/01/2026 | 3.00000000000000 |  | PB - Operation | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
3 | High point vent to be modeled | High point vent modeled. | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | PCW-0012 | 0573C |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
3 | Sampling connection line valve to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0012 | 0574C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Bolt volumes missing. Bolt removal to be verified. High point vents to be added. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-12230770 | 0575C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | XE-1223005 to be modeled. Access to be provided. | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | XE-1223005 | 0576C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Spectacle blind to be located on nozzle. PB Operations confirms that additional means of access is not required to be provided. | Spacer re-located in nozzle | None | PIP | Pending PB Reply | 21/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | PC-0288 | 0577C |  | 2.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 24/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 24/12/2025
4 | Sampling cabinet number to be updated. Valve and line to be routed. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | ESP-12238013 | 0578C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | AIT Panel to be relocated and AIT line to be routed without pocket | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | PN-AIT-1223009 | 0579C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Downstream drain to be modelled as per P&ID | Downstream drain modelled as per P&ID | None | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | no piing dcn required | M10B |  | PC-0636 PC-0067 | 0580C |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
4 | Lines branch together at 20", P&ID shows 26". Configuration to be checked and confirmed with Process. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | 20&quot;-PC-C16N-0288-NI 20&quot;-PC-C16N-0601-PP | 0581C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Valve to be located as close as possible to the header. | Valve shifted near to the header as much as feasible | KBR | PIP | Pending PB Reply | 07/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | VALV-12230813 | 0582C | 30/01/2026 | 0 | 0 | PB - Operation | None |  | None | None | 10/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
3 | ESP removable spool to be named as separate line. Blind flanges to be captured both sides of line. Supporting of the line should consider removable spool. | ESP removable spool named as separate line. Blind flanges captured both sides of line. Supporting of the line considered removable spool. | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | PC-2738 | 0583C |  | 0 | 6.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | CIP connection valves to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PC-1708 | 0584C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Portable access to be provided for strainer maintenance | None | KBR | PIP | OPEN |  | None |  | None | None | STR | None | None | M10B |  | PC-0584 PC-0539 | 0585C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Instrument stand to be relocated to clear strainer access. Access volume to strainer to be modeled. | Instrument has been reocated. | None | CSE | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | CSE | None | None | M10B |  | SPI-M10B-153 | 0586C | 20/02/2026 | -1.00000000000000 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
1 | Straight drain connection to be provided | straight drain connection to be provided | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | no piing dcn required | M10B |  | PC-0539 | 0587C |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
1 | Equipment coaming to be modeled inside the bracing | Coaming updated | KBR | STR | Pending PB Reply | 25/12/2025 | None |  | None | None | STR | None | None | M10B |  | None | 0588C | 22/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | PIT tapping to be side connection | PIT tapping updated as side taping | None | PIP | Pending Seatrium Reply | 01/01/2026 | None |  | None | None | CSE | None | None | M10B |  | PC-0584 | 0589C |  | 7.00000000000000 |  | PB - Operation | None |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
1 | Drain connection in Aft side of pump to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | B-1223004A | 0590C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Removable spool to be made shorter | The removable spool has been updated and shortened as much as possible. However, as shown in the second snapshot, the routing cannot be modified further due to stress requirements. | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | PC-0272 PC-0271 | 0591C |  | 1.00000000000000 | 2.00000000000000 | PB - Engineering | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
1 | Rotate push button to face toward accessway | None | None | CSE | OPEN |  | None |  | None | None | ELE | None | None | M10B |  | B-1223004A/B | 0592C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Drip pan requirement to be checked with Process | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | FIT- FIT-5133003 | 0593C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | PIT tapping to be side connection | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | PC-0571 PC-0530 | 0594C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Sampling panel and associated lines to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PC-0571 | 0595C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valve to be modeled in outlet line | valve udated. | KBR | PIP | RE-OPEN | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | F-0848 | 0596C |  | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | Requirement of this valve to be verified by Process - PB Operations consider they are redundant, other PSVs to open drain do not have these block valves. Vent connection also considered not required. | Valves are required as the PSV outlets are combined together before routed to open drain funnel. Hence no change is required. | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M10B |  | VALV-12230360 VALV-12230364 VALV-12230362 VALV-12230366 VALV-12231775 VALV-12231745 VALV-12231753 VALV-12231771 VALV-53310106 VALV-53310103 VALV-53310665 VALV-53310663 VALV-53310708 VALV-533107077 | 0597C |  | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
3 | Instrument tapping to be from side of pipe | PDIT-1223011 PIT-1223010 PDIT-1223140 PIT-1223160 instrument taping updated as side tapings. | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | dcn required | M10B |  | PDIT-1223011 PIT-1223010 PDIT-1223140 PIT-1223160 | 0598C | 23/01/2026 | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | AIT panel location to be verified. Piping to be routed with no pocket | BSW Analyser is a Inline Equipment supplied by vendor. So There is no panel requirement. | KBR | CSE | Pending PB Reply | 11/12/2025 | None |  | None | None | INST | None | 21-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10B |  | P-0019 P-0255 | 0599C | 30/01/2026 | 9.00000000000000 | 18.0000000000000 | PB - Operation | True |  | None | None | 14/12/2025 | 23/12/2025 |  |  | 23/12/2025 | 14/12/2025
2 | Category 3 block valve to located close to the header. Temporary access is sufficient. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-51240267 VALV-51240357 VALV-51240521 VALV-51240522 | 0600C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Drain arrangement to updated as marked | As per the 90% design review discussion, PB comments have been addressed: the drain valve has been updated with limited access, and the dead leg has been removed | KBR | PIP | RE-OPEN | 01/01/2026 | None |  | None | None | PIP | None | dcn required | M10B |  | P-0418 | 0601C | 23/01/2026 | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | Drain line to be shortened | Utility Connection updated with short spool. | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | DCN REQUIRED | M10B |  | P-0346 | 0602C | 23/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
3 | Piping to be connected | piping connected. | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | P-0125 | 0603C |  | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | Valve to be located inside the coaming | Valve located inside coaming | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | VALV-51330426 | 0604C |  | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | Filter removal temporary access to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | FT-5133001 | 0605C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Davit rotation volume to be modelled and ensure no piping interference during movement | davit rotation volume has been modeled, and breakup flanges have been provided for piping that interferes with the rotational volume. | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no dcn required | M10B |  | FT-5133001 | 0606C |  | 0 | 6.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
2 | Instrument air supply line to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | Z-5133002 | 0607C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Handling path to be updated and clear of interference with cable tray | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | None | 0608C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Globe valve to be upstream of ball valve | globe valve updated as per p&id | None | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piing dcn required | M10B |  | VALV-51330216 | 0609C |  | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
5 | Sampling connection to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | D-0218 | 0610C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Sampling line to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | D-0111 | 0611C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Block valve to be a close as possible to vessel nozzle - typical for all utility connections | Block valve updated nearby nozzle. | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no dcn required | M10B |  | VALV-51330195 | 0612C |  | 0 | 6.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
5 | Vent valve to be mounted at vessel nozzle. Permanent access is not required. | Vent valve is mounted at vessel nozzle. | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | VALV-51330198 | 0613C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
5 | Drain tapping to be updated with elbow to maintain proper clearance from grade | Drain taping is updated with elbow , presently enough clearance is available from grade | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | VALV-51330076 | 0614C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
1 | Add a 3" cleaning connection at lowest point of header | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRCK |  | None | 0615C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Change tee to elbow. | Only 2.1 m clearance is available from the pipe to the deck. If an elbow with flanges is used, the headroom requirement from grade cannot be met.(Refer second snap) | KBR | PIP | RE-OPEN | 04/01/2026 | None |  | None | None | PIP | None | dcn required | M10B |  | 16"-PCW-C11-0034-PP | 0616C |  | 1.00000000000000 | 2.00000000000000 | SEA/KBR | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
1 | Vent connection to be relocated between spectacle blind and exchanger - typical for produced water and cooling medium lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | P-5331001A/B/C | 0617C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain connection to be at the lowest point | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | W-0497 | 0618C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain connection to be re-oriented | Drain connection re-oriented | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | dcn required | M10B |  | W-0607 | 0619C | 23/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
4 | Blind flange to be shifted, reduce pipe length | Blind flange location shifted to near the pipe support | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | PCW-0046 | 0620C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
1 | Cleaning connection to be shifted as bottom connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0035 | 0621C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain to be added downstream of check valve | Dain is added in the location | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | dcn required | M10B |  | W-0201 | 0622C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
1 | Sampling connection orientation and line to be routed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0808 | 0623C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Cut out size to be increased on one side to allow for spacer removal. Extraction volume to be modeled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | ESP-53310012 | 0624C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Utility connection block valve to be located as close to vessel nozzle as possible | Utility connection block valve located as close to vessel nozzle. | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | VALV-53310060 VALV-53310032 | 0625C |  | 1.00000000000000 | 5.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 05/01/2026 | 07/01/2026 | 07/01/2026 | 05/01/2026 | 04/01/2026
1 | Closed drain block valve to be located at vessel nozzle. Second block valve to be located close to first. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-53310047 VALV-53310104 | 0626C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | SDV to be located close to vessel nozzle. PB Operation confirms limited access is acceptable. | he SDV has been relocated near the nozzle; however, only limited access is available | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | SDV-5331022 | 0627C |  | 1.00000000000000 | 5.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 05/01/2026 | 07/01/2026 | 07/01/2026 | 05/01/2026 | 04/01/2026
1 | LG vent and drain valves to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | LG-5331016 LG-5331010 | 0628C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Coaming to be extended to cover drains. Avoid sharp corners on coaming considering water accumulation | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | V-5331001 | 0629C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | 200mm clearance to be maintained below drain | Drain taping updated . | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping cn required | M10B |  | PC-0600 | 0630C |  | 1.00000000000000 | 5.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 05/01/2026 | 07/01/2026 | 07/01/2026 | 05/01/2026 | 04/01/2026
1 | Valve to be located close to vessel nozzle | as discussed with PB in model review Valve located close to vessel nozzle with limited access. | KBR | PIP | RE-OPEN | 04/01/2026 | None |  | None | None | PIP | None | no piing dcn required | M10B |  | PCW-0810-N6C | 0631C |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
1 | PIT tapping to be from side | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PIT -5331016 | 0632C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure access to sampling panel - blocked by instrument stand | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | ESP-53310205 | 0633C | 15/02/2026 |  |  | PB - Operation | None |  | None | None
1 | PIT to be modelled | As per instrument hook up drawing pressure transmitter connection taken from instrument tubing. no taping in piping scope.(please refer snap-1) | KBR | PIP | Pending Seatrium Reply | 04/01/2026 | None |  | None | None | PIP | None | None | M10B |  | FE-5331022 PIT-5331022 | 0634C |  | 4.00000000000000 |  | PB - Operation | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
4 | Flare line to be connected to header 26"-F-B3N-0365-NI | Flare line connected to the header | KBR | PIP | OPEN | 18/12/2025 | None |  | None | None | PIP | None | None | M10B |  | 2"-F-B9-0545-NI | 0635C | 16/01/2026 | 20.0000000000000 |  | PB - Operation | None |  | None | None | 21/12/2025 |  |  |  |  | 21/12/2025
1 | Bypass lines to be connected directly above deck level | Bypass lines connected directly above deck level | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | HWP-0032 PC-0605 PC-0608 | 0636C |  | 1.00000000000000 | 5.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 05/01/2026 | 07/01/2026 | 07/01/2026 | 05/01/2026 | 04/01/2026
4 | Spectacle blind to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0059 | 0637C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Spectacle blind to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | ESP-3310245 ESP-3310249 ESP-3310250 ESP-3310251 ESP-3310255 | 0638C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Sampling connection line and valve to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | ESP-53310206 / 7 / 8 / 9 /10 | 0639C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Oil outlet sampling box & lines to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0138 | 0640C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Missing valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0914 | 0641C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Line connecting with Slop vessel minimum slope to be maintained I-DE-3010.2S-5331-943-S2N-001 7 OILY WATER REJECT. FLOW BY GRAVITY, DESIGN SHALL CONFIRM / REVISE THE MINIMUM PIPING SLOPE OF 1% IN ORDER TO GUARANTEE COMPLETE FLOW FOR V-5336501. | Minimum slope maintained.pocket removed. | KBR | PIP | Pending PB Reply | 30/12/2025 | None |  | None | None | PIP | None | no PIPING DCN required | M10B |  | 4"-PCW-B11-0016-NI | 0642C |  | 2.00000000000000 | 6.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
2 | High point vent to be deleted | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0076 | 0643C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | One set of High point vent to be deleted | One set of High point vent deleted | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | PCW-0048 | 0644C |  | 1.00000000000000 | 5.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 05/01/2026 | 07/01/2026 | 07/01/2026 | 05/01/2026 | 04/01/2026
1 | Drain to be added downstream XV because dead-leg downstream and check upstream the XV. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | XV-5331026A/B/C/D/E | 0645C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Closed drain line to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0023 | 0646C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Access to valve from adjacent module M10C to be evaluated, considering reach across empty space. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-53310224 | 0647C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Portable access to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-53310423 VALV-53310428 | 0648C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Block valve to be located close to vessel nozzle | Block valve located as close to vessel nozzle both valve tag VALV-53310247 & VALV-53310253 | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | VALV-53310247 | 0649C |  | -9.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 04/01/2026
1 | Block valve to be located close to vessel nozzle | Block valve moved close to vessel nozzle | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | None | M10B |  | VALV-53310256 | 0650C |  | 6.00000000000000 |  | PB - Operation | True |  | None | None | 04/01/2026 |  |  |  |  | 04/01/2026
1 | Vent and drain to be modelled at top and bottom of stand pipe. End connection to be blind flanged. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-53310243 VALV-53310240 VALV-53310439 VALV-53310440 | 0651C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Vent valve to be located on nozzle | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PC-2417-N21 | 0652C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Eductor P&amp;ID I-DE-3010.2S-5331-944-S2N-003 Note 23 to be updated based on vendor confirmation on Eductor piping arrangement. EDUCTOR E-5331001A SHALL BE LOCATED AS CLOSE AS POSSIBLE TO THE GAS FLOTATION UNIT NOZZLE N18 IN HORIZONTAL POSITION WITHOUT ANY ELBOW. ALTERNATIVELY, THE EDUCTOR CAN ALSO BE INSTALLED VERTICALLY WITH DISCHARGE GOING UP WITH ONLY ONE ELBOW ENTRING INTO GFU VESSEL AS CLOSE AS POSSIBLE TO NOZZLE N18 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0214 | 0653C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Coaming to be extended to cover drains. | Coaming updated | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | STR | None | None | M10B |  | PCW-0214 | 0654C | 22/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Sampling lines and valves to be modeled distance between sampling panel and sampling point max 4m | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | SC-FIT-5331023A/B ESP-53310219 ESP-53310221 ESP-53310226 ESP-53310222 | 0655C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | 14&quot;-PCW-B26-0093-PP 14&quot;-PCW-B26-0109-PP | 0656C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | PIT connection to be taken as side tapping - PB Operations confirmed that PIT tapping can be located between the two headers with limited access. | PIT connection taken as side tapping | KBR | PIP | Pending PB Reply | 01/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | PIT-5331023A/B | 0657C |  | 1.00000000000000 | 5.00000000000000 | PB - Operation | None |  | None | None | 04/01/2026 | 05/01/2026 | 07/01/2026 | 07/01/2026 | 05/01/2026 | 04/01/2026
1 | P&ID I-DE-3010.2S-5331-944-S2N-003 Note 38 for Sampling point in vertical upward section is not met. To be checked and confirmed with Process to remove the note. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | ESP-53310224 | 0658C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Removable spool Tag no. to be added | ESP-53310117 Tag added in isometrics | KBR | PIP | Pending PB Reply | 30/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M10B |  | ESP-53310117 | 0659C |  | 2.00000000000000 | 6.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
1 | Freshwater line to be routed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | W-3272 | 0660C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Strainer removal to be inside skid | under SEA verification to PB review and approval | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M10B |  | RS-FL-5331001 | 0661C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Verify if this is a wafer check valve, there should be an additional flange for the spectacle blind I-DE-3010.2S-5331-944-Fl4-101 | under SEA verification to PB review and approval | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M10B |  | VALV-53318006 ESP-53318003/006/009 | 0662C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Push button to be modelled | under SEA verification to PB review and approval | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M10B |  | PRODUCE WATER TREATMENT_RE | 0663C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve orientation to be made horizontal | under SEA verification to PB review and approval | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M10B |  | PRODUCE WATER TREATMENT_RE | 0664C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve handwheel to close to structure | under SEA verification to PB review and approval | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M10B |  | PRODUCE WATER TREATMENT_RE | 0665C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Dedicated portable access to be verified with Vendor | under SEA verification to PB review and approval | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M10B |  | PRODUCE WATER TREATMENT_RE | 0666C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | F-0572 F-0674 | 0667C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Strainer filter removal access is blocked by Instrument stan | Instrument has been relocated away from the strain removal. | KBR | CSE | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | CSE | None | None | M10B |  | PCW-0105 PCW-0242 | 0668C | 15/02/2026 | -1.00000000000000 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
1 | Fresh water supply line to be connected with nozzle | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | W-3686 | 0669C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | PIT tappings to be in horizontal. PIT located between the headers with limited access is acceptable | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10B |  | PCW-0186 PCW-0108 | 0670C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Upstream and downstream straight length requirements for FEs to be ensured | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | FIT-5331028A FIT-5331028B | 0671C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | ESP Sampling Panel and connecting line to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0108 | 0672C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve handwheel clearance to be improved - too close to blind flange | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-53310314 | 0673C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Add a drain downstream of check valve or relocate check valve to high point | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-53310374 | 0674C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Low point drain to be added upstream of valves | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | VALV-53310328 VALV-53310517 | 0675C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | High point vent to be added | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0108 | 0676C | 22/01/2026 |  |  | PB - Operation | None |  | None | None
None | Evaluate locating sampling box within 4m of sample point | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | None | 0677C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | PIT to be straight side tapping, permanent access not required | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PDIT-5331031A | 0678C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | FO, XV location and size to be updated as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0160 | 0679C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve handwheel to be rotated upwards | Valve handwheel t rotated towards upward | KBR | PIP | Pending PB Reply | 18/12/2025 | None |  | None | None | PIP | None | no piping DCN required | M10B |  | PCW-0160 | 0680C |  | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
1 | DBB valve and connected line to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | PCW-0209 | 0681C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Add high point vent | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | HWP-0014 | 0682C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Hydrant support to be located behind hydrant | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | H-5423080 | 0683C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Extinguisher volumes to be modeled - typical punch for M10B | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | Z-5428100 | 0684C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure visability of the extiguisher is not restricted | Access volume modeled to ensure extiguisher visibility | KBR | PIP | Pending Seatrium Reply | 18/12/2025 | None |  | None | None | PIP | None | None | M10B |  | Z-5428247 | 0685C |  | 20.0000000000000 |  | PB - Operation | None |  | None | None | 21/12/2025 |  |  |  |  | 21/12/2025
1 | Ensure no interference between extinguisher operating area and coaming | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | Z-5428249 | 0686C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment modelling to updated as EEBD | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | Z-5434035 | 0687C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Model the safety shower volume and ensure no interference with coaming. | Safety shower volume is modeled, no interference with coaming. | KBR | PIP | Pending Seatrium Reply | 18/12/2025 | None |  | None | None | PIP | None | None | M10B |  | Z-5434367 | 0688C |  | 20.0000000000000 |  | PB - Operation | None |  | None | None | 21/12/2025 |  |  |  |  | 21/12/2025
1 | Safety shower block valves to be modelled (typical for M10B safety showers) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | Z-5434367 | 0689C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Hydrant support to be located behind hydrant | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | H-5423083 | 0690C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Safety equipment to be oriented to face the accessway | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | Z-5434036 | 0691C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Removal volume to be modeled and clear of interference | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | FT-5331001A | 0692C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Hydrant support to be modelled - typical for all M09 hydrants. Support should be behind hydrant. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A |  | H-5423176 | 0693C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | Fire extinguisher support to be updated as per drawing - typical for M09 extinguishers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A |  | Z-5428171 | 0694C | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
2 | Fire extinguisher operating volume to be modeled - typical for M09 extinguishers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A |  | Z-5428171 | 0695C | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
2 | Escape route to be modeled on stairway. Typical for M09 stairs. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A |  | None | 0696C | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09A |  | OFLD-M09A-0042232 | 0697C | 03/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Coaming to be extended and connected. Coaming to be at module boundary clear of escape route. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09A |  | OFLD-M09A-0051103 | 0698C | 03/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Pipe support for vacuum breaker to be modeled and update vacuum breaker tag. Typical punch for M09 vacuum breakers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A |  | FW-1123 | 0699C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
4 | Hydrant operating volume to be at front of hydrant (typical for hydrants on M09 Level 4) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A |  | H-5423066 | 0700C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
4 | Kickplate to be extended to close the gap | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09A |  | HNDR-ELEV4-FRP | 0701C | 03/03/2026 |  |  | PB - Engineering | None |  | None | None
3 | Coaming to be updated to avoid interference with escape route | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09B |  | OFLD-M09B-0049740 | 0702C | 03/03/2026 |  |  | PB - Engineering | None |  | None | None
3 | SOPEP KIT to be shown on Safety Plan drawing. M09B & D | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M09B/D |  | SOPEP-KIT | 0703C |  |  |  | PB - Engineering | None |  | None | None
4 | Connect the escape way to M11 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09B |  | None | 0704C | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Kickplate to be extended | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09B |  | OFLD-M09B-0049476 | 0705C | 03/03/2026 |  |  | PB - Operation | None |  | None | None
5 | Move the fire box twoards portside closer to the handrail (to align with Safety Plan drawing) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09B |  | Z-H-5423214 | 0706C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Clear width 1000mm to be maintained in escape way | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09C |  | None | 0707C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Fire extinguisher to be deleted - not shown on Safety Plan drawing | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09C |  | Z-5428176 | 0708C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Quarter pipe to be modeled where coaming crosses escape route | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09C |  | OFLD-M09C-0050793 | 0709C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Equipment locations to be updated on Safety Plan drawing | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M09C |  | Z-5428487 | 0710C |  |  |  | PB - Engineering | None |  | None | None
5 | Kickplate to be extended | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M09C |  | PultrudedHandrail_E5-5-2154 | 0711C | 04/03/2026 |  |  | PB - Engineering | None |  | None | None
3 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09D |  | OFHR-M09D-0000034 | 0712C | 04/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09D |  | OFHR-M09D-0000004 | 0713C | 04/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09D |  | OFHR-M09D-0000050 OFHR-M09D-0000051 | 0714C | 04/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09D |  | OFHR-M09D-0000005 | 0715C | 04/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09D |  | OFHR-M09D-0000007 | 0716C | 04/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Kickplate to be extended on stair landing - typical for M09 module | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09D |  | PultrudedHandrail_E5-5-2155 | 0717C | 04/03/2026 |  |  | PB - Engineering | None |  | None | None
2 | Hydrant operating volume to be modeled in front of hydrant (typical punch for M09E and F) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09E/F |  | H-5423184 | 0718C | 27/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Coaming to be updated to clear escape route | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09E |  | OFLD-M09E-0049841 | 0719C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09E |  | OFHR-M09E-0000049 | 0720C | 05/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Clear width 1000mm to be maintained in escape way | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09E |  | KBR_Escape Route-6-1748 | 0721C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Update the tag number in model Z-5428212 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09E |  | Z-5428212 | 0722C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09E |  | OFHR-M09E-0000053 OFHR-M09E-0000054 | 0723C | 05/03/2026 |  |  | PB - Engineering | None |  | None | None
4 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-09E |  | OFHR-M09D-0000007 | 0724C | 05/03/2026 |  |  | PB - Operation | None |  | None | None
5 | Quarter pipe to be modeled where coaming crosses escape route | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09E |  | OFLD-M09E-0050854 | 0725C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Equipment tag to be updated in model Z-5428428. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09E |  | Z-5428428 | 0726C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Fire extinguisher location to be updated on Safety Plan drawing | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M09E |  | Z-5428428 | 0727C |  |  |  | PB - Engineering | None |  | None | None
2 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M09F |  | OFHR-M09F-0000008 | 0728C | 05/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Escape route edge to be aligned with handrail edge and avoid interference from coaming | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09F |  | None | 0729C | 27/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M09F |  | OFHR-M09F-0000023 OFHR-M09F-0000024 | 0730C | 05/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Kickplate to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M09F |  | OFHR-M09F-0000047 | 0731C | 08/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Kickplate and quarter pipe to be modeled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M09F |  | OFLD-M09F-0050732 | 0732C | 08/03/2026 |  |  | PB - Engineering | None |  | None | None
4 | Clear width 1000mm to be maintained in escape way. Quarter pipe to be modelled where coaming crosses escape route. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09F |  | KBR_Escape Route-6-1740 | 0733C | 27/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Clear width 1000mm to be maintained in escape way. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09F |  | OFLD-M09F-0050737 | 0734C | 27/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Coaming to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09F |  | OFLD-M09F-0050724 | 0735C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Fire extinguisher location to be updated on Safety Plan drawing | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M09F |  | Z-5428431 | 0736C |  |  |  | PB - Engineering | None |  | None | None
1 | Model the swivel flange - typical for all risers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0737C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | To check and update the tubing as bend or elbow | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | CNI-2172 CNI-2159 CNI-2158 CNI-2145 CNI-2144 CNI-2131 CNI-2130 CNI-2173 | 0738C | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Couplings to be added for tube at 6m length | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | CNI-2172 CNI-2159 CNI-2158 CNI-2145 CNI-2144 CNI-2131 CNI-2130 CNI-2173 | 0739C | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Tubing supports to be modeled in tray | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | TUBING TRAY | 0740C | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | Maintain a minimum of 50mm between bottom of steel and tray | None | KBR | CSE | OPEN |  | None |  | None | None | STR | None | None | M09 |  | TUBING TRAY | 0741C | 08/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Length of piping to be minimised as much as possible | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0742C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model a space reservation volume for 12&quot; Globe valve. Ref Note 19 - I-DE-3010.2S-1210-944-S2N-001 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | PC-0166 | 0743C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Check valve to be located minimum distance from isolation valve. Flange requirement for check valve to be checked. Typical punch for M09 CIP injection points. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12100833 | 0744C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Handwheel to be rotated toward the accessway | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12101175 | 0745C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | High point vent to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | PC-0684 PC-0685 | 0746C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Relocate the utility line to the other side of the Receiver | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | PC-2374-N8 | 0747C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Model the XIT Pig Signaller - typical comment for PIG Launchers/Receivers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | XIT-1210003B | 0748C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
Mezz | Distance between Static Mixer and AIT not attended | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10C |  | ESP-12230108 AIT-1223001 | 0749C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Low point drain needed downstream of check-valve VALV-12231721 VALV-12230537 (Train A) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A/C |  | VALV-12231721 | 0750C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Missing the injection Quill ESP-12238046 Inlet 3&quot; / Outlet 6&quot;, with flanges connection. ESP-12238045 (train A) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10A/C |  | 6&quot;-PC-B30N-1108-HC ESP-12238046 ESP-12238045 | 0751C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | PDIT-1223016 low pressure point tie-in shall be placed near from the line joint (bifurcation) and at the same level of the high pressure PDIT tie in. Change the tie-in as in the Snapshot | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10C |  | PDIT-1223016 6&quot;-ADW-B11-0006-HC | 0752C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Sampling point tie-in can be placed at a accessible position. The outlet point shall be closer to the sampling tie-in (less than 4m). And first block valve (VALV-12230528) shall be closer to the process line (6&quot;-ADW-B11-0001-NI) as possible | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10C |  | VALV-12230528 ESP-12230458 | 0753C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | 10&quot;-PC-E16N-0197-HC - Tie in of the line is on the PSV line. Should be before the beforcation to PSVs Verify the arrengement The actual layout the line 10&quot;-PC-E16N-0197-HC need a low point drain downstream of the check valve VALV-12231373, or to replace the check valve to a place with self draining downstream of it | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-10C |  | 10"-PC-E16N-0197-HC | 0754C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | VALV-12231339 - Should be a double ball valve according to P&ID. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | VALV-12231339 | 0755C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Pressure Instruments shall be tie-in at lateral position for liquid pipings | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M10C |  | PIT-1223054B-1 PIT-1223054B-2 PDIT-1223277 PIT-1223132 PIT-1223128C PDIT-1223019 PDIT-1223016 PIT-1223008 | 0756C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Missing block valves for CIP lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | CIP-12230037 CIP-12230032 CIP-12230031 | 0757C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | General Punch: Sampling Point Panels shall meet the requirement: 3.6 Sampling line length shall be as short as possible, preferably less than 4 meters. For produced water sampling, sampling line length shall not exceed 4 meters. As per: I-ET-3010.00-1200-588-P4X-001 Examples given on the pictures Snap1 - SC-FIT-1223053B Snap2 - ESP-12230417 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | None | 0758C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Missing modelled PV-1223064B-1 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | PV-1223064B-1 | 0759C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate block valve to a similar position as the anothers sample colection valves from TO-122302B | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | VALV-12231623 VALV-12231700 | 0760C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Rotate AIT tie-in to guarantee instrument maintenance space, the instrument are to close from structure. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | AIT-1223012 | 0761C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Fix the drain line suport VALV-12230138 tha are conected into the valve CAP. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | VALV-12230138 | 0762C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | VALV-12232513 - Cleaning connection, shall be on horizontal position to hose connection. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | VALV-12232513 | 0763C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Remove the dead end upstream the instrument, install it directly on the process line Confirm if this punch is already taken on 10A | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | PDIT-1223142 | 0764C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Evaluete whether the valve shall be a gate valve instead of ball valve. All other similar system valves are diferent. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | VALV-12232665 | 0765C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate the cable trays and post to provide cleaning conection clear acess from P-1223001D | currently Nothing is infront of the valve. | KBR | CSE | Pending PB Reply | 25/12/2025 | None |  | None | None | CSE | None | 28-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M10C |  | VALV-12232512 | 0766C | 20/02/2026 | 2.00000000000000 | 11.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 30/12/2025 | 01/01/2026 | 01/01/2026 | 30/12/2025 | 28/12/2025
None | Missing CIP-1223008 branch and valve modeling | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | CIP-1223008 | 0767C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | All the vents without block valve shall have flange instead cap. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | 3/4"-PC-B30N-1126-PP | 0768C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Extend the PSV discharge pipes to inside the colector to avoid hot water spillage | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | 6&quot;-DA-B9-0247-NI 6&quot;-DA-B9-1342-NI 6&quot;-DA-B9-1355-NI 6&quot;-DA-B9-1354-NI | 0769C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Process to evaluate the requirement for vent. Typical for all HV valves | Double ball isolation is available with venting capability. Hence no additional vent is deemed required. (Refer Process PB weekly meeting #607). | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M09 |  | None | 0770C |  | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
4 | First isolation valve to be located close to nozzle with minimum elbows upstream. PB confirmed limited access is acceptable, valve category change from 2 to 3. Typical for all PIG Launchers/Receivers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12101194 VALV-12101196 VALV-12101238 VALV-12101240 VALV-12100377 VALV-12100381 VALV-12101374 VALV-12101377 VALV-12101376 VALV-12101383 | 0771C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | To ensure the PSV lines going from FWD to AFT have the minimum slope requirement to towards the Launcher/Receivers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0772C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Handwheel positions to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12440171 | 0773C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | PG SHALL BE VISIBLE TO OPERATOR DURING THE DEPRESSURISING OPERATION. Typ. For all HV | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0774C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Orientation to be in horizontal for Liquid lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | PIT-1210080B PIT-1210080A PIT-1210027U | 0775C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Re-orient the TIT to horizontal position - typical punch. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0776C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Clamp on FE to be modeled - typical for Water Injection lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0777C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Update the flange rating and spec | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0778C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09B |  | 8"-P-J12N-0723-PP | 0779C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Model the TIT connection at horizontal position | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | TIT-1210006K | 0780C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Update the handwheel orientations to not face each other | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0781C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Model the TIT connection - typical for Gas Injection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | TIT-1210003Q TIT-1210001U TIT-1210009R TIT-1210008T TIT-1210003S TIT-1210003W TIT-1210008S TIT-1210009T TIT-1210003R TIT-1210015P TIT-1210015L TIT-1210001V TIT-1210015M TIT-1231031 TIT-1210008M TIT-1210008N TIT-1210001Q TIT-1210001S TIT-1210003T TIT-1210001R TIT-1210009U TIT-1210001T TIT-1210001W TIT-1210015K TIT-1244007P TIT-1210003U TIT-1231033 TIT-1210009S TIT-1210015N TIT-1210003V TIT-1210009V | 0782C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Model penetrations for CIP lines (typical) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0783C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | For WAG wells to be included free draining upstream of HV (Despressurization) Ex. 8&quot;-PC-J12N-0328-PP 8&quot;-PC-J12N-0854-NI 8&quot;-PC-J12N-0870-PP | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | 8&quot;-PC-J12N-0328-PP 8&quot;-PC-J12N-0854-NI 8&quot;-PC-J12N-0870-PP | 0784C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
None | Model the spacer as per PID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0785C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Check valve to be located at maximum distance of 1m from Gas Injection header as per P&ID Note 8. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0786C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Bolt removal to be verified - typical for all choke valve arrangements at Level 5 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0787C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Process to check the requirement of bleed valve - typical for depressuring lines | Bleed valve required between the two isolation valves at the inlet of depressurization choke valves. (Refer Process PB weekly meeting #607). Note: Piping to implement only after SEA provides approval | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M09 |  | None | 0788C |  | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
None | Delete the PIT connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0789C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Ensure clear space for bolt removal | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12101054 VALV-12101061 | 0790C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Sampling point modeling and line numbers to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | ESP-12100841 ESP-12100876 ESP-12100946 ESP-12100948 ESP-12100950 ESP-12100952 ESP-12100956 ESP-12100958 ESP-12100960 ESP-12330467 | 0791C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Evaluate to locate the check valve closer to the DBB | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0792C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Break out flanges to be added for flushing purpose (for lines without valve) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | None | 0793C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Pipe spool before valve to be removed | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09 |  | VALV-12100636 | 0794C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Flare line to be connected to header | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M09 |  | 10&quot;-F-J40N-1217-ET 10&quot;-F-J40N-0396-ET 24&quot;-F-B3NV-0532-NI | 0795C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Connect the bypass line in horizontal orientation to avoid low point | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M09 |  | PC-0696 | 0796C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Low point drain to be provided | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M09 |  | PC-0120 | 0797C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Low point drain to be provided | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M09 |  | PC-0670 | 0798C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Low point drain to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | PC-0130 | 0799C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M09 |  | HV-1210050 | 0800C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Update the control valve as per latest vendor GA | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | FV-1244001K | 0801C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | 4"-F-C19N-0560-NI | 0802C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M09 |  | 8"-P-J40N-1867-PP | 0803C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Prosess to check the requirement of bleed valve | Bleed between double ball and PSV for 5133-002 (PSV-5133013A/B & PSV-5133015A/B). The bleeds to be retained as per TQF-P84P85-S2N-BE-TOP-PRO-0006 alignment. (Refer Process PB weekly meeting #604). | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M09 |  | PSV-5133013/B PSV-5133015A/B | 0804C |  | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
2 | Connect the pipe to the nozzle | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | 4"-DA-B9-2217-NI | 0805C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | 6"-DA-B9-1820-NI | 0806C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | 6"-DA-B9-1820-NI | 0807C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | 4&quot;-DA-B9-1X59-NI 6&quot;-DA-B9-1X56-NI | 0808C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Spectacle blind to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12441067 | 0809C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | High point vent to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12102022 | 0810C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Bleed valve to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12100351 | 0811C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | PB recommends high point vent not required at this location and try to minimise the number of vents | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | PC-0131 | 0812C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Penetration to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | CNI-2038 CNI-2043 CNI-2228 CNI-2266 | 0813C | 06/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Provide a drain at AFT end of the two diesel headers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | 8&quot;-D-H12N-0138-PP 8&quot;-D-H12N-0434-NI | 0814C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Sampling cabinet to be relocated close to sample point. Sample point to be minimum distance 3m from the branch connection. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | 1"-PCW-B26-0812-NI | 0815C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Model the bleed valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12100329 | 0816C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model the TIT connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | TIT-1212002 | 0817C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Model the XE and retrieval volume | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | XE-1231003 10&quot;-P-H12N-0694-NI | 0818C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Avoid pipe and install valve directly to the nozzle | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | VALV-12310531 | 0819C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Update the model to 4D bend | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | P-0323 | 0820C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Model the lever rotation vol, Check to relocate the lever towards the access side, If not possible rotation vol to be clash free | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09 |  | FE-1244001A | 0821C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Locker support to be updated as per standard detail | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | Z-H-5423085 | 0822C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Handrail to be updated while keeping clearance for valve operation | Handrail updated | KBR | STR | Pending PB Reply | 30/12/2025 | None |  | None | 08/01/2026 - UP56 - ok - close | SAF | None | None | M10B |  | VALV-54231009 | 0823C | 28/01/2026 | 2.00000000000000 | 6.00000000000000 | PB - Engineering | None | 08/01/2026 | True | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
4 | Handwheel and support of block valve to be oriented behind the hydrant | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | H-5423193 | 0824C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Extinguisher to be moved toward escape route to minimise interference by coaming | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | Z-5428268 | 0825C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Crossover step required where coaming crosses escape route | Cross over step modelled | KBR | STR | RE-OPEN | 31/12/2025 | None |  | None | None | SAF | None | None | M10B |  | OFLD-M10B-0097584 | 0826C | 19/01/2026 | 4.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 03/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
1 | Crossover step to be updated to clear interference with escape route | None | KBR | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | OFLD-M10A-1074863 | 0827C | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
2 | Crossover step to be modelled and coaming adjusted not to protrude into escape route | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | OFLD-M10C-0094718 | 0828C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | Crossover step to be modelled and coaming adjusted not to protrude into escape route | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | None | 0829C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | Crossover step to be modelled | Cross over step updated 09/01/26- Escape route clash cleared | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0830C | 19/01/2026 | -3.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 11/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 11/01/2026
3 | Escape route to be adjusted to avoid coaming | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | LEVEL-3-6-5142 | 0831C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Escape route volume to be modeled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | LEVEL-3-6-5137 | 0832C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Crossover step to be modelled | Cross over step updated 9/01/2026- Handrail clash cleared | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0833C | 19/01/2026 | -3.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 11/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 11/01/2026
4 | Crossover step or escape route to be updated to clear step's protrusion into escape route | Cross over step and escape route clash cleared | KBR | STR | Pending Seatrium Reply | 04/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0834C | 07/01/2026 | 3.00000000000000 |  | PB - Engineering | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
4 | Escape to to be modeled above crossover step | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | None | 0835C | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Crossover and coaming to be updated. Crossover to be in infill area | Cross over step updated. 9/01/2026- Handrail updated | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0836C | 19/01/2026 | -3.00000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 11/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 11/01/2026
5 | Handrail to be modelled at interconnections | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | None | 0837C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Handrail gap to be as per standard detail - typical punch for M10B | Handrail gap updated | KBR | STR | Pending Seatrium Reply | 06/01/2026 | None |  | None | None | PIP | None | None | M10B |  | None | 0838C | 22/01/2026 | 1.00000000000000 | 0 | PB - Engineering | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
1 | Vertical ladder 760 mm clearance to be maintained | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | None | 0839C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Vertical ladder safety cage height from deck to be 2m | None | KBR | STR | Pending PB Reply | 01/01/2026 | None |  | None | 08/01/2026 - UP56 - ok - close | SAF | None | None | M10B |  | None | 0840C | 28/01/2026 | 0 | 6.00000000000000 | PB - Engineering | None | 08/01/2026 | True | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
1 | Coaming to be modified so that ladder is outside coaming | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | None | 0841C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Top of cage to be same height as top of ladder | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | None | 0842C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Coaming to be adjusted to avoid water accumulation | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | None | 0843C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Vertical ladder safety cage height from deck to be 2m (typical for M10B ladders not above escape routes) | Ladder cage updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0844C | 28/01/2026 | 3.00000000000000 | 0 | PB - Engineering | None |  | None | None | 07/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 07/01/2026
1 | Handrail to be extended | Kick plate extended | KBR | STR | RE-OPEN | 01/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0845C | 22/01/2026 | 0 | 6.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
1 | Handrails to be modeled | Handrail updated | KBR | STR | RE-OPEN | 06/01/2026 | None |  | None | None | PIP | None | None | M10B |  | None | 0846C | 22/01/2026 | 1.00000000000000 | 0 | PB - Engineering | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
2 | Cross over steps to be modeled | Quater cut pipe modelled | KBR | STR | Pending PB Reply | 04/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0847C | 07/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Engineering | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
2 | Kick plates to be modeled | Kick plate updated | KBR | STR | Pending PB Reply | 01/01/2026 | None |  | None | 08/01/2026 - UP56 - There is a gap between the lickplate and the plataform - re-open | SAF | None | None | M10B |  | None | 0848C | 28/01/2026 | 0 | 6.00000000000000 | PB - Engineering | None | 08/01/2026 | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
2 | Handrail height to be extended with two rails due to nearby ladder. | Handrail Height extended | KBR | STR | RE-OPEN | 01/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0849C | 28/01/2026 | 0 | 6.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
2 | Handrail height to be extended due to ladder less than 1500mm distance | Handrail updated | KBR | STR | Pending PB Reply | 04/01/2026 | None |  | None | 08/01/2026 - UP56 - ok - close | SAF | None | None | M10B |  | None | 0850C | 28/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Engineering | None | 08/01/2026 | True | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
3 | Handrail to be provided | Handrail provided | KBR | STR | RE-OPEN | 01/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0851C | 28/01/2026 | 3.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 04/01/2026
3 | Kickplate to be modeled | Kick plate extended | KBR | STR | RE-OPEN | 01/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0852C | 28/01/2026 | 0 | 6.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | Ladder to be outside the coamed area | Coaming plate updated | KBR | PIP | RE-OPEN | 01/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0853C | 28/01/2026 | 0 | 6.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | Fall arrestor to be modelled | Ladder cage updated 09/01/2026- Fall arrestor modelled | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0854C | 28/01/2026 | -3.00000000000000 | 3.00000000000000 | PB - Engineering | None |  | None | None | 11/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 11/01/2026
3 | Deluge piping too close to ladder | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | None | 0855C | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
4 | Handrails and kickplates to be updated all around this platform, as per the standard | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | None | 0856C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
4 | Handrail to be modeled | Handrail updated | KBR | STR | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0857C | 28/01/2026 | 0 |  | PB - Engineering | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
4 | Ladder is missing safety bar. Fall arrestor to be modelled. | Safety bar updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0858C | 28/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Engineering | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
4 | 300mm coaming height to be considered | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | None | 0859C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Equipment coaming to be adjusted as marked to avoid water accumulation | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M10B |  | None | 0860C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Check the requirement for the quarter pipe. Coaming to run column to column. | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M10B |  | None | 0861C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Foam headers routed and penetrating inside equipment coaming. Check with Safety and relocate outside coaming if required. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | V-5331001 FL-1845 FL-1847 FL-1846 | 0862C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Handrail height to be extended due to ladder less than 1500mm distance | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | None | 0863C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
5 | Handrail and kickplate to be extended | Handrail updated | KBR | STR | Pending PB Reply | 04/01/2026 | None |  | None | 09/01/2026 -UP56 - ok - close | SAF | None | None | M10B |  | None | 0864C | 28/01/2026 | 1.00000000000000 | 3.00000000000000 | PB - Engineering | None | 09/01/2026 | True | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
4 | Stair landing kickplates to be extended. Typical punch for M10B | Kickplate extended | KBR | STR | Pending PB Reply | 04/01/2026 | None |  | None | None | SAF | None | None | M10B |  | None | 0865C | 20/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Engineering | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
3 | Limited access to instruments. Proposed to move the PIT and Sampling point into module. Typical for M07A & B | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | PIT-1231109 PIT- 1231125 AIT-1231010 PIT-1231126 PIT-1231110 | 0866C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
3 | High point vent type to be checked and updated as per standard detail - cap vs flange | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-0474 | 0867C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
None | Access volume to T-type strainers to be modelled. Typical for all strainers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | None | 0868C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
1 | 500mm reserve volume to be modeled in front of LITs for maintenance space. PB Operations agreed downward orientation is acceptable. | None | None | PIP | OPEN | 01/02/2026 | None |  | None | None | PIP | None | None | M07A/B |  | None | 0869C |  | -25.0000000000000 |  | PB - Operation | None |  | None | None | 04/02/2026 |  |  |  |  | 04/02/2026
1 | Utility connection check valve to be relocated close to elbow, 450 to 500mm in front of valve to be provided for access. Typical for all Utility connections. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | VALV-12310058 | 0870C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Bolt removal to be verified | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-0091 VALV-12311202 VALV-12312449 VALV-12312448 VALV-12312503 VALV-12312502 PSV-1231103A PSV-1231104A VALV-12311122 VALV-12310726 VALV-12310500 VALV-12310499 VALV-12520092 VALV-12310046 VALV-12310045 VALV-12310206 VALV-12310048 FV-1231041A FV-1231041B VALV-12311168 VALV-12310395 VALV-12310751 VALV-12310462 VALV-12310183 VALV-12310247 VALV-12311205 VALV-12310092 ESP-12310083 ESP-12310080 ESP-12310338 ESP-12520051 | 0871C | 26/01/2026 |  |  | PB - Operation | None |  | None | None
1 | LG vent and drain to be modeled - typical for all LGs | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | LG-1231006A | 0872C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Block valve to be as close as possible to the nozzle. Bolt removal to be considered. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | VALV-12310046 | 0873C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
1 | To check with Process if the piping configuration is acceptable considering slope/no pocket requirements. I-DE-3010.2S-1231-944-S2N-006 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | 3"-P-C6N-0439-NI | 0874C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Sample connection to be upstream of the branch. Valve to be updated to DBB. Sampling box to be relocated to provide access to DBB. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-0096 | 0875C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Requirement of vent for commissioning to be checked with Process - typical for anti-surge hot gas bypass | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | XV-1231010A/B | 0876C | 26/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Vent without valve to be flanged | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-1872 | 0877C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Valve handwheel to be corrected to accessible orientation | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | VALV-12311017 | 0878C | 11/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Access to the utility connection is blocked by instrument stands | 17/12/25 - F&G devices is a Safety item and to be resolve by Safety discipline. | None | SAF | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | AST-CH4-M07A-201-014 AST-CO2-M07A-201-012 | 0879C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Filling vent to be provided at the high point for cooling water lines at exchangers. Typical for all compressors. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | 3&quot;-W-B10-3207-NI 4&quot;-W-B10-3210-NI 4&quot;-W-B10-3211-NI 4&quot;-W-B10-3214-NI 4&quot;-W-B10-3217-NI | 0880C | 12/01/2026 |  |  | PB - Operation | None |  | None | None
1 | High point vent to be provided either at inlet or outlet line. Access to valve is not required to be provided. Typical for all compressors. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | W-3204 W-3207 | 0881C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Gap to be maintained at tundish | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | DA-1735 DA-1736 | 0882C | 12/01/2026 |  |  | PB - Operation | None |  | None | None
1 | All instrument air and nitrogen lines to be modeled - general comment | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | None | 0883C | 26/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Air line and drain lines to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | PN-UC-1231002A-02_TANK PN-UC-1231002B-02_TANK PN-UC-1252001A-02_TANK | 0884C | 12/01/2026 |  |  | PB - Operation | None |  | None | None
2 | To check with the compressor vendor on the distance between flame arrestor and the oil mist equipment. Drop limit pressure to be updated on P&ID. Typical for all compressors | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | OL-0123 | 0885C | 12/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Goose neck vent to be added | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | IA-1152 IA-1158 IA-1158 | 0886C | 12/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model vent and Drain valves for the LG and check with process to remove the break flange from the stand pipe | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | LG-1231101B | 0887C | 12/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Handrail to be modified for valve operation | Handrail updated for valve operation | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | PIP | None | None | M07A/B |  | TMHandrail-5-1595 | 0888C | 22/01/2026 | 7.00000000000000 | 6.00000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 28/12/2025
1 | All tie-in connections to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | None | 0889C | 13/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure clear access around platform | None | None | PIP | OPEN | 01/02/2026 | None |  | None | None | PIP | None | None | M07A/B |  | ACCESS PLATFORM FRP GRATING | 0890C |  | -25.0000000000000 |  | PB - Operation | None |  | None | None | 04/02/2026 |  |  |  |  | 04/02/2026
1 | Handrail to be provided at gap on compressor package | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | None | 0891C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Piping to be connected to tie-in - typical for all compressors | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | 1&quot;-OL-B3-0124-PP 6&quot;-OL-B3-0125-PP 1&quot;-DFC-H3N-1847-PP 1/2&quot;-DFC-B9-1848-NI | 0892C | 13/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Handrail to be provided at gap on compressor package | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | None | 0893C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Evaluate reorienting the drain valves to provide access | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | W-3182 W-3193 | 0894C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Gap opening through access platform to be filled | None | None | PIP | OPEN | 01/02/2026 | None |  | None | None | STR | None | None | M07A/B |  | None | 0895C |  | -25.0000000000000 |  | PB - Operation | None |  | None | None | 04/02/2026 |  |  |  |  | 04/02/2026
1 | Instrument dials and valves in Injection package to be reoriented for access from within skid. Ensure panel opening is clash free. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | None | 0896C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Handrail to be provided at gap on compressor package | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | None | 0897C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Handrail to be provided at gap on compressor package. Gaps at handrails to be minimised as per standard detail - typical 75mm, max 125mm. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | None | 0898C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Handrail not required in front of seal gas panel | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M07A/B |  | PultrudedHandrail_E3-7-0996 PultrudedHandrail_E5-7-3920 | 0899C | 13/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Access to the compressor platform behind working oil cooler to be evaluated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | W-3207 | 0900C | 13/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Casing drain valves' levers to be easily accessible as per HAZOP recommendation. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | None | 0901C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Remove the ladder near the compressor skid and keep the pipe rack side ladder. Model accessway from piperack to the compressor | None | None | PIP | OPEN | 01/02/2026 | None |  | None | None | PIP | None | None | M07A/B |  | LadderA1-5-0630 | 0902C |  | -25.0000000000000 |  | PB - Operation | None |  | None | None | 04/02/2026 |  |  |  |  | 04/02/2026
1 | Remove the handrails | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | Top-MountedFixedGuardrail-7-1247 Top-MountedFixedGuardrail-7-1248 | 0903C | 13/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipe support to be modified to give more space in the platform | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | SP-M07A-59341 | 0904C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Coaming segregations between the vessels to be kept to avoid overflow near the drain box on the piperack. | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M07A/B |  | OFLD-M07A-0070529 OFLD-M07A-0070527 | 0905C | 13/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Coaming to be modified as marked to avoid water accumulation | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M07A/B |  | OFLD-M07A-0089184 | 0906C | 13/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Increase the height of the coaming to 200mm at the marked locations with tapered end | None | None | PIP | OPEN |  | None |  | None | None | STR | None | None | M07A |  | None | 0907C | 14/01/2026 |  |  | PB - Operation | None |  | None | None
4 | PDIT to be updated to correct orientation for liquid service | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | PDIT-1231018A PDIT-1231034A PIT-1231036B PDIT-1231034B PDIT-1231018B PIT-1231036A PDIT-1231003B PDIT-1231003A | 0908C | 14/01/2026 |  |  | SEA/KBR | None |  | None | None
2 | FE tappings to be modelled. Typical for all Compressors. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | FE-1231003A/B FE-1231004A/B FE-1252006A | 0909C | 14/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Supports to be modeled for anti-surge and HGBV for all compressors. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | P-2080 P-2062 P-2077 P-2061 | 0910C | 14/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Modify utility connection line to be within the coaming - typical for all compressors | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | VALV-12310132 / VALV-12310210 / VALV-12311283 / VALV-12311186 | 0911C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
4 | PDIT to be relocated to upstream of valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | PDIT-1231003A | 0912C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Check if the valve can be mounted directly to the nozzle - typical for all filters | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | FT-P-UC-1231002A-02 | 0913C | 14/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Mismatch between PSV flange and connecting flange | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | PSV-1231015A-A PSV-1231015A-B | 0914C | 14/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Flanged outlet to be modelled as per P&ID note 8 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | W-0163 | 0915C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Pipe spool to be shortened to reduce dead leg. Typical for all M07A/B utility connections. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | VALV-12310140 | 0916C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Penetration type to be updated to plating | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | PG-M07A-L4-36302 | 0917C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | 500mm box be modelled in front of LIT to reserve space for maintenance. Typical for all LITs | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | None | 0918C | 02/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Flushing ring to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | LIT1231026A/B LIT-1231009A/B LIT-1252004A LIT-1252003A | 0919C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
1 | LG to be modeled - typical for all Scrubbers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | None | 0920C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
5 | TITs to be modeled downstream of PSVs | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | TIT-1231114A-A/B/C / B-A/B/C | 0921C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Purging line to be modeled for flare headers and provide access to the valves. Attention to note 3 of P&amp;ID I-DE-3010.2S-5412-944-S2N-009 I-DE-3010.2S-5412-944-S2N-010 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | 1&quot;-F-B3N-0872-NI VALV-54120151 VALV-54120152 1&quot;-F-C3N-0884-NI - VALV-54120195 1&quot;-F-B3N-1077-NI VALV-54120181 | 0922C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Sampling connection to have DBB and reduce length from tapping point. Check with process on location of the tapping point. Piping connection to the sample box to be modeled. Typical for all sampling points. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | P-0548 | 0923C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve arrangement and handwheel orientation to be updated. Typical for DBB valves with catalogue update. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | VALV-12312410 / VALV-12310034 / VALV-12310038 / VALV-12310086 / VALV-12310073 | 0924C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Locate the valves as close as possible to the instrument panel nozzles | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | PN-1231007 VALV-12311324 / VALV-12310162 /VALV-12311319 | 0925C | 15/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Instrument Air connections to export metering to be modeled. Flame arrestor line to be modeled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | 2&quot;-F-B10N-1947-NI 2&quot;-F-B3N-2056-NI 2&quot;-F-B3N-1945-NI | 0926C | 18/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Flare line from MIT and the connection from the pipe to MIT to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-0769 | 0927C | 18/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Spool length to be shortened. Check valve to be modeled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-0294 | 0928C | 18/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Vent valve to be as close as possible to the nozzle | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-1840-N11 | 0929C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Bolts to be modeled on the outlet line for Second Stage Scrubber and the Injection Scrubber. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-0688 | 0930C | 18/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Block valve to be as close as possible to the nozzle. Valve category change to 3. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | VALV-12520092 | 0931C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Block valve to be as close as possible to the nozzle. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | VALV-12520091 | 0932C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipe support to be modified to have clear access to the handwheel | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | SP-M07A-56343 VALV-12520100 | 0933C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Piping to be connected. Piping configuration to be checked with Process considering No Pocket requirement for the seal gas line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | 3&quot;-PC-C3N-0319-PP 2&quot;-PC-H40N-2520-PP | 0934C | 18/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Flange mismatch to be fixed. Bolts to be modeled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-2056 P-0688 | 0935C | 18/01/2026 |  |  | PB - Operation | None |  | None | None
5 | PSVs to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | None | 0936C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Flange mismatch at TITs to be fixed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | TIT-1252002A-D TIT-1252002A-B TIT-1252002A-A | 0937C | 19/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate instruments behind FE | None | PB Ops | CSE | OPEN |  | None |  | None | None | PIP | None | None | M09C |  | FIT-1210015N-1 FIT-1210015N-2 PIT-1210015N | 10579C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
General | Rearrange the tubing to meet sloping requirement | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09C |  | General | 10580C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
General | Tubing penetration to be modeled where ever is missing | None | PB Ops | CSE | OPEN |  | None |  | None | None | PIP | None | None | M09D |  | PDA-M09D-NE-02 | 10581C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Punch Deleted and agreed by SEA and PB | None | PB Ops | CSE | Pending PB Reply |  | None |  | None | None | INST | None | 23-DEC-2025 SEA REMARKS: Punch Deleted and agreed by SEA and PB | M09D |  | General | 10582C | 26/02/2026 |  | 16.0000000000000 | PB - Operation | True |  | None | None |  | 25/12/2025 |  |  | 25/12/2025
None | Relocate the instrument away from handwheel. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09D |  | PIT-1231051 | 10583C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Reorient and relocate the air manifold away from transmitters. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09D |  | PDA-M09D-E-02 | 10584C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate transmitters and manifold as marked | None | PB Ops | CSE | OPEN |  | None |  | None | None | PIP | None | None | M09D |  | PDA-M09D-NE-05 | 10585C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
General | Cable tray and tubing trays to be modelled where ever missing | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09E |  | General | 10586C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
General | Punch Deleted and agreed by SEA and PB | None | PB Ops | CSE | Pending PB Reply |  | None |  | None | None | INST | None | 23-DEC-2025 SEA REMARKS: Punch Deleted and agreed by SEA and PB | M09E |  | General | 10587C | 26/02/2026 |  | 16.0000000000000 | PB - Operation | True |  | None | None |  | 25/12/2025 |  |  | 25/12/2025
Level 2 | Relocate the instruments near to pipe for maintenance access. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09E |  | FIT-1210003V-1 | 10588C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
General | Cable tray penetration to be modelled wherever missing. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09E |  | General | 10589C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Re orient and relocate instrument. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09E |  | PIT-1244016U | 10590C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Need to discuss with safety about handling path requirement. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09E |  | PDA-M09E-NE-04 | 10591C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Rearrange the transmitter and manifold. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09E |  | PDA-M09E-NE-05 | 10592C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Relocate the instrument from valve and ensure proper access. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09F |  | PIT-1210004P | 10593C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate instruments closer to pipe for better access. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09F |  | FIT-1210001W-1 FIT-1210001W-2 PIT-1210001W | 10594C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Instrument to be relocated. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09F |  | PIT-1210015R | 10595C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
General | Rearrange tubes to meet sloping requirement. Also ensure correct tapping orientation. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M09F |  | General | 10596C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Relocate the instrument away from hand wheel. | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M09F |  | PIT-1244002P | 10597C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Instrument/Piping to ensure actuator panel is accessible. | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M09F |  | BDV-1252003 | 10598C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | CCTV should shift to opposite side as per operation team recommendation and need to check with Hull pulley handling team. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09A |  | CAM-5514036 | 10599C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | CCTV should shift to opposite side as per operation team recommendation and need to check with Hull pulley handling team. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09D |  | CAM-5514037 | 10600C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | CCTV height should be reduced to 2.1m | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09A |  | CAM-5514038 | 10601C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | CCTV height should be reduced to 2.1m | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09F |  | CAM-5514039 | 10602C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Relocate the BLE to column mount | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09B/D |  | BLE-5511142 BLE-5511140 | 10603C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Check the location and height | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09E |  | BLE-5511143 | 10604C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 3 | Rotate the BLE to 90deg | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09A |  | BLE-5511145 | 10605C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 3 | Shift the camera as per mark up and height should be 2.1m | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09A |  | CAM-5514040 | 10606C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 3 | Shift the camer away from obstruction | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09E |  | SPP-M09E-00008 | 10607C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Lower the camera height to 2.5m | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09F |  | SPP-M09F-00006 | 10608C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 3 | Relocate the speaker as per mark up | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09C |  | COR-5518168B | 10609C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 4 | Relocate the speaker as per mark up | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09A/D |  | COR-5518181A SPP-M09D-00009 | 10610C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 4 | Relocate BLE to column mount | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09B |  | BLE-5511153 | 10611C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 4 | Extend the BLE support | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09D |  | BLE-5511157 | 10612C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 4 | Change the BLE support facing platform side | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09F |  | BLE-5511161 | 10613C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 5 | Move the BLE inside the platform | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09D |  | SPP-M09D-00017 | 10614C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 4 | Move the camera as per operation team recommendation to option 1 or option 2. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09 |  | CAM-5514044 | 10615C | 28/01/2026 |  |  | PB - Operation | None |  | None | None
General | Secondary trays and penetrations are missing for Telecom equipment. General for M09 | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M09 |  | General | 10616C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
General | Alignment of MCT and tray to be considered in cable routing, cable bending to be considered in close-out. Typical for M09A to F. | Alignment of MCT and tray is considered in cable routing, MCT's are placed as much as closer and brought front of cable tray for cable bending. | SEA | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 05-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M09 |  | General | 10617C |  | 17.0000000000000 | 3.00000000000000 | SEA/KBR | True |  | None | None | 21/12/2025 | 07/01/2026 |  |  | 07/01/2026 | 21/12/2025
Level 3 | Provide tray below lighting panel to support the cables. | Tray provided below lighting panel to support the cables. | SEA | ELE | Pending PB Reply | 05/12/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M09A/D |  | PL-5148009 | 10618C |  | 14.0000000000000 | 19.0000000000000 | SEA/KBR | True |  | None | None | 08/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 08/12/2025
None | Tray routing and supports arrangement to be optimized. Tray sizes to be checked. | Tray routing and support arrangement optimized. Tray sizes are verified. | SEA | ELE | RE-OPEN | 24/12/2025 | None |  | None | None | ELE | None | None | M09A |  | ET-M09A-L-N-TRAY-30000-TRAY | 10619C |  | 12.0000000000000 | 2.00000000000000 | SEA/KBR | None |  | None | None | 27/12/2025 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 28/12/2025
None | Model all related electrical tray/supports/penetration within HPU area. | None | SEA | PIP | OPEN |  | None |  | None | None | ELE | None | None | M09A |  | UH-1210001 | 10620C | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Socket location and handling equipment to be checked. Socket location to suit space occupied by handling activities/equipment. | Socket location and handling equipment checked. Handling doesnt require "A frame" arrangement for handling equipments. Hence A frame is deleted by handling. | SEA | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M09C |  | SKN-M09C-408 | 10621C |  | 4.00000000000000 | 16.0000000000000 | SEA/KBR | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
Level 4 | Check options to bring MCT in front of socket support/stand. | MCT relocated in front of socket support/stand. | SEA | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M09C |  | SKN-M09C-417 | 10622C |  | 8.00000000000000 | 19.0000000000000 | SEA/KBR | True |  | None | None | 14/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 14/12/2025
Level 2 | Sockets are frequently accessed by operations team compared to the instrumentation JBs. Swap positions of assembled sockets and instrumentation JBs. | Positions of assembled sockets and instrumentation JB's are swapped. | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M09D |  | SKN-M09D-421 | 10623C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
Level 4 | Socket support too close to nearby pipe support, welding issues foreseen. Adjust position of socket support accordingly, to ensure constructability. MCT to be adjusted accordingly. | Space between socket support and pipe support is around 60mm for welding clearance. MCT is adjusted with all around clearance of 50mm. | SEA | ELE | RE-OPEN | 11/12/2025 | None |  | None | None | ELE | None | None | M09D |  | SKN-M09D-411 | 10624C |  | 8.00000000000000 | 19.0000000000000 | SEA/KBR | None |  | None | None | 14/12/2025 | 22/12/2025 | 24/12/2025 | 24/12/2025 | 22/12/2025 | 14/12/2025
None | Position of flame detector to be evaluated considering JB position. If JB position obstructs detector coverage, flame detector to be re-positioned accordingly. | None | SEA | CSE | OPEN |  | None |  | None | None | SAF | None | None | M09D |  | UST-M09D-301-001 | 10625C |  |  |  | SEA/KBR | None |  | None | None
Level 4 | Penetration model to be added accordingly. | MCT modelled for moisture analyser | SEA | ELE | RE-OPEN | 11/12/2025 | None |  | None | None | ELE | None | None | M09D |  | MIT-1231001-MOISTURE ANALYZER | 10626C |  | 8.00000000000000 | 19.0000000000000 | SEA/KBR | None |  | None | None | 14/12/2025 | 22/12/2025 | 24/12/2025 | 24/12/2025 | 22/12/2025 | 14/12/2025
Level 2 | Sockets obstructed by detector. Re-position the sockets and detector to resolve access issues to socket. | Sockets and detector repositioned to resolve acess issue to socket. | SEA | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M09E |  | SKN-M09E-416 | 10627C |  | 4.00000000000000 | 16.0000000000000 | SEA/KBR | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
None | Adjust socket support slightly forward, ensuring minimum welding space is still provided for socket support. | Socket support adjusted slightly forward and ensured a minmum welding space of 50mm provided for socket support. | SEA | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M09E |  | SKN-M09E-405 SPS-M09E-002 | 10628C |  | 8.00000000000000 | 19.0000000000000 | SEA/KBR | True |  | None | None | 14/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 14/12/2025
None | Socket support and drain box to be adjusted accordingly. Support should not stand on drain box. | Drain box adjusted to avoid support standing on drain box | SEA | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M09F |  | SKN-M09F-421 | 10629C |  | 4.00000000000000 | 16.0000000000000 | SEA/KBR | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
None | Trimmer beams to be added whenever required, accordingly. However, trimmer beam addition to be avoided if there are nearby exitsing beam which can be used. | Trimmer beam added as per requirement. | SEA | ELE | Pending PB Reply | 11/12/2025 | None |  | None | None | ELE | None | 20-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M09F |  | CXN-L-M09F-407 | 10630C |  | 8.00000000000000 | 19.0000000000000 | SEA/KBR | True |  | None | None | 14/12/2025 | 22/12/2025 |  |  | 22/12/2025 | 14/12/2025
None | Fixed end of drag chain for electrical/instrument cable connection to be modelled by HULL. E&I cable trays and supports from O/H crane interface JB and fixed end of drag chain to be modelled by Topsides. | E&I cable trays and supports from O/H crane interface JB and fixed end of drag chain modelled by Topsides. | SEA | ELE | OPEN | 21/12/2025 | None |  | None | None | ELE | None | None | M09C |  | PS-M09C-0009663 | 10631C | 12/02/2026 | 17.0000000000000 |  | SEA/KBR | None |  | None | None | 24/12/2025 |  |  |  |  | 24/12/2025
General | Ensure that all sub-cable trays are properly terminated and connected to the bottom of each JB. All lighting fixtures shall be connected using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all lights and JB within Module M09. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09 |  | General LNO-216-02-M09A-001 CXN-L-M09B-018 LNO-217-08-M09E-003 | 10632C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Avoid pole mounted lights outside handrail if alternative is available for easier accessibility during operations. Mount light at nearby tubular column, respective trays to be modified accordingly. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09A/D/E |  | LEM-333-04-M09A-001 LEM-332-03-M09A-001 LES-304-08-M09D-001 LES-304-10-M09E-003 | 10633C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Check if light can be mounted on nearby tubular column, but maintaining the lux level requirement for front side of lighting panels. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09A |  | LEM-333-04-M09A-002 | 10634C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Check and extend support to avoid being blocked by pipe for light coverage. Related sub-tray to be modelled. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09B |  | LNO-216-15-M09B-003 | 10635C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
General | Floodlight / linear light to be mounted on top of nearby pipe support. Relevant supports required to suit installation at top of pipe support to be checked and addressed. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09 |  | LNO-216-19-M09B-002 LEM-333-06-M09B-006 LNO-216-20-M09C-001 LNO-217-07-M09D-004 LES-304-04-M09D-001 LNO-217-18-M09D-002 LNO-217-18-M09D-003 LNO-217-18-M09D-005 LEM-335-07-M09E-002 LNO-217-14-M09E-003 LNO-217-20-M09F-002 | 10636C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Acceptable welding space to be verified with STR discipline. Floodlight to adjust elevation accordingly. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09A-F |  | LES-303-02-M09C-003 | 10637C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Welding issues foreseen. Resolve using different type of mounting for floodlight. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09C/D/E |  | LNO-216-07-M09C-005 LEM-334-03-M09D-002 LNO-217-07-M09E-006 | 10638C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Tray to be shifted closer to column, to improve JB access. | Tray shifted to column to have better access to JB | PB Ops | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 06-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M09D |  | LEM-335-01-M09D-006 | 10639C |  | 12.0000000000000 | 2.00000000000000 | PB - Operation | True |  | None | None | 27/12/2025 | 08/01/2026 |  |  | 08/01/2026 | 28/12/2025
None | Light support too close to pipe on top, causing difficulty in pipe preservation works. Lighting to be adjusted accordingly. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09D |  | LNO-217-01-M09D-002 | 10640C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Bring tray at other side so cable will not touch the nearby small bore pipes. | Tray Moved to Opp. side as per comments | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09F |  | LEM-335-04-M09F-004 | 10641C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Adjust location of pole to south side, creating space between tray and nearby pipe elbow, and avoiding pinch point against valve handwheel. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09F |  | LES-304-15-M09F-001 | 10642C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
General | Mount light at nearby beam instead of pole outside guard rail. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09 |  | LEM-334-08-M09F-006 | 10643C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
None | Linear lights with sea projection to consider 1.7m mounting height, to be checked in lighting calculation. Floodlights with sea projection to consider moving to other side of column (near L2) inward, to be checked in lighting calculation. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M09 |  | LNO-217-05-M09F-005 LEM-335-02-M09F-004 LNO-217-05-M09F-005 LEM-334-02-M09F-003 LEM-335-02-M09E-003 LNO-217-05-M09E-003 LEM-335-02-M09E-002 LNO-217-05-M09D-002 LEM-334-02-M09D-001 LES-304-02-M09D-001 LEM-335-02-M09D-001 LNO-217-05-M09D-001 LEM-333-02-M09C-008 LES-303-03-M09C-003 LEM-332-02-M09C-008 LNO-216-03-M09C-005 LEM-333-02-M09C-006 LNO-216-03-M09B-004 LEM-332-02-M09B-006 LEM-333-02-M09B-004 LNO-216-03-M09B-003 LEM-332-02-M09B-004 LNO-216-03-M09A-002 LEM-332-02-M09A-002 LES-303-03-M09A-001 | 10644C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | The junction box should be check and relocated. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07A |  | SPP-M07A-0003 | 10645C | 28/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | To relocate the BLE-5511117 to the column L-type | BLE-5511117 has been relocated as per the snapshot | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M07A |  | BLE-5511117 | 10646C | 28/12/2025 | 3.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
Level 1 | Move CAM-5514027 to the new proposed location as shown in the snaphot (STBD side). | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07A |  | CAM-5514027 | 10647C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | To check the location and relocate for better cabling | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07A |  | COR-5518105A COR-5518105B | 10648C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | To move the speaker as per the snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-07A |  | COR-5518110B | 10649C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Cable ladder accessories to be provided to meet cable bending radius requirement. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-07A |  | CDI-5518007B CJE-5518007B | 10650C | 28/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | BLE-5511119 to be moved to staircase platform support | BLE-5511119 has been relocated to the staircase platform support as per the markup | KBR | TEL | Pending Seatrium Reply | 06/01/2026 | None |  | None | None | TEL | None | None | M-07A |  | BLE-5511119 | 10651C | 28/12/2025 | 1.00000000000000 |  | SEA/KBR | None |  | None | None | 09/01/2026 |  |  |  |  | 11/01/2026
Level 2 | BLE-5511118 to be relocated to another facing (south) | BLE-5511118 has been moved to the south-facing side as per markup | KBR | TEL | Pending Seatrium Reply | 06/01/2026 | None |  | None | None | TEL | None | None | M-07A |  | BLE-5511118 | 10652C | 28/12/2025 | 1.00000000000000 |  | PB - Engineering | None |  | None | None | 09/01/2026 |  |  |  |  | 11/01/2026
Level 2 | To move the Electrical LNO-214-04-M07A-001 to the left and move Telecom speaker COR-5518115B adjacent to | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07A |  | LNO-214-04-M07A-001 COR-5518115B | 10653C | 29/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | To move ANT-5515018 inside the module | ANT-5515018 has been moved inside the module. | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M07A |  | ANT-5515018 | 10654C | 28/12/2025 | 3.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
Level 3 | To relocate CAM-5514029 to North as shown in the snapshot | CAM-5514029 has been moved as per the mark up | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M07A |  | CAM-5514029 | 10655C | 28/12/2025 | 3.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
Level 3 | To relocate the BLE-55111121 to the opposite side | BLE-5511121 has been relocated as per the mark up | KBR | TEL | Pending Seatrium Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M07A |  | BLE-55111121 | 10656C | 28/12/2025 | 2.00000000000000 |  | SEA/KBR | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
Level 4 | To relocate the COR-5518122B - as per the mark-up in the snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07A |  | COR-5518122B | 10657C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | To move the speaker COR-5518121A to the platform support - as per the mark up in the snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07A |  | COR-5518121A | 10658C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | CAM-5514030 clashing with Electrical ligting support to be resolved - away from the 360-view volume. | The clash between CAM-5514030 and the electrical system has been resolved | KBR | TEL | Pending PB Reply | 05/01/2026 | None |  | None | None | TEL | None | None | M07A |  | CAM-5514030 SPL-M07A-00443 | 10659C | 28/12/2025 | 3.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 08/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 08/01/2026
General | Secondary trays are missing for Telecom equipment. General for M07A | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07A |  | General | 10660C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Cable tray to be re-routed to avoid behind the vertical cable ladder | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M07A |  | IC-M07A-S-I-TRAY-01008 | 10661C |  |  |  | SEA/KBR | None |  | None | None
General | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all Instruments, JB and valves M07A. Also the Tray which running close to the deck is should be checked and routed above the coaming height. | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M07A |  | General | 10662C | 17/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Move the instrument towards East side to avoid clash | 10-01-26: relocted the instruments. | SEA | CSE | Pending Seatrium Reply | 09/01/2026 | None |  | None | None | INST | None | None | M07A |  | SPI-M07A-255 | 10663C | 19/02/2026 | -1.00000000000000 |  | SEA/KBR | None |  | None | None | 12/01/2026 |  |  |  |  | 12/01/2026
Level 2 | Relocate the transmitter away from the valve. Trays also needs to be rerouted. | None | PB Ops | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-07A |  | PDIT-1252003A PDIT-1252007A | 10664C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2<br>Level 4 | Relocate the transmitter close to the tapping point. (For example: for PIT-1252009A - pit it infront of penetration.) | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | PIT-1252002A PIT-1252009A PDIT-1231002B (Level 4) | 10665C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Move the transmitter and Penetration west side little bit. | KBR Comment - relocated the instruments | KBR | CSE | Pending Seatrium Reply | 05/01/2026 | None |  | None | None | INST | None | None | M-07A |  | PIT-1252063A PIT-1252066A | 10666C | 29/01/2026 | 2.00000000000000 |  | PB - Operation | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
Level 2 | Change the type of mounting to column mounting in the near column. | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | TIT-1231003A TIT-1231007A | 10667C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | To model the tubing penetration wherever missing | KBR Comment - Tubing Penetration updated. | KBR | CSE | Pending Seatrium Reply | 05/01/2026 | None |  | None | None | ELE | None | None | M-07A |  | PDA-M07A-E-03 | 10668C | 29/01/2026 | 2.00000000000000 |  | SEA/KBR | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
Level 2 | Need include flushing ring and tapping point Diff. Pressure Level Transmitter - Provide Flushing ring to allow cleaning and reduce maintenance time These instruments are classified as capillary diaphragm instruments, therefore they must have a flushing ring to allow for cleaning and calibration. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 | None | PB Ops | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-07A |  | LIT-1231002A LIT-1231002B LIT-1231003A LIT-1231003B LIT-1231009A LIT-1231009B LIT-1231026A LIT-1231026B VALV-12310203 VALV-12310204 | 10669C | 02/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Move the penetration away from the beam. Maintain some distance from the beam. Combine the penetrarion into single pentration | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | I-M07A-S-PEN-355 PIT-1252044A | 10670C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Electrical and Instrument cable trays need to be modelled for the Analyser panel. PN-1231007, PN-1231010, PN-AT-1231006, PN-MT-1231008, PN-MT-1252001 Need to check with Structural whether any platform is required to access the panel. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-07A |  | PN-1231007 PN-1231010 PN-AT-1231006 PN-MT-1231008 PN-MT-1252001 | 10671C | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Electrical JB to be located on the opposite side of the column. The Transmitter to be mounted on the column. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-07A |  | FIT-1231130A | 10672C | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Reroute the tubing tray through the floor maintining 200mm distance from the floor. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | PDIT-1231002A | 10673C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Check the possibilities to relocate the transmitter to the column | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | PDIT-1231003B PIT-1231015B PIT-1231021B | 10674C | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Move the transmitter in between the penetration and combine the penetration into sinlge pnetration. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | PDIT-1231006B | 10675C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | To combine both tube trays. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | PDIT-1231014B | 10676C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Reroute the tubing from transmitter to tapping point. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | PIT-1231013B | 10677C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Check the possibilities to relocate or check with MH to adjust the MH path. | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | PDA-M07A-NE-02 | 10678C |  |  |  | PB - Operation | None |  | None | None
Level 5 | To move the panel to the opposite side of the valve for the better access. | None | PB Ops | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-07A |  | FV-1231041A | 10679C | 02/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Relocate the volume tank and skid away from the walkway. V-BDV-1252014A-2, V-BDV-1231002B | None | PB Ops | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-07A |  | V-BDV-1252014A-2 V-BDV-1231002B | 10680C | 02/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | "Transmitters with the same tag PDIT-1252024A | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07A |  | DIFF. PRESS. TRANSM. W/ INDICATOR - ELEV3 PDIT-1252024A | 10681C | 12/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 5 | No tapping point found for this instruments. PIT-1231110 PIT-1231126 PIT-1252009A PIT-5412010 PIT-5412011 PIT-5412012 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-07A |  | PIT-1231110 PIT-1231126 PIT-1252009A PIT-5412010 PIT-5412011 PIT-5412012 | 10682C | 02/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Not enough space to install MCT. Installation space to be resolved. Vendor tray to suit the cable entry plan/bending, avoiding blockage to MCT location. | Awaiting info from Vendor Siemens | SE | MECH | OPEN |  | None |  | None | None | ELE | None | None | M-07A |  | ET-M07A-H-TRAY-05002 | 10683C | 17/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Check how to access vendor JB (Instrument). Vendor to resolve access issues. | None | PB | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-07A |  | UC-1231002A-07NOV25 | 10684C | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Cable bending issues foreseen. Modify type of penetration to suit the cable routing considering cable bending radius requirements. | Cable tray and pentration is updated by considering cable bending radius | SEA | ELE | RE-OPEN | 11/12/2025 | None |  | None | None | ELE | None | None | M-07A |  | ET-M07A-L-N-TRAY-20004 | 10685C |  | 8.00000000000000 | 19.0000000000000 | SEA/KBR | None |  | None | None | 14/12/2025 | 22/12/2025 | 24/12/2025 | 24/12/2025 | 22/12/2025 | 14/12/2025
2 | Instrumentation need to relocate away from flange. | 8/1/26 - AST is a F&G devices and not Instrument item. This is to be resolve by Safety. | None | SAF | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | AST-CH4-M09A-201-002 AST-CO2-M09A-201-001 | 20146C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Tag number in selection tree is wrong. There are 2 beams, should have 2 tag numbers. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | SS-M09A-0553208 | 20147C | 08/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Turning radius to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | HV-1223070 SPP-M09A-00011 | 20148C | 21/02/2026 |  |  | PB - Operation | None |  | None | None
3 | General comment: Stacker model to be updated with actual/vendor dimensions. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | GEN/M-09A |  | VALV-12100852 | 20149C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
3 | support to be removal type for valve handling | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | HV-1210025 | 20150C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | SWL of the padeye needs to confirm with latest valve weight. Swing direction with load to be confirm by STR. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09A/B/C/D/E/F |  | HV-1223063 | 20151C | 21/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Instrumentation needs to relocation from the piping flange | 8/1/26 - AST-CH4-M09A-301-005 is a F&G devices and not Instrument item. This is to be resolve by Safety. | None | SAF | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | AST-CH4-M09A-301-005 | 20152C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Instrument to be relocated away for valve removal | None | None | SAF | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | HV-1210050 | 20153C |  |  |  | PB - Operation | None |  | None | None
3 | MH volume position to be corrected to valve position | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | VALV-12100277 | 20154C | 21/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Instrument needs to move away from the valve | None | None | SAF | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | VALV-12100277 | 20155C |  |  |  | PB - Operation | None |  | None | None
3 | STR need to update the handrails to removable type. In the selection tree, the naming is without the "removable" word | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | Copy of OFHR-M09B-0000001 | 20156C | 08/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Hose saddle to be removal type. When doing lifting activity with the monorail, there will be more space. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | M09A-L3-US-0003-HS | 20157C | 09/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Instrument needs to move away from the handling volume | None | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | SPI-M09A-325 SPI-M09A-314 | 20158C |  |  |  | PB - Operation | None |  | None | None
4 | Handling to be provided for these heavy valves listed in the tags. In the DR90 discussion, to reduce weight impact, operation prefer to use scaffold since it is impacted to 3 valves. M09A: VALV-12100354 and VALV-12101169. M09F: VALV-12101215 | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | M09A VALV-12100354 , VALV-12101169 M09F VALV-12101215 | 20159C | 21/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Instrument items to be moved away from the FE, considering FE removal | None | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-09B |  | CXE-L-M09B-360 AST-CH4-M09B-201-005 | 20160C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Removable type handrail to be provided | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-09B |  | Copy of OFHR-M09B-0000001 OFHR-M09B-0000002 | 20161C | 09/03/2026 |  |  | PB - Operation | None |  | None | None
2 | Handling volume size to be increased to cover the space and kept clear of interference | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09B |  | Copy of SPI-M09B-329 HV-1223001L HV-1223061 | 20162C | 21/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Handling path to be updated into temporary structure and travel towards starboard side. Turn radius to be modeled. Instrument to be relocated if required based on handling volume | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09B |  | VALV-12440017 | 20163C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
5 | After update of swing volume (ref punch 20165c) Lighting fixture and instrumentation stands to be moved clear of davit lifting area. Handrails to be made removable type. | None | None | ELE | OPEN |  | None |  | None | None | HAND | None | None | M-09B/C/D/F |  | LEM-333-06-M09B-005 SPP-M09B-00019 SPI-M09B-509 Copy of OFHR-M09B-0000129 | 20164C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Swing volume to be updated as per vendor details and intended swing direction. There is no tilting of jib arm during operation. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09B/C/D/F |  | PE-M09B-5001- 5 TON | 20165C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
5 | All davit tag numbers to be updated correctly to indicate permanent/removable/portable type | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | GEN/M-09 |  | PE-M09B-5001- 5 TON | 20166C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Instrument stand to be relocated or made removable type to clear access to valve | None | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-09C |  | VALV-12101465 SPI-M09C-303 | 20167C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve transfer volume to be provided | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09C/D/E |  | SDV-1223056-1 | 20168C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handling drop volume size to be increased to structure edge. Piping and cable trays to be rerouted away from drop volume. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09B/C/D |  | MR-M09C-4001 MR-M09D-4001 MR-M09E-4001 | 20169C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Handling path SWL needs to be updated in the arrangement drawing. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09B/C |  | None | 20171C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Area to be kept clear for FE removal | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09D |  | FE-1210001V FE-1210001U FE-1210001T | 20172C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Removable handrail to be provided | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-09D |  | OFHR-M09D-0000049 | 20173C | 09/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Drop zone volume to be updated as per valve dimensions and turning radius to be deleted | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09D |  | Copy of PERMANENT DAVIT - 5TONE - LEVEL 05 | 20174C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
5 | SDV Handling volume to be updated. Lighting fixture to be clear of handling operations. | None | None | ELE | OPEN |  | None |  | None | None | HAND | None | None | M-09D |  | BDV-1231088 | 20175C | 12/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Instrument needs to relocated away from FE handling.FE-1210003U, FE-1210003W, FE-1210003V, VALV-12520168. | 17/12/26 - F&G devices is a Safety item and need to be resolve by Safety discipline. | None | SAF | OPEN |  | None |  | None | None | HAND | None | None | M-09E |  | Z-5428206 AST-CH4-M09E-201-001 AST-CH4-M09E-201-002 Z-5428205 AST-CH4-M09E-201-004 | 20176C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Handrail to be removal type | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-09E |  | OFHR-M09E-0000002 OFHR-M09E-0000004 OFHR-M09F-0000001 | 20177C | 09/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Handling volume to be model and instrument need to relocate. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09E |  | SPI-M09E-315 HV-1223001H HV-1223001J | 20178C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Instrument needs to relocate away from the valve | 8/1/26 - AST-CO2-M09E-301-007 & AST-CO2-M09E-301-006 is a F&G items and need to be resolve by SAFETY & not instrument. | None | SAF | OPEN |  | None |  | None | None | HAND | None | None | M-09E |  | AST-CO2-M09E-301-007 AST-CO2-M09E-301-006 | 20179C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Instrument needs to relocate away from the valve | 17/12/25 - F&G device is a Safety item and need to be resolve b Safety discipline. | None | SAF | OPEN |  | None |  | None | None | HAND | None | None | M-09E |  | AST-CO2-M09E-401-006 AST-H2S-M09E-401-005 AST-CH4-M09E-401-006 AST-CO2-M09E-401-005 | 20180C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Instrument needs to relocate away from the valve | 17/12/25 - F&G device is a Safety item and need to be resolve by Safety discipline | None | SAF | OPEN |  | None |  | None | None | HAND | None | None | M-09E |  | AST-CO2-M09E-401-007 | 20181C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Escape route and handling path is clashing with coaming. Coaming needs to clear/modify | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09E |  | BM-FB 200x8-0050707 | 20182C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Platform extension is still in the study model. Structure need to do detail model and handrails need to be removable type. | Framing of platform extension is shown in Drawing No. I-DE-3010.2S-1419-140-S2N-221 Sheet 9. | KBR | STR | Pending Seatrium Reply |  | None |  | None | None | STR | None | None | M-09E |  | VALV-12310475 | 20183C | 09/03/2026 |  |  | PB - Operation | None |  | None | None
5 | Davit need to optimise for shortest jib length, can consider with 2 padeyes. Height of jib is not sufficient high for the valve to lift over the pipe. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09E |  | PE-M09E-5001- 5 TON | 20184C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Instrument needs to relocate away from the FE | 17/12/25 - F&G device is a Safety item and need to be resole by Safety discipline. | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-09F |  | AST-CO2-M09F-201-003 | 20185C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Handling path and turning radius needs to update and clear the coaming clash. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09F |  | None | 20186C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Instrument need to move away from the valve for valve handling | 17/12/25 - F&G device is a Safety item and to be resolve by Safety discipline. | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-09F |  | AST-CH4-M09F-401-006 | 20187C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Handling transport route to confirm if the width is sufficient. Handling volume need to done for BDV valve scaffolding. if transport width is insufficient, alternative handling method such as davit to handle this BDV. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09F |  | BDV-1252003 | 20188C | 10/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Pig launcher handling volume to be model. Instrument panel to be relocated away for pig launcher handling. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-09A |  | JBC-1419-004 JBC-1419-002 JBC-1419-001 | 20189C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Pig launcher handling volume to be model. Instrument panel to be relocated away for pig launcher handling. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-09E |  | JBI-1419-401 AST-CH4-M09E-401-002 AST-CO2-M09E-401-003 PG-1244004K | 20190C | 27/02/2026 |  |  | PB - Operation | None |  | None | None
4 | To place the A-frame in the correct position, handling volume, pig trolley rotation volume for pig launcher handling. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-09A/B/C/D/E/F |  | None | 20191C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipe support clashing against monorail transport volume of gearbox. Applicable to both M-07A/B | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | None | 20192C | 02/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Access path clash with pipe support to be cleared. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | SP-M07A-05784 | 20193C | 03/02/2026 |  |  | PB - Operation | None |  | None | None
1 | 1.Vendor cable tray to be shifted/ made removable type to move the main plate til the end. (Typical for all 3 trains). 2. Clear pipe &amp; cable tray clash. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | UC-1231002A UC-1231002B UC-1231001A | 20194C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Additional flanges to be added to make spool removable, to facilitate handling | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | None | 20195C | 03/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Bundle dimensions to be updated as per vendor data. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | UC-1231002A/B/C/D UC-1231001A/B | 20196C | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Provide removable flange for sprinkler as marked. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | 2&quot;-FW-B7-1271-NI 2&quot;-FW-B7-1272-NI | 20197C | 03/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Model scaffolding for heat exchanger plating handling. Applicable for both M-07A/B | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | UC-1231002B | 20198C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Relocate the camera, clashing with bundle removable volume. | None | KBR | TEL | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | CAM-5514026 | 20199C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
1 | 1. Bundle volume to be shifted inline with the handling path. 2. Speaker is to close to the bundle transportation path. 3. Emergency light to be relocated away from transportation. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | COR-5518105A LSE-5518014A | 20200C |  |  |  | PB - Operation | None |  | None | None
1 | Bundle handling simulation using Deck trolley to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | None | 20201C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | KBR to provide philosophy on mechanical handling for internal part of the scrubber.(Typical for all scrubbers in all both M-07A/B). | Please check this document I-PR-3010.2S-1200-540-HM9-001 | None | MECH | Pending PB Reply | 06/01/2026 | None |  | None | 08.01.26_B0RG_CLOSE | HAND | None | None | M-07A/B |  | None | 20202C | 29/01/2026 | 2.00000000000000 |  | PB - Operation | True | 09/01/2026 | True | None | 09/01/2026 |  | 11/01/2026 | 11/01/2026 |  | 11/01/2026
1 | Provide area block infront of the valve as per mark up. Provide break up flange for the sprinkler line as per mark up. For both M-07A/B | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | None | 20203C | 03/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Provide obstruction volumes 1 meter height for valve in the selected area. For both M-07A/B. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | None | 20204C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Piping to move and clear clash with handling path. Both M07A/B | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | None | 20205C | 03/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Handling obstruction volume to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | None | 20206C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Provide filter maintenance volume. Applicable to both M-07A/B. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | None | 20207C | 03/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Handling of the 8 valve need to be re-checked. Switch between A-Frame to Beam clamp is not advisable. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | M07A HV-1231001 VALV-12310316 HV-1231076 VALV-12310320 M07B: HV-1231078 VAULT-12311292 VAULT-12311271 HV-1231082 | 20208C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | 1. Provide padeye obstruction volume. 2. Provide the padeye on the pipe support. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | VALV-12310400 (M07A) VALV-12311253 (M07B) | 20209C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Valve handling to be re-checked. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | SDV-1231036A-1 (M07A) SDV-1231036B-1 (M07A) SDV-1231036D-1 (M07B) SDV-1231036C-1 (M07B) | 20210C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Provide handling obstruction volume. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | None | 20211C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | 1. Shift the sensor to clear handling path clash. 2. Rotate the pipe tapping towards PORT direction. | None | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | None | 20212C |  |  |  | PB - Operation | None |  | None | None
2 | Shift the instrument items to access the valve. | None | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | SDV-1252009A-2 | 20213C | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | 1.Obstruction volume to be updated. 2. padeye position to be checked. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | VALV-12520052 VALV-12520925 | 20214C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | 1.Shift the instrument item to clear space for placing A-Frame. 2. Show handling towards STARTBOARD direction. | None | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | VALV-12310459 | 20215C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | All IGC Compressor tie-ins to be fixed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | 1&quot;-OL-B3-0121-PP 6&quot;-OL-B3-0122-PP 1/2&quot;-DFC-B9-1840-NI 4&quot;-F-B3N-1694-NI 1-1/2&quot;-PC-J12N-2521-ET 4&quot;-F-B3N-1693-NI | 0938c | 19/01/2026 |  |  | PB - Operation | None |  | None | None
1 | High point vent to be provided on the water line for lube oil coolers and working oil coolers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | 4&quot;-W-B10-3196-NI 4&quot;-W-B10-3199-NI 4&quot;-W-B10-3192-NI 4&quot;-W-B10-3193-NI 4&quot;-W-B10-3189-NI | 0939c | 19/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Missing and not connected lines to be completed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | 2&quot;-F-J12N-1699-PP 4&quot;-F-B3N-1698-NI 2&quot;-PC-J12N-2749-PP 2&quot;-PC-H40N-2520-PP | 0940c | 19/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Handrail to be modified for valve operation | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | PultrudedHandrail_E5-7-3619 | 0941c | 19/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipe penetration on access platforms to be modelled for all compressor access platforms | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | None | 0942c | 19/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Adjust the routing of the line in Injection package to improve valve accessibility | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | UC-1252001A | 0943c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve handwheel in Injection package orientation to face upward | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | UC-1252001A | 0944c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Valves in Injection package inside skid are not reachable. To be modified to be reachable from outside skid. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | UC-1252001A | 0945c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve lever in Injection package is not accessible. Modify orientation of the valve to provide access to the lever | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M07A/B |  | UC-1252001A | 0946c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Utility connection to be moved to downstream of the valve and to be within the coamed area | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | VALV-12521341 | 0947c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Small pockets on coaming on the aft side to be avoided due to water accumulation | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | COAMING_FT-P-UC-1252001A | 0948c | 04/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Utility connection piping to be as short as possible for both Filters | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | FT-P-UC-1252001A | 0949c | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Line to be modified to be as short as possible, vent with flange and blind to add at the tapping point | None | None | PIP | OPEN |  | None |  | None | None | INST | None | None | M07A/B |  | P-1839-N6 | 0950c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Check to see if spade and filter can be sandwiched in order to avoid need for the second removable spool | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | P-0721 | 0951c | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | N5 Vent connection to be modeled | None | None | PIP | OPEN |  | None |  | None | None | ELE | None | None | M07A/B |  | P-UC-1252001A | 0952c | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Instrument gauge stand in Export Package to be relocated toward handrail and rotated toward motor to provide more space for access | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | CSE | None | None | M07A/B |  | UC-1231002A | 0953c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Missing sampling points and PITs to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | ESP-12310512 PIT-1252009A PDIT-1233005 | 0954c | 20/01/2026 |  |  | SEA/KBR | None |  | None | None
4 | TIT is to be deleted as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | TIT-1252045A | 0955c | 20/01/2026 |  |  | PB - Operation | None |  | None | None
5 | BDV to FO should be sloping down towards FO, same for XV | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | P-0349 | 0956c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | High point vent to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | PC-0306 | 0957c | 20/01/2026 |  |  | SEA/KBR | None |  | None | None
3 | Tubing tie-ins to be routed and clear of access way | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07A |  | PN-UH-5139007A | 0958c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Pipe spec in the model is G3N. To be changed to H40N as per P&ID. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | PC-2520 | 0959c | 21/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Check with Instruments on correct orientation of the PIT | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | PIT-1231004B | 0960c | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Quarter pipe with coaming to be provided where coaming crosses escape route | Quarter cut pipe added in escape route | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | SAF | None | None | M07A |  | None | 0961c | 22/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
2 | Soft volume of escape route to match the route | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | LEVEL-2-5-4689 | 0962c | 04/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Access to ladder to be evaluated | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | OFLD-M07A-0000009 | 0963c | 04/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Extinguisher support to be updated. Extinguisher to be moved as close as possible to escape route. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5428138 | 0964c | 04/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Extinguisher to be relocated as marked | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5428139 | 0965c | 04/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Equipment support to be modeled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5434019 | 0966c | 04/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Equipment support to be modeled. Door opening to be modeled. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5434103 | 0967c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Equipment support to be modeled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5428142 | 0968c | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Pipe support to be relocated behind hydrant | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | H-5423052 | 0969c | 21/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | Access to hydrant is obstructed by lighting junction box | Light Fixture location updated. | None | ELE | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | CXE-L-M07A-311 H-5423053 | 0970c | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Equipment support to be modeled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5434021 | 0971c | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Support member to be deleted | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | SS-M07A-0098164 | 0972c | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Equipment support to be updated | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5428150 | 0973c | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Equipment support to be updated | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5434022 | 0974c | 05/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Pipe support to be relocated behind hydrant | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | H-5423056 | 0975c | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
5 | Pipe support modeling to be fixed | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5428432 SP-M07A-05951 | 0976c | 08/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Equipment support to be updated. Pipe support modeling to be fixed. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-5434023 SP-M07A-11221 | 0977c | 08/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Equipment to be relocated out of escape route | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | Z-H-5423056 | 0978c | 08/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Handrail to be updated considering bracing is temporary | Handrail gap updated | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | SAF | None | None | M07A |  | OFHR-M07A-0000111 | 0979c | 22/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Engineering | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Cage height from deck to be 2.1m as per standard | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | OFLD-M07A-0000009 | 0980c | 19/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Gap between handrails to be minimised as per standard detail - typical 75mm, max 125mm. Typical for module M07A/B handrails. | Handrail gap updated | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | SAF | None | None | M07A/B |  | None | 0981c | 22/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Engineering | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Ladder cage height from deck to be 2m (for ladders not in escape routes). Cage height to be extended to top of ladder. Fall arrestor to be provided for ladders of 5m or higher. Typical for all vessels. | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M07A/B |  | V-UC-1252001-A-LADDER-1 | 0982c | 19/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Cable tray is too close to ladder | None | None | CSE | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | IC-M07A-S-I-TRAY-01015 | 0983c |  |  |  | PB - Engineering | None |  | None | None
1 | Cable tray to be relocated to avoid obstructing the ladder access | None | None | ELE | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | EC-M07A-L-E-TRAY-10520-TRAY-0001 | 0984c | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Cross over platform to be modelled as per standard with handrails | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | None | 0985c | 19/01/2026 |  |  | PB - Engineering | None |  | None | None
PPRK | Commissioning to provide the locations of the spool split as per P&ID I-DE-3010.2S-5124-944-S2N-003 Note 9 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | 10"-W-B10-0311-NI | 0986c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Ensure PDV-5124012 is above all the consumers as per P&amp;ID Note 1. Add high point vent. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | PDV-5124012 | 0987c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | PDV-51240005 to be above all the consumers as per P&ID Note 1. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | PDV-51240005 | 0988c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | High point vents to be added | High point vents are modelled | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | dcn required | PPRK |  | HWP-0100 HWP-0103 | 0989c | 23/01/2026 | 1.00000000000000 | 0 | SEA/KBR | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
PPRK | Missing valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | VALV-51250611 VALV-51250602 VALV-51250616 | 0990c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Distance between the two corrosion coupons to be verified with process whether 500mm mentioned on P&ID is minimum distance | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | HWP-0100 | 0991c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Ensure no pocket requirement is met for this line (maintain 2% slope to counter the vessel trim slope from AFT-FWD) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | PC-0730 | 0992c | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Ensure no pocket requirement is met for this line (maintain 2% slope to counter the vessel trim slope from AFT-FWD). Check with process to add low point drain. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | PC-0160 | 0993c | 21/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Slope requirement is not met on piperack. Process to verify the slope requirement and check to provide a low point drain suitably | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | PC-0310 | 0994c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | High point vent to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | P-0379 | 0995c | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
PPRK | Purge line is not modeled | F-0875 purge line is modelled | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | no pping dcn required | PPRK |  | 1"-F-B3N-0875-NI | 0996c |  | 1.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 25/12/2025
PPRK | High point vent to be flanged for FG header, loops and tappings. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | FG-0016 | 0997c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Low point drain to be modelled at the expansion loops and aft end | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | FG-0119 | 0998c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | FG-0119 VALV-51350647 VALV-51350646 VALV-51350645 | 0999c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Low point drain to be added | Low point drain modelled | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | no piping dcn required | PPRK |  | FG-0037 | 1000c |  | 1.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 25/12/2025
PPRK | Verify to make the loop from 3D to 2D or add low point drain | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | FG-0038 | 1001c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Low point drain of at least 3" to be added for draining sediment. Space to be reserved for connecting hose. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | PCW-0034 | 1002c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Tubing tie in points to be modelled from M14 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1003c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | VALV-51330125 | 1004c | 21/01/2026 |  |  | PB - Operation | None |  | None | None
None | Valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M12/13/13B |  | VALV-51330022 VALV-51330241 VALV-51330244 VALV-51330430 | 1005c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
None | Valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M16 |  | VALV-51330185 VALV-51330360 | 1006c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Drain pit to be added for the diesel line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | None | 1007c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Valve to be closer to the edge of M13B | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | VALV-51150218 | 1008c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Lines to be modelled and add high point vents. Connection points with CIP equipment to be modelled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | 2&quot;-CNI-B3-2463-NI 2&quot;-CNI-B3-2440-NI | 1009c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Piping to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | DW-0020 | 1010c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Piping to be connected | Disconnected line is connected. | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | no piping dcn required | PPRK |  | SW-1261+[@[S3D Item Tags]] | 1011c |  | 1.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 25/12/2025
PPRK | Piping to be modeled | Disconnected lines connected | KBR | PIP | Pending PB Reply | 22/12/2025 | None |  | None | None | PIP | None | no piping dcn required | PPRK |  | WB-3682WB WB-3751 | 1012c |  | 1.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 25/12/2025
PPRK | Piping to be connected | Line is connected | KBR | PIP | RE-OPEN | 22/12/2025 | None |  | None | None | PIP | None | no piping dcn reuired | PPRK |  | CI2-0002 | 1013c |  | 1.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 25/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 25/12/2025
PPRK | Piping to be modelled and connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | PPRK |  | D-0474 | 1014c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Escape route height to be 2.1m on top deck of M13B Piperack | Escape route at 2.1m height now. | KBR | PIP | Pending Seatrium Reply | 29/12/2025 | None |  | None | None | SAF | None | None | M13B |  | None | 1015c |  | 9.00000000000000 |  | PB - Operation | None |  | None | None | 01/01/2026 |  |  |  |  | 01/01/2026
PPRK | Gap between handrails to be minimised as per standard detail - typical 75mm, max 125mm. Typical for module M13B handrails on top of Piperack. | Handrails on top of M13B piperack have been modelled and checked having 125mm center to center (75 clear) gap per standard detail | KBR | STR | RE-OPEN | 18/12/2025 | None |  | None | None | STR | None | None | M-13B |  | None | 1016c | 11/02/2026 | 5.00000000000000 | 15.0000000000000 | PB - Operation | None |  | None | None | 21/12/2025 | 26/12/2025 | 28/12/2025 | 28/12/2025 | 28/12/2025 | 21/12/2025
PPRK | Kickplates to be modelled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M16 |  | None | 1017c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Evaluate the requirement for kickplate - portside and starboard side | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M16 |  | None | 1018c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Safety plan to be updated to match modelled escape routes | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | None | 1019c |  |  |  | PB - Operation | None |  | None | None
PPRK | Kickplates to be modelled at M02 and M07 intersection | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-02 |  | None | 1020c | 15/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Safety plan drawing to be updated to match equipment locations | 8 Jan 2026: The location of Z-5428031 and Z-H-5423014 is consistent in M02 Safety Plan I-DE-3010.2S-5400-947-S2N-052_A and 3D model. | None | SAF | Pending Seatrium Reply | 07/01/2026 | None |  | None | None | SAF | None | None | M-02 |  | Z-5428031 Z-H-5423014 | 1021c |  | 0 |  | PB - Operation | None |  | None | None | 10/01/2026 |  |  |  |  | 11/01/2026
1 | Quarter pipe with coaming to be provided where coaming crosses escape route | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1022c | 11/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Coaming creating trip hazard within escape route. Escape route can be modified to avoid coaming. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1023c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Pipe support to be located behind hydrant - typical for M14 hydrants | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1024c | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Evaluate location of the JB box and the extinguisher to avoid hindrance while accessing the extinguisher | None | None | CSE | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | CXE-L-M14-302 | 1025c |  |  |  | PB - Engineering | None |  | None | None
1 | Extinguisher operating volume to be modeled - typical for M14 | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1026c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Floor marking for the hydrant to be modeled - typical for M14 | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1027c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Safety shower volume to be modeled - typical for M14 | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1028c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Gaps in coaming to be filled. Typical for module M14. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1029c | 11/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Gap between handrails to be minimised as per standard detail - typical 75mm, max 125mm. Typical for module M14. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1030c | 15/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Tray routing to be modified in order to avoid obstruction while operating the ladder | None | None | ELE | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1031c | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Hydrant operating volume to be clear of obstruction | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1032c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
2 | Escape route is not required here as per Safety Plan drawing | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1033c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
2 | Obstruction of quarter pipe to extinguisher operating area to be evaluated | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1034c | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | Evaluate location of the JB box and the extinguisher to avoid hindrance while accessing the extinguisher | None | None | CSE | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | None | 1035c |  |  |  | PB - Engineering | None |  | None | None
2 | Piping to safety shower to be connected | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1036c | 16/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | Secondary escape routes to be 1m width - typical for all levels | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1037c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
2 | Kickplates or coaming to be provided at gaps - typical punch for Level 2 | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1038c | 15/02/2026 |  |  | PB - Engineering | None |  | None | None
2 | Coaming plate to be modeled at all missing locations | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1039c | 15/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Hydrant operating volume to be modelled - typical for M14 hydrants | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1040c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Hydrant pipe supports to be modelled - typical for all locations | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1041c | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | Hydrant to be moved toward STB side for better accessibility | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1042c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Wheeled type extinguisher to be relocated. Operating volume to be modeled for wheeled type extinguisher - typical for wheeled type extinguisher | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1043c | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | Safety layout drawing to be updated as per 3D model | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | None | 1044c |  |  |  | PB - Engineering | None |  | None | None
3 | Exinguisher location to be modified to clear the coaming trip hazard. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1045c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Kickplate to be provided | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1046c | 15/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Handrail to be provided at the bracings | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1047c | 15/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Cage height from deck to be 2m or 2.1m for ladder in escape routes. Typical punch for M14 ladders. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1048c | 15/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Requirement for 200mm between centre of ladder rung and tank body. Coaming to be modified based on ladder relocation, to increase the gap from coaming to the tank . Typical for all locations. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1049c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Coaming plate inclination to be updated | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1050c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Kickplate to be provided - typical at all applicable locations in M14 | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1051c | 16/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Escape route is not required here as per Safety Plan drawing | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1052c | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Hydrant block valve to oriented behind hydrant - typical punch for all M14 hydrants | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | None | 1053c | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
None | Escape route to be updated as per Safety Layout | None | None | PIP | OPEN | 16/01/2026 | None |  | None | None | SAF | None | None | M15 |  | None | 1054c | 06/02/2026 | -9.00000000000000 |  | PB - Engineering | None |  | None | None | 19/01/2026 |  |  |  |  | 19/01/2026
1 | Ensure the design for pump suction is updated based on Note 16 on P&ID I-DE-3010.2S-1251-944-S2N-001 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1055c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model the maintenance volume and portable access platform for accessing the strainers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1056c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain valve to be moved to downstream of strainer or on the strainer and consider as HPV for the suction line as per P&ID Note - "18 EACH PUMP SHALL HAVE 2 VENTS, ONE LOCATED ON PUMP VOLUTE AND THE OTHER LOCATED ON THE HIGHEST POINT BEFORE THE PUMP" | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1057c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Casing vent valve to be modelled, P&ID to be verified accordingly. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1058c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Sampling connection to be modeled - typical punch for M14 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1059c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Relocate the drain valve on the upstream of the block valve. Typical for both pump discharge lines. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | VALV-12510434 VALV-12510437 | 1060c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check possibility to rotate the push button towards AFT side for both pumps | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M-14 |  | None | 1061c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | The removable spool ESP tag as per P&ID to be updated in 3D model. Typical for all pumps. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1062c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain valve shall be provided downstream of the check valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1063c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | 1. Enlarge the area of coaming covering the strainer flange. 2. Check the possibility to route the drain valve to the coaming. 3. Process to check the impact on open drain line size. Typical for all the pumps. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1064c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure to have the necessary clearance between the handwheel and the header piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1065c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check possibility to rotate the push button towards AFT side for both pumps | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M-14 |  | None | 1066c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Update the drain to vent | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1067c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | 1. Evaluate the accessibility of the platform while the filter davit is opened especially when the operator is on the platform. 2. Ensure the davit opening considers the handwheel and verify if clashing with structural beam. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1068c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | In order to benefit the filter cleaning on mezz deck, increase the coaming area on Level 1 provided for the filter. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1069c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | TQF to be raised for the connecting location of sampling point | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | ESP-12630115 ESP-12630108 ESP-12630111 ESP-12630104 ESP-12620117 ESP-12620118 ESP-12620111 ESP-12620104 ESP-12620107 ESP-12610180 ESP-12610152 ESP-12610148 ESP-12510207 ESP-12610162 ESP-12610168 ESP-12610171 ESP-12610114 ESP-12610118 ESP-12610128 ESP-12610131 ESP-12610139 ESP-12610140 ESP-12610144 ESP-12610108 ESP-12610104 ESP-12610122 ESP-12610175 ESP-12620122 ESP-12620126 ESP-12630120 ESP-12610159 | 1070c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Verify the tapping connection details for XE-5124001/XW-5124001 and XE-5124002/XW-5124002 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | XE-5124001/XW-5124001 XE-5124002/XW-5124002 | 1071c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | 1. Enlarge the area of coaming covering the strainer flange. 2. Update the MH volume for the strainer. 3. Check the possibility to route the drain valve within the coaming. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1072c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check possibility to rotate the push button towards FWD side | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M-14 |  | None | 1073c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Verify if the removable spool can have instrument connections - typical for all pumps. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1074c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | The instrument header line as per P&ID to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1075c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Verify the size (1.5") of the valve connection provided for CW Non-Classified suction header against the size (3") provided for CW classified area suction piping in line with P&ID 5124-001 & 002 Note 3. | The provided valve are for dual purpose (drain & filling) as per Note 5 & 3 (as per P&ID 5124-001 & 002). Hence the indicated sizes are correct and to be retained. | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M14 |  | None | 1076c |  | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
3 | Ensure all the lines associated with pump skid Tie-in Points are updated in the model | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1077c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Hot water supply lines to be modelled for the sampling lines as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1078c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Ensure to model the penetration details for the tubing penetrating at deck level | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1079c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Ensure the lines from the TOTE tank to the CI tank especially the gravity flow is addressed considering the flow from AFT to FWD (especially the lines in P&ID 6825-001). The slope shall be considered towards FWD. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | 2&quot;-CNI-B3-1377-NI 2&quot;-CNI-B3-0932-NI 2&quot;-CNI-B3-0321-NI 2&quot;-CNI-B3-0315-NI 2&quot;-CNI-B3-1814-NI 2&quot;-CNI-B3-1362-NI 2&quot;-CNI-B3-0326-NI 2&quot;-CNI-B3-0331-NI | 1080c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Considering the gravity flow, supply from point A to point B would not be achievable. Ensure to verify the design with proper flow of chemical wrt the tank being used for filling. Ensure to avoid pocket in the line and consider slope if line is routed toward FWD. Comment typical at all applicable locations. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | 2&quot;-CNI-B3-2397-NI 2&quot;-CNI-B3-0321-NI 2&quot;-CNI-B3-0319-NI 2&quot;-CNI-B3-2444-NI 2&quot;-CNI-B3-2565-NI 2&quot;-CNI-B3-1814-NI 2&quot;-CNI-B3-2607-NI 2&quot;-CNI-B3-0389-NI 2&quot;-CNI-B3-0326-NI 2&quot;-CNI-B3-2796-NI 2&quot;-CNI-B3-0331-NI 2&quot;-CNI-B3-2890-NI 2&quot;-CNI-B3-0316-NI 2&quot;-CNI-B3-2954-NI | 1081c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Safety to evaluate if the handrail can be modified so the valves can be easily accesible from AFT side closer to the step to the crossover platform. Maintain min 500mm path width from the valves | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1082c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Verify if the crossover platform can be changed to step kind arrangement. If not possible, ensure the current step over platform are provided with necessary guards during usage. | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M-14 |  | None | 1083c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 | The tundish size to be standardised and to consider the max size applicable to avoid spillage of chemicals. To be discussed internally between SOC & COC to have common design. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1084c | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | 1. Update the pipe routing as marked. The design requirement is, sampling line considering the sample of the chemical can be taken at the lowest level of chemical inside the tank. 2. The needle valve shall be updated and the clearance of 300mm shall be maintained for sample bottle usage. Comment is typical for all tank. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1085c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Ensure the valves are kept closer to the tank and are not suitable to be kept at this deck below TOTE tank. At the present location these valves are with pocket. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | VALV-12610173/74/75 | 1086c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
None | The lever operation is difficult. Relocate the valve away from the support structure and ensure proper access to the valves. Position the valve at 45deg is also acceptable. Necessary note for the valve lever orientation shall be taken care in the isometrics. Comment is applicable for all locations. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1087c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | The line is associated with different chemicals. The termination of the chemical shall be updated by locating the spectacle blind and valve near to the TEE as marked. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | 2&quot;-CNI-B3-0387-NI 2&quot;-CNI-B3-1423-NI 2&quot;-CNI-B3-3119-NI | 1088c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Complete the piping for line as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | 2"-CNI-B3-2337-NI | 1089c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Structural arrangement to be provided to hold the hose at all locations of TOTE tank arrangement. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1090c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | Line routing to be completed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | 2"-CNI-B3-0318-NI | 1091c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Considering the line size change for most of the CI Tanks, confirm if in case the vent is located closer to the crane access area. Safety shall eNsure and validate the final pipe routing if routed near to the crane access area. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1092c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | 1. All the tube routing design shall be completed with proper tube support as well as tube tray including support. 2. There shall be union considered for every 6m | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1093c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Evaluate the relocation of the drain box by interchanging with the JB. Modify the coaming plate to avoid dead end at the AFT-STB corner. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1094c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | Vendor to verify the upstream pipe of the bumpers as there is no possibility to vent. The bumpers are located too high. | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M-14 |  | None | 1095c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | The details in the model to be updated as per latest PID. There are missing valves to be modelled, and the flame arrestors to be deleted. The line modelling shall be completed. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | None | 1096c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Quarter pipe direction should match direction of escape route | Quater cut pipe updated based on direction of escape route. | None | PIP | RE-OPEN | 25/12/2025 | None |  | None | None | SAF | None | None | M-01 |  | None | 1097c | 29/12/2025 | 3.00000000000000 | 10.0000000000000 | PB - Engineering | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Quarter pipe direction should match direction of escape route | Quater cut pipe direction updated based on the escape route direction | KBR | STR | Pending PB Reply | 25/12/2025 | None |  | None | None | SAF | None | None | M-01 |  | None | 1098c | 29/12/2025 | 3.00000000000000 | 10.0000000000000 | PB - Engineering | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Coaming to be shortened to finish at gutter | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | None | 1099c | 19/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Handling route to be moved AFT side to be clear of extinguisher | MH Reply: 13/12/2025 1.Turning radius clash with extinguisher is cleared. | None | HAND | Pending Seatrium Reply | 12/12/2025 | None |  | None | None | SAF | None | None | M-01 |  | None | 1100c | 20/01/2026 | 26.0000000000000 |  | PB - Engineering | None |  | None | None | 15/12/2025 |  |  |  |  | 15/12/2025
1 | Move safety equipment to provide space for UC | Z-5428004 safety equipment moved as marked | KBR | PIP | Pending Seatrium Reply | 23/12/2025 | None |  | None | None | PIP | None | None | M-01 |  | Z-5428004 | 1101c | 16/01/2026 | 15.0000000000000 |  | PB - Engineering | None |  | None | None | 26/12/2025 |  |  |  |  | 28/12/2025
1 | Safety shower piping to be modeled - typical for M01 Safety Showers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | Z-5434331 | 1102c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Ladder rungs above top of safety cage to be removed or cage height to be increased to top of ladder | Ladder updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | STR | None | None | M-01 |  | None | 1103c | 11/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Engineering | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
1 | Coaming to be behind ladder area | 18Dec25 : Coaming Updated | PB | STR | Pending PB Reply | 17/12/2025 | None |  | None | None | SAF | None | None | M-01 |  | None | 1104c | 23/12/2025 | 11.0000000000000 | 10.0000000000000 | PB - Engineering | None |  | None | None | 20/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 21/12/2025
1 | Clear space required behind ladder as per standard detail - typical for all M01 ladders | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | None | 1105c | 21/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Cage height from deck to be 2m or 2.1m for ladder in escape routes. Typical punch for M01 & FT ladders. | None | KBR | STR | RE-OPEN | 30/12/2025 | None |  | None | None | STR | None | None | M-01 |  | None | 1106c | 11/12/2025 | 2.00000000000000 | 6.00000000000000 | PB - Engineering | None |  | None | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
2 | Equipment supports to be updated as per standard detail | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | Z-H-5423003 Z-H-5423004 Z-H-5423007 | 1107c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
2 | Hydrant operating volume to be clear of obstruction | 09-01-25-Hydrant operating volume clash removed | None | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M-01 |  | H-5423004 | 1108c | 06/02/2026 | 0 |  | PB - Engineering | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
2 | Supporting of equipment to be completed | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | Z-5423008 | 1109c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
2 | Ladders to be modeled as per layout requirement | Ladder updated | KBR | STR | Pending PB Reply | 30/12/2025 | None |  | None | None | STR | None | None | M-01 |  | None | 1110c | 29/12/2025 | 2.00000000000000 | 6.00000000000000 | PB - Engineering | None |  | None | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
2 | Gap between handrails to be minimised as per standard detail - typical 75mm, max 125mm. Typical for module M01. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-01 |  | None | 1111c | 25/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | Safety bar to be provided on access platform ladders - typical punch for M01 | Safety bar updated | KBR | STR | RE-OPEN | 30/12/2025 | None |  | None | None | STR | None | None | M-01 |  | None | 1112c | 25/01/2026 | 2.00000000000000 | 6.00000000000000 | PB - Engineering | None |  | None | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
2 | Relocate the cable tray dropping point to provide ladder head clearance | None | None | ELE | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | KBRLadder_Right-7-0805 | 1113c | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Escape routes from vendor package to be updated on Safety Plan drawing | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | None | 1114c |  |  |  | PB - Engineering | None |  | None | None
3 | Quarter pipe direction should match direction of escape route | Quarter cut pipe direction changed | KBR | STR | RE-OPEN | 01/01/2026 | None |  | None | None | SAF | None | None | M-01 |  | None | 1115c | 11/12/2025 | 0 | 6.00000000000000 | PB - Engineering | None |  | None | None | 04/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | Connect the escape route to the ladder | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | None | 1116c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Escape route width to be updated to 1m | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | None | 1117c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Quarter pipe direction should match direction of escape route. Extinguisher operating space to be clear of quarter pipe. | Quater cut pipe updated | KBR | STR | Pending Seatrium Reply | 04/01/2026 | None |  | None | None | SAF | None | None | M-01 |  | Z-5428013 | 1118c | 06/01/2026 | 3.00000000000000 | 0 | PB - Engineering | None |  | None | None | 07/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 07/01/2026
3 | Fall arrestor to be modeled for ladder more than 5m height - typical for M01 ladders more than 5m | Fall arrestor modeled for ladders more than 5m height | KBR | STR | Pending Seatrium Reply | 04/01/2026 | None |  | None | None | STR | None | None | M-01 |  | None | 1119c | 08/01/2026 | 3.00000000000000 | 0 | PB - Engineering | None |  | None | None | 07/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 07/01/2026
3 | Handrail close to ladder, height to be extended as per standard detail | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-01 |  | None | 1120c | 11/01/2026 |  |  | PB - Engineering | None |  | None | None
4 | Escape route volumes to be modelled for ladders | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | None | 1121c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Escape route volume to be modelled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | None | 1122c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Evaluate to provide 1m clearance in front of extinguisher | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | Z-5428014 | 1123c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Handling route through hydrant to be resolved - check possibility to move hydrant (isometric issued) or modify handling route | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | H-5423007 | 1124c | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
4 | Extinguisher volume to be modelled 1.2m height - typical for M01 extinguishers | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | None | 1125c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
PPRK | Relocate the valves to other side to avoid operation requirement from starboard side with limited means of access | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | F-1765 F-1632 F-0725 | 1126c | 21/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Ladder support to be modelled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M07A |  | KBRLadder_Right-7-0818 | 1127c | 19/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Check package height above 600mm - handrail to be provided by vendor. Valve accessibility inside skid to be considered. Typical for both LP and HP skids. | None | None | STR | OPEN |  | None |  | None | None | MECH | None | None | M07A |  | None | 1128c | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
FT | 1. Check the requirement for hand grips at top of ladder access to Flare Tower and update model. Should be stainless steel as per deck shield structure. 2. Ladder modeling to be updated as per standard detail (Typical for Flare Tower ladders). | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | FLR |  | None | 1129c | 18/02/2026 |  |  | PB - Engineering | None |  | None | None
FT | Safety Bar to be provided on access platform ladders - typical punch for Flare Tower | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | FLR |  | None | 1130c | 18/02/2026 |  |  | PB - Engineering | None |  | None | None
FT | Support to be placed on beam and kickplate to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | FT |  | None | 1131c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Reserve volume for maintenance access to be modelled for TIT | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | TIT-5412005 | 1132c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Nozzle penetration to be modelled | Nozzle penetration modelled | KBR | STR | RE-OPEN | 31/12/2025 | None |  | None | None | STR | None | None | M-01 |  | V-5412001 | 1133c | 22/01/2026 | 1.00000000000000 | 6.00000000000000 | SEA/KBR | None |  | None | None | 03/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
1 | Block valve to be located as close as possible to vessel nozzle. PB confirms that these valves should change to category 3. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | VALV-54120072 VALV-54120101 VALV-54120077 VALV-54120107 VALV-54120019 VALV-54120016 VALV-54120008 | 1134c | 23/01/2026 |  |  | None | None |  | None | None
2 | Provide ladder to FE platform from LP platform and modify cable tray accordingly | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | None | 1135c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | To lift up the tie-in cable tray align with tray provided by Vendor (applied for all compressor). | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | IT-M07A-S-I-TRAY-01008-TRAY-0102 IT-M07A-S-I-TRAY-01017-TRAY-0114 | 10686C |  |  |  | SEA/KBR | None |  | None | None
Level 2 | The JB frame to be shifted to the West side and the penetration change to 3 side coaming. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | SPI-M07A-02012 SPI-M07A-02013 | 10687C |  |  |  | SEA/KBR | None |  | None | None
Level 3 | The JB frame to be shifted to the East side to reduce the number of trimmer | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | SPI-M07A-03001 SPI-M07A-03002 | 10688C |  |  |  | SEA/KBR | None |  | None | None
Level 4 | Moved back the JB frame and put on the primary beam, to avoid the two trimmer | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | SPI-M07A-04002 SPI-M07A-04003 | 10689C |  |  |  | SEA/KBR | None |  | None | None
Level 4 | JB to be moved back side and the penetration to be avoid sitting on the secondary beam. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | SPI-M07A-04009 | 10690C |  |  |  | SEA/KBR | None |  | None | None
General | All single JB supports need to be evaluated as the penetrations are overlapping with the support doubler plate. Please check the possibility of how to bolt this. Also, if possible, reduce the tray size to minimise the penetration | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | General | 10691C |  |  |  | SEA/KBR | None |  | None | None
Level 4 | 1. The cable tray below and on top of the penetration needs to be aligned. 2. One side plate of the penetration should be removed so that it can be attached to the coaming. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | SPI-M07A-04012 | 10692C |  |  |  | SEA/KBR | None |  | None | None
Level 2 | Vendor to update the 3D model showing the cable tray align with the Client tie-in point. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | VV-UC-1231002A | 10693C |  |  |  | SEA/KBR | None |  | None | None
None | 1. To model tray and penetration 2. To align interface between Vendor and KBR | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | PN-UH-5139007A(HCR-05)-Rev-B | 10694C |  |  |  | SEA/KBR | None |  | None | None
Level 3 | 1. The cable tray interface to be aligned with vendor penetration. 2. Vendor to provide dropper from JB up to the penetration/tie-in point. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | None | 10695C |  |  |  | SEA/KBR | None |  | None | None
None | To follow up with Vendor on the penetration cable - subject to received aster receive the I/O alignment for each control panel. Note: Changed from a &quot;Parking Lot&quot; to a Punch. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | None | 10696C |  |  |  | SEA/KBR | None |  | None | None
None | 1. KBR to provide cable tray connected to the vendor tie-in point. 2. Vendor to provide dropper and its penetration . 3. Vendor to provide wiring diagram for cable connection | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | None | 10697C |  |  |  | SEA/KBR | None |  | None | None
None | KBR to model and incorporate the necessary supports in accordance with the standard KBR typical drawings for all 90 deg cable ladder Bends(Typ). Wherever its missing. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07A |  | None | 10698C |  |  |  | SEA/KBR | None |  | None | None
Level 1 | Current lighting JB position has maintenance access issues (referring to equipment surrounding the area). Location to be resolved to ensure adequate maintenance space is available. | With all the possible options, The Lighting JB is mounted at 1600mm. (earlier it is 1300mm). | SEA | ELE | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | ELE | None | None | M07A |  | CXE-L-M07A-204 | 10699C |  | 5.00000000000000 |  | SEA/KBR | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
Level 1 | Lighting too close to valve resulting to maintenance issues. Resolve clearance issues between 2 equipment. | Light support arm length reduced and light fixture location updated to provide better access to valve | SEA | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 05-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M07A |  | LEM-328-01-M07A-007 | 10700C |  | 11.0000000000000 | 3.00000000000000 | SEA/KBR | True |  | None | None | 27/12/2025 | 07/01/2026 |  |  | 07/01/2026 | 28/12/2025
General | Ensure connectivity of sub-trays and lighting fixtures. Adequate glanding space to be provided | Sub trays provided and maintained sufficient space for Glanding. | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M07A |  | General | 10701C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Glanding and cable termination issue for light fixture. Beacon to be re-positioned not to block cable termination space for light. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07A |  | LSE-5518014A | 10702C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | To confirm why there are 2 Beacons: LSE-M07A-101-001 & LSE-5518014B | None | PB Ops | SAF | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | LSE-M07A-101-001 LSE-5518014B | 10703C |  |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate JB to an accessible position with no maintenance access obstruction. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M07A |  | CXE-L-M07A-207 CXE-L-M07A-309 CXN- L-M07A- 027 CXN-L-M07A-036 CXE-L-M07A-364 CXN-L-M07A-037 | 10704C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Multilevel | Relocate floodlight where there is no obstruction on illumination coverage. | Light Fixture location updated. | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M07A |  | LNO-214-06-M07A-004 | 10705C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Ensure tray is positioned based on glanding position of the light fixture. Trays to be adjusted accordingly considering cable coiling and cable entry position to fixture. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M07A |  | LNO-214-10-M07A-001 LNO-214-10-M07A-005 | 10706C | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Welding issues foreseen. Resolve using different type of mounting for floodlight. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M07A |  | LNO-214-10-M07A-004 | 10707C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Check maintainability of pole mounted lights. Relocated these lights as required, to ensure access/maintainability of equipment is provided. | Light fixtures location updated as per latest calculation. | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M07A |  | LES-301-12-M07A-002 | 10708C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
General | To check with IM the Telecom cable tray colour coding and reflect in 3D model. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | PPRK |  | General | 10709C | 29/01/2026 |  |  | PB - Engineering | None |  | None | None
General | All EIT cable trays in the Piperack shall maintain a minimum clearance of 80 mm between ladder-to-ladder, and a minimum clearance of 60 mm between tray and structural member. EIT Trays to follow same Pattern at each Frame. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | PPRK |  | General | 10710C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
General | All EIT cable trays in the Piperack shall maintain a minimum clearance of 80 mm between ladder-to-ladder, and a minimum clearance of 60 mm between tray and structural member. EIT Trays to follow same Pattern at each Frame. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | PPRK |  | General | 10711C |  |  |  | SEA/KBR | None |  | None | None
General | All EIT cable trays in the Piperack shall maintain a minimum clearance of 80 mm between ladder-to-ladder, and a minimum clearance of 60 mm between tray and structural member. EIT Trays to follow same Pattern at each Frame. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | PPRK |  | General | 10712C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
General | The structural two members located at the center shall be shifted towards the port side to provide sufficient clearance between Tray to structure. A minimum of 60 mm between the ladder and the structure is required to accommodate the hold-down clamp to secure the cable ladder. Applicable to all module except M-05B (M-05B already implemented). | None | SEA | STR | OPEN |  | None |  | None | None | STR | None | None | PPRK |  | General | 10713C | 18/02/2026 |  |  | SEA/KBR | None |  | None | None
M-13B | To inform and get agreement with PB on the 42mm gap between instrument cable trays - due to space constraint | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | PPRK |  | IT-M13-S-I-TRAY-04004 | 10714C |  |  |  | SEA/KBR | None |  | None | None
General | At cable ladder crossing locations, a minimum clearance of 100 mm shall be maintained between the two ladders when they belong to the same system. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | PPRK |  | General | 10715C |  |  |  | SEA/KBR | None |  | None | None
General | At cable ladder crossing locations, a minimum clearance of 100 mm shall be maintained between the two ladders when they belong to the same system. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | PPRK |  | General | 10716C | 27/01/2026 |  |  | SEA/KBR | None |  | None | None
General | Cable tray optimization shall be evaluated and implemented from AFT to FWD modules. A tray sizing report shall be provided, taking into account the current loading status, design growth percentage, and PB spare allowance 20%. If support not required - it can be removed. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | PPRK |  | General | 10717C | 27/01/2026 |  |  | SEA/KBR | None |  | None | None
General | Cable tray optimization shall be evaluated and implemented from AFT to FWD modules. A tray sizing report shall be provided, taking into account the current loading status, design growth percentage, and PB spare allowance 20%. If support not required - it can be removed. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | PPRK |  | General | 10718C |  |  |  | SEA/KBR | None |  | None | None
General | The expansion joint shown in the typical drawing does not match the one modeled in 3D. The 3D model shall be updated to match with the typical drawing | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | PPRK |  | General | 10719C |  |  |  | PB - Operation | None |  | None | None
M-16 | Instrument tray to maintain minimum segregation with HV cable trays. Instrument tray to be relocated/re-routed. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | PPRK |  | IC-M16-S-S-01003-TRAY-0011 | 10720C | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
General | HV tray and proposed cable routing bending have cable pulling issues. Resolve HV tray connections/droppers to horizontal piperack HV trays. Cable bending minimum requirement to be ensured compliant. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | PPRK |  | General for all tray all modules. For examples: ET-M14-H-TRAY-30000 ET-M14-M-TRAY-30000 ET-M02-H-TRAY-30000 ET-M07B-M-TRAY-01000 ET-M07B-M-TRAY-01000-TRAY-0203 | 10721C | 26/02/2026 |  |  | PB - Engineering | None |  | None | None
M-14 | LV tray connectivity issues. Provide proper connectivity of trays based on latest cable routing plan. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | PPRK |  | ET-M14-L-N-TRAY-01016 | 10722C | 26/02/2026 |  |  | PB - Engineering | None |  | None | None
M-14<br>M-15 | To resolve the clash between HV tray and structural stiffeners. (Structural stiffeners to explore reduction in size post lifting of module and trays to occupy the required space, or trays to consider re-sizing/reduction of tray.) | None | PB | STR | OPEN |  | None |  | None | None | STR | None | None | PPRK |  | ET-M14-H-TRAY-01000 ET-M15-H-TRAY-01000 | 10723C | 18/02/2026 |  |  | PB - Engineering | None |  | None | None
M-14<br>M-15 | Piping to ensure no flange connections on top of HV tray, or relocate the drain box away from tray top area. | None | SEA | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14/15 |  | ET-M14-H-TRAY-01000 ET-M15-H-TRAY-01000 | 10724C | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
M-15 | To correctly position the tray reducer based on tray dropper locations. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | PPRK |  | ET-M15-H-TRAY-01000 | 10725C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
General | Provide proper tray fitting between vertical cable tray branching out from horizontal piperack tray. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | PPRK |  | Check all modules. Example: ET-M10B-L-N-TRAY-0023 | 10726C | 26/02/2026 |  |  | PB - Engineering | None |  | None | None
General | Piperack tray supports modelled by STR discipline to remove the support members not used by EIT trays, based on EIT discipline input. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | PPRK |  | General | 10727C | 22/01/2026 |  |  | SEA/KBR | None |  | None | None
M-07A | Check the cables loaded to LV2 trays and optimize the tray size (reduce if possible). Close-out requires Electrical & Telecom input and confirmation. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | PPRK |  | ET-M07A-L-E-TRAY-01000 ET-M07A-L-E-TRAY-01001 ET-M07A-L-E-TRAY-01003 ET-M07A-L-E-TRAY-01004 | 10728C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
M-16 | Piperack tray model to be updated based on optimization and tray dropper locations. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | PPRK |  | ET-M16-L-N-TRAY-01004 | 10729C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
General | Cable tray optimization shall be evaluated and implemented from AFT to FWD modules. A tray sizing report shall be provided, taking into account the current loading status, design growth percentage, and PB spare allowance 20%. If support not required - it can be removed. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | PPRK |  | General | 10730C | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Shift these equipment to the edge of the column for better cabling | The equipment has been shifted to the edge of the column for better cabling. | PB Ops | TEL | Pending PB Reply | 23/12/2025 | None |  | None | None | TEL | None | 05-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M14 |  | SPI-M14-01514 SPP-M14-00024 SPP-M14-00027 | 10731C |  | 12.0000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 26/12/2025 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 28/12/2025
Level 1 | Shift the equipment (COR-5518383B) down by 100mm | shifted the equipment by 100mm down.now its in 2400mm. | SEA | TEL | Pending PB Reply | 23/12/2025 | None |  | None | None | TEL | None | 05-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M14 |  | COR-5518383B | 10732C |  | 12.0000000000000 | 3.00000000000000 | SEA/KBR | None |  | None | None | 26/12/2025 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 28/12/2025
Level 1 | Shift the equipment (LSE-5518058A) down by 150mm | The equipment has been shifted down by 150 mm | PB Ops | TEL | Pending PB Reply | 23/12/2025 | None |  | None | None | TEL | None | 05-JAN-2026 SEA REMARKS: 3D MODEL UPDATED AS PER COMMENT. (SEE KBR ACTION COMMENT) | M14 |  | LSE-5518058A | 10733C |  | 12.0000000000000 | 3.00000000000000 | PB - Operation | None |  | None | None | 26/12/2025 | 07/01/2026 | 09/01/2026 | 11/01/2026 | 07/01/2026 | 28/12/2025
Level 1 | Shift the equipment (LSE-5518057B) to the location marked up in the snapshot or based on the study. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M14 |  | LSE-5518057B | 10734C | 27/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Relocate the CCTV (CAM-5514087) to the (South) location marked-up in the snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M14 |  | CAM-5514087 | 10735C | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Shift the equipment (SPP-M14-00012) down by 150mm | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M14 |  | SPP-M14-00012 | 10736C | 27/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 Mezzanine | Shift the equipment (COR-5518385B) as marked-up in the snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M14 |  | COR-5518385B | 10737C | 27/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2<br>Level 3 | Shift the equipment (BLE-5511300 & BLE-5511302) to the other side of the column - refer marked-ups in the snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M14 |  | BLE-5511300 BLE-5511302 | 10738C | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | 1. Tray lighting to move to left side. 2. Shift the electrical lighting - elevate and move to the opposite site. Refer to mark-ups in the snapshots | light fixture relocated and cable tray updated accordinly to have better access | SEA | ELE | RE-OPEN | 18/12/2025 | None |  | None | None | ELE | None | None | M-14 |  | SPL-M14-00203 SPL-M14-00209 SPL-M14-00265 EC-M14-L-E-TRAY-20630 | 10739C |  | 4.00000000000000 | 16.0000000000000 | SEA/KBR | None |  | None | None | 21/12/2025 | 25/12/2025 | 27/12/2025 | 28/12/2025 | 25/12/2025 | 21/12/2025
Level 3 | Shift the equipment (CAM-5514090) inside | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M14 |  | CAM-5514090 | 10740C | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 3 | CCTV to be relocated to South where the electrical socket is currently located. The Electricalsocket to be relocated as per the mark-up. Electrical to check the possibility of relocating the socket to accommodate the CCTV. Refer to mark-up in snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M14 |  | CAM-5514090 | 10741C | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Shift the equipment as per marked-up in snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M14 |  | BLE-5511306 | 10742C | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 4 | Shift these equipment as per marked-up in snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M14 |  | BLE-5511307 COR-5518407A | 10743C | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
General | Cooling water pump cable tray tie in must be finalised and aligned with the instrumentation cable tray/penetration | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M14 |  | Typical IT-M14-S-I-TRAY-01099 B-5124001A/B/C/D B-5124002A/B/C | 10744C |  |  |  | SEA/KBR | None |  | None | None
General | To provide small vertical cable trays dropper going to JBs. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M14 |  | Typical example: JBC-1425-003 JBI-1425-003 | 10745C |  |  |  | SEA/KBR | None |  | None | None
Level 1 | Cable tray need to connect with proper connectivities | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M14 |  | IT-M14-S-I-TRAY-01096 | 10746C |  |  |  | SEA/KBR | None |  | None | None
Level 2 | To provide horizontal cable tray (typical JBs) | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M14 |  | JBI-1425-006 | 10747C |  |  |  | PB - Operation | None |  | None | None
Level 2 | Lewa vendor cable tray to be aligned with KBR MCT (PS-08, 09, 10 & 11) | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M14 |  | PS09 | 10748C |  |  |  | SEA/KBR | None |  | None | None
Mezzanine | Update the penetration according to approved TQF (TQF-P84P85-S2N-DD-TOP-ELE-0019), Typical dwg, Catalogue and Structural guideline | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M14 |  | I-M14-S-PEN-124 | 10749C |  |  |  | SEA/KBR | None |  | None | None
Level 1 | Trimmer support to be provided | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M14 |  | PIT-5124007C | 10750C |  |  |  | SEA/KBR | None |  | None | None
Level 1 | Relocate transmitter to optimize tubing route - rotate the instrument to the east facing Refer to the mark-up in the snapshot | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-14 |  | PIT-5124017 | 10751C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Penetration to follow the structural standard spacing requirements - need to maintain min 50mm gap between penetration and nearby structure. Typical - To check all equipment not limited to the tags listed in this Punch. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-14 |  | PIT-1251020 I-M14-S-PEN-212 I-M14-S-PEN-213 I-M14-S-PEN-205 I-M14-S-PEN-202 | 10752C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Missing tubing MCT to be modelled. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-14 |  | PDS-M14-NE-02 | 10753C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
General | To check with vendor if flush ring is considered. All Level 3 LIT diaphragam flush ring to be modelled by Vendor. | None | PB | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-14 |  | General | 10754C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Vendor to update the model of package skid opening for cable tray. | Awaiting a response from Vendor KSB | PB | MECH | OPEN |  | None |  | None | None | Vendor | None | None | M-14 |  | ET-M14-M-TRAY-05021 | 10755C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Vendor to model internal cable tray within the package. | Awaiting a response from Vendor KSB | PB | MECH | OPEN |  | None |  | None | None | Vendor | None | None | M-14 |  | ET-M14-L-N-TRAY-10017 | 10756C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Vendor to model internal cable tray within the package. | Cable tray inside pump package is modelled. | PB | MECH | Pending Seatrium Reply | 06/01/2026 | None |  | None | None | Vendor | None | None | M14 |  | EC-M14-L-N-TRAY-01027 | 10757C | 19/02/2026 | 1.00000000000000 |  | PB - Engineering | None |  | None | None | 09/01/2026 |  |  |  |  | 11/01/2026
Level 1 | Vendor to resolve Instrument JB access issues. | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M14 |  | None | 10758C |  |  |  | PB - Operation | None |  | None | None
Level 1 | Vendor to model internal cable tray within the package. | Awaiting KSB vendor response. | SEA | MECH | OPEN | 05/01/2026 | None |  | None | None | Vendor | None | None | M-14 |  | EC-M14-L-N-TRAY-01013 | 10759C | 19/02/2026 | 2.00000000000000 |  | SEA/KBR | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
Level 1 | Lighting JBs to be arranged side by side. Mounting height to comply as per typical installation detail information. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-14 |  | CXN-L-M14-451 | 10760C | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Vendor to update model details to avoid obstruction of cable entry to package. | Awaiting a response from Vendor LEWA | SEA | MECH | OPEN |  | None |  | None | None | Vendor | None | None | M-14 |  | E-M14-L-MCT-030 E-M14-L-MCT-041 | 10761C | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
Mezzanine | Deck penetration model to be updated based on floor steel grating type. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-14 |  | E-M14-L-PEN-001 | 10762C | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
Mezzanine | Instrument deck penetration model to be updated based on floor grating type. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-14 |  | I-M14-S-PEN-123 I-M14-S-PEN-125 I-M14-S-PEN-127 I-M14-S-PEN-128 | 10763C | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
Multilevel | Space issues on glanding and cable termination. Resolve and provide adequate space for cable termination. | cable tray reocated to have better glanding space | PB Ops | ELE | Pending PB Reply | 18/12/2025 | None |  | None | None | ELE | None | 23-DEC-2025 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-14 |  | LEM-351-01-M14-003 LNO-225-06-M14-002 | 10764C |  | 4.00000000000000 | 16.0000000000000 | PB - Operation | True |  | None | None | 21/12/2025 | 25/12/2025 |  |  | 25/12/2025 | 21/12/2025
Multilevel | Provide missing sub-tray between lighting cable trays main run and the lighting fixture. | Missing sub-tray provided between lighting cable trays main run and the lighting fixture. | PB Ops | ELE | Pending Seatrium Reply | 24/12/2025 | None |  | None | None | ELE | None | None | M-14 |  | LEM-351-02-M14-001 LEM-351-02-M14-004 LNO-225-05-M14-001 LNO-225-07-M14-009 LNO-225-14-M14-004 LEM-351-08-M14-003 | 10765C |  | 14.0000000000000 |  | PB - Operation | None |  | None | None | 27/12/2025 |  |  |  |  | 28/12/2025
Level 2 | Bring the floodlights inside the guard rail and position accordingly in accessible locations within platform, for the purpose of easy maintainability of floodlights. (Note: Current position of floodlights were accepted in DR60, reference punch is 229B.) | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-14 |  | LNO-225-15-M14-001 LEM-350-05-M14-004 LNO-225-15-M14-002 LES-312-09-M14-005 | 10766C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Ensure beacon is easily visible for operators and personnel, it should not be obstructed. Relocate/adjust beacon location or relocate the light fixture. | None | PB Ops | CSE | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | LSE-5518062B | 10767C |  |  |  | PB - Operation | None |  | None | None
Level 2 | Adjust deluge pipe to create adequate clearance with the floodlight. | Flood light relocated to provide better clearance from the deluge pipe. | PB Ops | ELE | Pending PB Reply | 24/12/2025 | None |  | None | None | ELE | None | 10-JAN-2026 SEA REMARKS: (SEE KBR ACTION COMMENT) | M-14 |  | LNO-225-11-M14-002 | 10768C |  | 16.0000000000000 | 0 | PB - Operation | None |  | None | None | 27/12/2025 | 12/01/2026 | 14/01/2026 | 14/01/2026 | 12/01/2026 | 28/12/2025
Level 3 | Relocate JB, bring closer to location of light fixture. | JB relocated closer to light fixture. | PB Ops | ELE | Pending Seatrium Reply | 24/12/2025 | None |  | None | None | ELE | None | None | M-14 |  | LEM-351-08-M14-001 | 10769C |  | 14.0000000000000 |  | PB - Operation | None |  | None | None | 27/12/2025 |  |  |  |  | 28/12/2025
Level 1 | To check on rotating the JB to the opposite side or cable to face the same direction. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-01 |  | CCD-5514001 CCT-5517001 TT-M01-L-E-TRAY-00002 TT-M01-L-E-TRAY-00003 | 10770C | 27/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | To move the camera (CAM-5514001) to the other column and lift up by 3120mm. Refer to the mark-up in the snap shot | The camera (CAM-5514001) has been moved to the other column and raised by 3120 mm, as per the mark-up in the snapshot | KBR | TEL | RE-OPEN | 07/01/2026 | None |  | None | None | TEL | None | None | M-01 |  | CAM-5514001 | 10771C | 28/12/2025 | 0 |  | PB - Engineering | None |  | None | None | 10/01/2026 |  |  |  |  | 11/01/2026
Level 1 | Shift the equipment (PA-5517001) as per the mark-up in the snapshot | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-01 |  | PA-5517001 | 10772C | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Check the location for this speaker (COR-5518007A). Ensure it is accessible. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-01 |  | COR-5518007A | 10773C | 27/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Relocate the camera (CAM-5514003) to the left by 800mm - as shown in the mark-up | The camera (CAM-5514003) has been relocated 800 mm to the left, as shown in the mark-up | KBR | TEL | Pending PB Reply | 07/01/2026 | None |  | None | None | TEL | None | None | M-01 |  | CAM-5514003 | 10774C | 28/12/2025 | 1.00000000000000 | -1.00000000000000 | PB - Engineering | None |  | None | None | 10/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
Level 3 | Move the pole (BLE-5511029) across and rotate the speaker (COR-5518012B) direction - facing the module. Refer the snapshot. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-01 |  | BLE-5511029 COR-5518012B | 10775C | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 3 | Swap these equipment locations. | None | KBR | TEL | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | PA-5517003 CXE-L-M01-211 | 10776C | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 4 | Compressor Vendor to ensure the speakers sound coverage will reach the required Level 4 areas | Awaiting a response from Vendor GARO | PB | MECH | OPEN |  | None |  | None | None | MECH | None | None | M-01 |  | None | 10777C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | The cable tray needs to be added below the JB, and the MCT should be modelled in accordance with the guidelines. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | I-M01-S-MCT-102 | 10778C |  |  |  | SEA/KBR | None |  | None | None
Level 1 | The vendor is to provide the penetration in the grating to align with the KBR MCT. They must also verify whether the grating is removable. If it is not removable, sufficient space shall be provided to allow access to the deck MCT. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | IT-M01-S-I-TRAY-01031 | 10779C |  |  |  | SEA/KBR | None |  | None | None
Level 1 | MCT is missing - to be provided in the location shown in the mark-up | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | IT-M01-S-I-TRAY-01030 | 10780C |  |  |  | SEA/KBR | None |  | None | None
Level 2 | To extend the cable tray up to the JB. Maintain 300mm minimum clearance. Typical for all JBs | None | PB | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | IT-M01-S-I-TRAY-02020 | 10781C |  |  |  | PB - Operation | None |  | None | None
Level 2 | The JB is to be rotated 90°, and the penetration should be positioned in front of the JB. (Can be facing any of the access path direction) | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | JBIF-1411-007 | 10782C |  |  |  | SEA/KBR | None |  | None | None
Level 2 | RIO panel LV cables are to be connected from the bottom. The side LV MCT is to be checked and removed. The instrument opening should be sized to accommodate the LV cable tray. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | E-M01-L-PEN-205 | 10783C |  |  |  | SEA/KBR | None |  | None | None
Level 3 | The vendor is to provide the penetration in the grating to align with the KBR MCT. They must also verify whether the grating is removable. If it is not removable, sufficient space shall be provided to allow access to the deck MCT. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | IT-M01-S-I-TRAY-03005 | 10784C |  |  |  | SEA/KBR | None |  | None | None
Level 3 | Vendor to align the interface instrument cable tray as per the KBR proposal. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | IT-M01-S0I-TRAY-03006 | 10785C |  |  |  | SEA/KBR | None |  | None | None
Level 4 | Provide clearance between HV to Instrument trays as per PB specification. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | ET-M01-M-TRAY-20007 | 10786C |  |  |  | SEA/KBR | None |  | None | None
Level 3<br>Incl FT | Cable tray, Penetration & supports are missing. To be updated. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | JBIF-1354-012 | 10787C |  |  |  | SEA/KBR | None |  | None | None
None | Update missing cable tray supports | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | IT-M01-S-S-TRAY-01006 | 10788C |  |  |  | SEA/KBR | None |  | None | None
None | The deluge system Spray access is currently blocked by the cable ladder. This is a general comment: all access points must be verified to ensure that no cable ladder obstructs them. | None | PB | ELE | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | IT-M01-S-S-TRAY-01007-TRAY-0203 | 10789C |  |  |  | PB - Operation | None |  | None | None
Level 1 | Relocate the Instrument to clear the clash with ladder. | None | PB | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | LIT-5412008 | 10790C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
Multilevel | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all Instruments, JB and valves M01. Also the Tray which running close to the deck is should be checked and routed above the coaming height. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M01FT |  | General Examples: PIT-1350008 PIT-1350004-2 TS-M01-AUTO-INST-ELEV1-INST | 10791C | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
Multilevel | Provide Flushing ring to allow cleaning and reduce maintenance time These instruments are classified as capillary diaphragm instruments, therefore they must have a flushing ring to allow for cleaning and calibration. I-ET-3010.00-1200-800-P4X-013 - item 6.5.9 | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | DIFF. PRESSURE LEVEL TRANSMITTER- DIAPHR LIT-1350002 LIT-1350004 LIT-5412001-1 LIT-5412001-2 LIT-5412001-3 LIT-5412002 LIT-5412003 LIT-5412006-1 LIT-5412006-2 LIT-5412006-3 LIT-5412008 LIT-5412009 LIT-5412011 LIT-5412013 LIT-5412014 LIT-5412015 PRESS. TRANSMITTER W/ INDICATOR - DIAPHR PIT-1350001A PIT-1350001B PIT-1350002A PIT-1350002B PIT-1350004-1 PIT-1350004-2 PIT-1350004-3 PIT-1350006 PIT-5133014 PIT-5412001 PIT-5412002-1 PIT-5412002-2 PIT-5412002-3 PIT-5412004A PIT-5412004B PIT-5412005A PIT-5412005B PIT-5412006 PIT-5412007-1 PIT-5412007-2 PIT-5412007-3 PIT-5412013 PIT-5412014 PIT-5412027 | 10792C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Multilevel | Tubing penetrations are to be modeled for the missing area. Tubing should not share penetrations with cable trays. Tubing trays and cable trays must have separate penetrations. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | M01FT |  | PIT-5241002 TIT-5415004-1 | 10793C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Evaluate the possibility of changing the capillary to impulse tubing, as the tapping point is at a very high elevation and cannot be properly maintained if a capillary is used. | None | PB | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | PIT-5412006 | 10794C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Multilevel | Instrument cable trays, penetrations, and supports for the analyzer panels are missing. Please provide. | None | PB | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | PN-AIT-1350001-1 PN-AIT-1350001-2 PN-AIT-1350001-3 PN-AIT-1350002-1 | 10795C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Due to accessibility issues, the transmitter needs to be relocated separately. Piping is to evaluate whether there is sufficient access space, as there is a beam above the location. | None | PB | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-01 |  | TIT-5412005 I-1/2&quot;-F-B3NV-0679-NI | 10796C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Electrical trays, penetrations, and supports for the analyzer panels are missing. To be provided | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-01 |  | PN-AIT-1350002-1 | 10797C | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Two PDITs are to use one support, and the two TITs are also to use one support. | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | FT |  | PDIT-5415002-1 PDIT-5415002-2 TIT-5415004-1 TIT-5415004-1 | 10798C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Conduit penetrations are missing for the Flare JBs. | None | SEA | CSE | OPEN |  | None |  | None | None | CSE | None | None | FT |  | JBC-5412-820 | 10799C | 29/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Evaluate the cable ladder placement in FLR tower for electrical and instrument conduits, and plan to route them either on the platform area or beside the vertical cable ladder to ensure easy access. | None | PB Ops | CSE | OPEN |  | None |  | None | None | CSE | None | None | FT |  | TIT-5415004-1 | 10800C | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Vendor (Nitrogen Generator Unit) to model internal electrical cable tray within the package. | Awaiting a response from Vendor GDK | PB Ops | MECH | OPEN |  | None |  | None | None | MECH | None | None | M-01 |  | Z-5241001A Z-5241001B | 10801C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Vendor to model internal electrical cable tray within the package. | Awaiting a response from Vendor GDK | SEA | MECH | OPEN |  | None |  | None | None | MECH | None | None | M-01 |  | UC-Z-5241001 | 10802C | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Vendor to provide updated model (stp file), showing proper alignment of electrical cables to the terminal box. Resolve the MCT access issues. This is also DR60 Punch ID 10462B | Awaiting a response from Vendor GARO | None | MECH | OPEN |  | None |  | None | None | Vendor | None | None | M-01 |  | E-M01-M-MCT-001 E-M01-M-MCT-002 E-M01-M-MCT-003 | 10803C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Vendor to provide removable grating with penetrations and with proper size to enable access to MCT. Vendor to provide internal cable tray model. | Awaiting a response from Vendor GARO | KBR | MECH | OPEN |  | None |  | None | None | STR | None | None | M-01 |  | E-M01-M-MCT-007 | 10804C | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | To check the possibility of using common MCT for penetration, instead of 2 separate MCTs very close to each other. Implement the common MCT after all technical & constructability checks are completed. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-01 |  | E-M01-L-MCT-007 E-M01-L-MCT-008 | 10805C | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Consider floodlight mounted on beam instead of pole-mounted support. Ensure accessibility to floodlight. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-01 |  | LEW-295-01-M01-002 | 10806C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Provide heat shield to JBs near flare top platform. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | FLR |  | JBC-5412-801 JBC-5412-803 JBC-5412-810 JBC-5412-811 JBC-5412-820 JBC-5412-821 | 10807C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Provide sub-tray to lighting fixture. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-01 |  | General LES-295-04-M01-001 LES-295-04-M01-006 LNO-208-10-M01-004 | 10808C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Pipe obstructing light maintenance access. Re-position the light or change the mounting type. Ensure access for maintaining the light is provided. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-01 |  | LNO-208-06-M01-003 | 10809C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Adjust light approximately 100mm away from nearest valve handwheel. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-01 |  | LNO-208-16-M01-001 | 10810C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Evaluate lighting fixture location to ensure maintainability of equipment. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-01 |  | LEM-317-07-M01-004 | 10811C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | AOL lights sub-trays at flare base to avoid running close to the floor. Trays to be mounted on nearby available structures. | None | PB | ELE | OPEN |  | None |  | None | None | ELE | None | None | FT |  | TS-FLR-ELE-TRAY-HOOK-LV2 | 10812C | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | 1.Missing handling Route volume. 2.check to shift handling route along AFT direction. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | None | 20216C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
3 | 2D drawing to match with 3D drawing | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | None | 20217C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
3 | 1. valve transportation to be modelled. 2. valve handling to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | SDV-1252022A-1 VALV-12521163 | 20218C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Valve weight more than 3mt, handling volume for valve to be modelled | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | VALV-12520196 | 20219C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Shift the Hose stand to the marked location (clear space for valve handling) | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | M07A-L3-US-0004-HOSE STAND | 20220C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Drop zone volume is clashing with structure beam, hatch to be provided. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | None | 20221C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Missing handling path to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | None | 20222C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Relocate the insturement item, to close with PCHE handling path and turning. | None | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | None | 20223C | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Padeye orientation to be corrected. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | VALV-12310139 | 20224C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Provide removable flange at the the markup location. Typical for all 4 PCHE | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | P-UC-1252001A-01, P-UC-1231002A-02, P-UC-1231002B-01, P-UC-1231002B-02 | 20225C | 08/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Removable spool to be provided, for valve swing handling. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | VALV-12312396 | 20226C | 08/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve handling to be modelled | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | VALV-12310146, VALV-12310209, VALV-12310089 | 20227C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Padeye orientation to be corrected, update the handling path to 1 meter. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | VALV-12310092 | 20228C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve handling to be modelled, handling width to update to 1 meter. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | SDV-1231070A-1 | 20229C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Model multiple padeye for swing and drop on the deck trolley, Typical comment for all valve highlighted in the circle punch snapshot. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | VALV-12310091 , HV-1231003A , HV-1231067A , VALV-12310176 , VALV-12310527 , VALV-12311208 , HV-1231003B , HV-1231067B , VALV-12311210 , VALV-12311205 . | 20230C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve Handling to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | VALV-12311214 , VALV-12310559 | 20231C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve lifting handling to modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | SDV-1231070B-1 | 20232C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Relocate the JB to clear the handling path way. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | JBI-1417-801 | 20233C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Potential PCHE clash with valve during handling. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | P-UC-1252001A | 20234C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
5 | 1. Light fixture to be shifted from davit operation zone. 2. Cable tray to be route under the deck 3. Handrail to be removable type. 4. Model davit swing volume | None | None | ELE | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | None | 20235C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
5 | 1.Model scaffolding volume at the marked location. 2.shift the lift fixture to clear area for valve handling. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | BDV-1252014A-2 | 20236C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Light fixture and flood light to be shifted away from valve handling. | Light Fixtures location updated. | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-07A |  | LNO-214-15-M07A-006 , LNO-214-18-M07A-002 , LNO-214-16-M07A-003 | 20237C |  |  |  | PB - Operation | None |  | None | None
1 | MH to lower the Lift beam to clear the clash with Piping | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | OFBM-M14-1004-1MT | 20238C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Handling to add obstruction for pipe lifting. Piping to shift the line away from the spool handling. | 17/12/25 - It is Handling issue and to be resolved by Handling discipline and not instrument. | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | 4&quot;-FW-B7-1107-NI ESP-51240239 | 20239C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Handling to model 2 lifting beams for valve handling. The beams should be able to share with the cable tray supports and strong enough for valve handling. Transport of valve need to be in horizontal position as valve is very tall. Typical method how to transport this type of tall valve to be provided. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | FV-1251014 | 20240C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1mezz | Handrail to be made removable and handrail should be able to remove first before lifting the pipe. Apply to whole aft of mezz deck. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | None | 20241C | 16/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Piping and cabel tray to be shifted away fro beam clamp handling. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | VALV-12510435 VALV-12510441 | 20242C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Cable tray to rerouted to clear the clash | Cable tray rerouted to avoid the clash | None | ELE | Pending PB Reply | 24/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M-14 |  | EC-M14-L-E-TRAY-10557-TRAY-0001 | 20243C |  | 5.00000000000000 | 10.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 27/12/2025 | 01/01/2026 | 11/01/2026 | 11/01/2026 | 01/01/2026 | 28/12/2025
2 | Beam clamps that is use for handling the motor to be clamp on primary/secondary structure instead of adding new lifting beam. KBR shall optimise the amount of new structure to reduce weight increase. Obstruction volume for handling to be clash free. | After discussions with Structure team and Seatrium MH it was decided to keep the lifting beam as the current arrangement is optimised. also changing the Beam clamp location to Secondary & tertiary beams will change the design of already issued in AFC drawings. Kindly close this tag to avoid further changes in Structural drawings | KBR | HAND | Pending PB Reply | 28/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Noted, as per discussion with KBR & Seatrium structural team, the alternative design to current lifting beam design will not improve much. Additionally, changing will add more weight. Therefore, the team opt to keep current design as it is. | M-14 |  | None | 20244C | 10/01/2026 | 1.00000000000000 | 10.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 31/12/2025 | 01/01/2026 | 11/01/2026 | 11/01/2026 | 01/01/2026 | 31/12/2025
2 | General comment for M14 level 2: Handling of pump to be modelled. Handling volume/obstruction volume for handling to be clash free. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | GEN/M-14 |  | None | 20245C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Beam clamp capacity to be confirm. Study weight is 2.5mt but clamp capacity is model 2mt. Vendor "not commited" info weight is 1.6mt. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | None | 20246C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2&3 | Handrails to confirm is removable type. Hierichery to be name "removable" with correct coloring | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | None | 20247C | 16/02/2026 |  |  | PB - Operation | None |  | None | None
3 | All flame arrestors handling at level 3 to be simplified using beam clamps. During DR90, handling using stacker/counter weight crane is rejected. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | None | 20248C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handling of this flame arrestor to clamp on primary or secondary str and lower it so as to swing transfer to with beam clamp on pipe support. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | XSE-1261005 | 20249C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Cable tray, lighting, telecom (all EIT items) that are attached on the bumper bar shall not be higher that the top of the bumper bar. During the review in DR90, there are lighting angle bar protruding higher than the bumper bar by abit and no cable tray modelled in yet. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | None | 20250C |  |  |  | PB - Operation | None |  | None | None
4 | Bumper bar slope to connect/as close as possible. PB STR and Seatrium STR to have further discussion on decision. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | None | 20251C | 16/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Turning radius obstruction volume to be modelled. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | None | 20252C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipe line clashing with Handling path. | Handling path adjusted. now cah resolved | KBR | PIP | Pending PB Reply | 23/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | None | M-01 |  | None | 20253C | 23/01/2026 | 6.00000000000000 | 10.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 26/12/2025 | 01/01/2026 | 11/01/2026 | 11/01/2026 | 01/01/2026 | 28/12/2025
1 | Update handling path. During DR90 review, the obstruction and yellow path is not aligned. | MH Reply : 13/12/2025 1.Handling route and Obstruction volumes updated. | None | HAND | Pending PB Reply | 12/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec2025_Cleared. | M-01 |  | None | 20254C | 20/01/2026 | 17.0000000000000 | 10.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 15/12/2025 | 01/01/2026 | 11/01/2026 | 11/01/2026 | 01/01/2026 | 15/12/2025
1 | Handling simulation for compressor & motor needs to be modelled with required MH equipment until piperack. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | None | 20255C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | There are pad eye's on the skid for motor handling ,pipe line to be shifted outside (AFT direction) of the Skid to avoid motor handling swing volume clash. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | None | 20256C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | 1. Removable handreail to be marked in the Hierarchy as "REM" to identify. (Typical for all levels in M-01). Refer snapshot 1 and 2 locations. | 16DEC25 - Hierarchy Name Renamed | KBR | STR | RE-OPEN | 15/12/2025 | None |  | None | None | HAND | None | None | M-01 |  | None | 20257C | 11/01/2026 | 23.0000000000000 |  | PB - Operation | None |  | None | None | 18/12/2025 |  |  |  |  | 18/12/2025
1 | Add scaffolding volume at the marked locations for cylinder rack handling | MH Reply: 13/12/2025 1.MH Volumes updated. | None | HAND | Pending PB Reply | 12/12/2025 | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 30Dec205_Cleared. | M-01 |  | None | 20258C | 20/01/2026 | 17.0000000000000 | 10.0000000000000 | PB - Operation | True | 09/01/2026 | True | None | 15/12/2025 | 01/01/2026 | 11/01/2026 | 11/01/2026 | 01/01/2026 | 15/12/2025
2 | 1.shift the beam clamp towards the FWD direction (too close to pipe line). 2 . update beam clamp obstruction volume. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | XV-5412004 | 20259C | 06/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Lower the beam clamp to clear cable tray clash | MH Reply : 1312/2025 1.Inverted goal post structure added to clear cable tray clash. 2.Handling obstruction volumes updated. | None | HAND | Pending PB Reply |  | None |  | None | 07.01.26_B0RG_CLOSE | HAND | None | 16Dec2025_Cleared. | M-01 |  | PSE-5412003-1 | 20260C | 20/01/2026 |  | 24.0000000000000 | PB - Operation | True | 09/01/2026 | True | None |  | 18/12/2025 | 11/01/2026 | 11/01/2026 | 18/12/2025
2 | 1. MH to model the obstruction volume. 2.minimum clear space of 750 mm is required for handling the valve using scaffolding. 3.Instrumentation cable trey to be shifted / cut short to clear the space as mentioned. 4.instrument Air line to be re-routed to clear the space. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | HV-5412001 | 20261C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
2 | 1. Handrail to be designed to accommodate the valve removable. 2 make the handrail removable type. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | XV-5412017 | 20262C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Removable handrail to be marked in the Hierarchy as "REM" to identify. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | None | 20263C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
3&4 | Removable handrail to be marked in the Hierarchy as "REM" to identify. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | None | 20264C | 29/01/2026 |  |  | PB - Operation | None |  | None | None
3 | 1.instrument items to be shifted inside the skid / away from the handling path. 2. shift the camera away from the STGRO motor Drop zone. | 17/12/25 - Cameras and F&G devices are not Instrument item to resolve, It has to be done by Telecom and Safety. | None | TEL | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | AST-CH4-M01-301-006 AST-CH4-M01-301-003 CAM-5514003 | 20265C |  |  |  | PB - Operation | None |  | None | None
3 | Weight of filter striner basket to be clarified. | Awaiting a response from Vendor GARO | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | UC-5412001 | 20266C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Re-route the drain line behind the exchanger support. | Awaiting a response from Vendor GARO | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | UC-5412001 | 20267C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
4 | With reference to DR60 -M-01-1588B , handrail to be made split type (as per standard max length is 2.1 meter). | Awaiting a response from Vendor GARO | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | UC-5412001 | 20268C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Vendor to advice how to bring the motor along with the terminal box without clashing with the column. | Awaiting a response from Vendor GARO | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | UC-5412001 | 20269C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1.Model portable Davit. 2. make the handrail removable type. | Awaiting a response from Vendor GARO | SE | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | UC-5412001 | 20270C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Relocate the light fixture. | None | None | ELE | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | UC-5412001 | 20271C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Hydrant and instrument item to be relocated form handling path. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | UC-5412001 | 20272C | 13/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1. Handling volume to be updated. 2.light fixture and speaker to shift away from valve handling path. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | LNO-208-16-M01-003 COR-5518015B | 20273C |  |  |  | PB - Operation | None |  | None | None
4 | Light fixture to be shifted. | None | None | ELE | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | LNO-208-16-M01-001 | 20274C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1.Handling path to be modelled. 2. relocate the extinguisher and instrument item away from cylinder handling path.( Z-5428012 , DS-S12-7-0401 ) | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-01 |  | Z-5428012 DS-S12-7-0401 | 20275C | 20/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Cylinder handling to be provided. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | FLR |  | N2 BOTTLE RACK | 20276C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
Top of Piperack | Structure to ensure reinforcement under the deck for Winch and padeye Welding during Flare tip handling. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | FLR |  | None | 20277C | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Top of Piperack | Flare handling procedure to be provided in MH Study Report. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | FLR |  | None | 20278C | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 7 degree ramp required at the 2 specific circled area. During DR90 discussion, the 2 area marked "X" does not require ramp. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-14 |  | None | 20279C | 16/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Coaming to be deleted as there is drain pit provided. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-07A |  | None | 20280C | 21/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Structural to model the coaming inline with the gutter/ drain box. | Coaming updated | KBR | STR | RE-OPEN | 06/01/2026 | None |  | None | None | HAND | None | None | PPRK-M-04 |  | SPI-M07B-161 | 20281C | 08/01/2026 | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
1 | Delete the coaming as gutter and drain box is provided | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-07B |  | None | 20282C | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Update the platform as per marked | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | None | 1136c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Sampling panel to be rotated towards accessway | SPI-M01-256 to be relocated | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | SC3-C5-ESP-54120162 | 1137c |  |  |  | PB - Operation | None |  | None | None
2 | Model FIT Instrument connection for FEs | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FE-5412014 FE-5412013 | 1138c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check with vendor and Process on the line arrangement and tapping orientation - the lines to be connected on top of Process line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | ESP-54120038 2&quot;-F-B19-1924-NI 2&quot;-F-B3N-0423-NI | 1139c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Upstream of XV, slope to be provided | 31-12-25- slope updated upstream of XV-5412004 | None | PIP | Pending PB Reply | 30/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | nonpiing dcn required | M-01 |  | XV-5412004 | 1140c | 30/01/2026 | 2.00000000000000 | 7.00000000000000 | PB - Operation | True | 09/01/2026 | True | None | 02/01/2026 | 04/01/2026 | 11/01/2026 | 11/01/2026 | 04/01/2026 | 04/01/2026
1 | Check the instrument tapping orientation as per instrument standard and update. Typical for HP and LP. | 31-12-25 Following PG in suction lines placed vertical tapping as per instrument standard . PG-5412002A PG-5412002B PG-5412001A PG-5412001B Following PIT in discharge lines placed 45 down tapping as per instrument standard PIT-5412005A PIT-5412005B PIT-5412004A PIT-5412004B | None | PIP | Pending PB Reply | 30/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | NO PIPING DCN REQUIRED | M-01 |  | PG-5412002A PG-5412002B PIT-5412005A PIT-5412005B PG-5412001A PG-5412001B PIT-5412004A PIT-5412004B | 1141c | 30/01/2026 | 6.00000000000000 | 3.00000000000000 | PB - Operation | True | 09/01/2026 | True | None | 02/01/2026 | 08/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026 | 04/01/2026
1 | Closed drain to be modelled for HP/LP pumps | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | None | 1142c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check nozzle numbering is correct as per P&ID | KBR Process - Piping to refer the latest P&ID master for the correct nozzle numbers and update the model as required. | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | V-5412001 | 1143c |  |  |  | PB - Operation | None |  | None | None
1 | Model a reserve volume in front of LITs for maintenance space | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | LIT -5412006-1/2/3 LIT-54120011 LIT-5412009 | 1144c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Vent and drain valves to be modeled for LGs. Typical for LP and HP. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | LG-5412010/5412007 LG-5412005/5412004 LG-5412008 LG-5412012 | 1145c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain to be included - confirm with Process | None | None | PRO | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | PC-0209 | 1146c |  |  |  | PB - Operation | None |  | None | None
1 | TP point to be checked and line routing as per standard detail. Block valve to be as close as possible to the process line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | ESP-54120055 ESP-54120166 VALV-54120241 VALV-54120187 VALV-54120239 | 1147c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure slope is provided for these lines below deck | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 4&quot;-PC-B3N-0047-NI 4&quot;-PC-B3N-0675-PP | 1148c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Move PIT connection to Level 2 after confirming with Process | No concern from Process. Piping to evaluate the feasibility and move. | None | PRO | RE-OPEN | 08/01/2026 | None |  | None | None | PIP | None | no piping dnc required | M-01 |  | PIT-5412006 | 1149c |  | 0 | 0 | PB - Operation | None |  | None | None | 11/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
2 | Evaluate and provide minimum clearance between the PIT and TIT | 31-12-25-Minimum clearance provide between PIT and TIT | None | PIP | Pending PB Reply | 30/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | no piping dcn required | M-01 |  | PIT/TIT-5412013 PIT-5412014 TIT-5412014 | 1150c | 30/01/2026 | 3.00000000000000 | 6.00000000000000 | PB - Operation | True | 09/01/2026 | True | None | 02/01/2026 | 05/01/2026 | 11/01/2026 | 11/01/2026 | 05/01/2026 | 04/01/2026
None | Evaluate slope requirement 3% AFT to FWD and confirm with process on marked portion for M01 and Piperack flare lines. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M01/PPRK |  | 10&quot;-F-B3N-1181-NI 10&quot;-F-B19-0385-NI 38&quot;-F-B19V-0683-NI 28&quot;-F-B3N-1951-NI 38&quot;-F-B19V-0683-NI 28&quot;-F-B3NV-0558-NI | 1151c | 09/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Update the FE catalogue to show FIT and TIT | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FE-5412052 | 1152c |  |  |  | PB - Operation | None |  | None | None
4 | Remove spool near breakup flange and check if possible to provide common access by moving line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FG-0010 FG-0121 | 1153c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
4 | Model missing lines related to FE-5412008 and FE-5412007 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FIT-5412055A FIT-5412055B FIT-5412055C FIT-5412057 FIT-5412058A FIT-5412058B FIT-5412058C FIT-5412060 FIT-5412062 FIT-5412003 FIT-5412064 | 1154c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Model the missing piping and instruments | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FIT-5412007 FO-5412008 FIT-5412005 FO-5412006 1&quot;-FG-B19-0091-NI 1&quot;-FG-B3N-0090-NI 2&quot;-FG-B19-0121-NI | 1155c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Check and bring below portion to top of deck | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 2"-F-B19-1163-NI | 1156c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
PPRK | Model the PIT for HP/LP Staging Skid lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | PIT-5412016-1 PIT-5412016-2 PIT-5412016-3 PIT-5412015-1 PIT-5412015-2 PIT-5412015-3 20&quot;-F-B19-0337-NI | 1157c | 21/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | LP and HP Staging skid - not possible to access to panel | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | None | 1158c | 08/02/2026 |  |  | PB - Operation | None |  | None | None
PPRK | LP and HP Staging skid drain connections not matching P&ID. Location to be confirmed with Vendor and valve access to be considered. | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M07A |  | 1 1/2&quot;- VES-54128520 1 1/2&quot;- VES-54128522 | 1159c | 21/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Check and update Instrument Air supply requirements with Process and Instruments. Typical for HP and LP Staging Skid | None | None | PRO | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | None | 1160c |  |  |  | PB - Operation | None |  | None | None
PPRK | PSE valve modelling details to be updated. Actuators to reflect actual type of valve - buckling pin, hydraulic actuator. Typical for LP and HP Staging Skid. | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M07A |  | PSE-5412910A/B PSE-5412911A/B | 1161c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Purge lines should be connected as close as possible to downstream of valves HV-5412005/HV-5412012. Current configuration to be checked and confirmed with Process. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | 2&quot;-F-B19-0942-NI 2&quot;-F-B19-1655-NI 2&quot;-F-B3N-0876-NI 2&quot;-F-B3N-1641-NI | 1162c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | FIT and PIT to be modelled on FE. Typical for LP and HP. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | FE-5412010 FIT-5412010 PIT-5412010 FE-5412011 FIT-5412011 PIT-5412010 FE-5412012 FIT-5412012 PIT-5412012 | 1163c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Line from Chromatograph panel to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | 2"-F-B19-0950-NI | 1164c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
None | Lines to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 2&quot;-F-B3N-1766-ET 1&quot;-F-B3N-0725-NI 1&quot;-F-B3N-1632-NI | 1165c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Spec break flanges to be modelled | 31-12-25-Spec break flanges to be modelled (I-DE-3010.2S-5412-944-S2N-007) as per PID. | None | PIP | Pending PB Reply | 30/12/2025 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | no piping dcn required | M-01 |  | 38"-F-B3NV-0679-NI 8"-F-B10-0955-NI | 1166c | 06/02/2026 | 2.00000000000000 | 7.00000000000000 | PB - Engineering | True | 09/01/2026 | True | None | 02/01/2026 | 04/01/2026 | 11/01/2026 | 11/01/2026 | 04/01/2026 | 04/01/2026
PPRK | Valve to be relocated to accessible position | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | VALV-54120116 | 1167c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Sampling connection lines to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 2&quot;-F-B6-0791-NI 2&quot;-F-B16-0794-NI | 1168c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | I-DE-3010.2S-5412-944-S2N-003 Area breaks for M07A/B to be updated on P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | None | 1169c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Flare ignition skid and Flare Tips and Flare Tip lines to be modelled. Low point drain to be included as per P&ID I-DE-3010.2S-5412-944-S2N-003. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | Z-TA-5412001-03 TA-5412001 | 1170c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Strainer and spectacle blind to be modelled. Nozzle tie-in size to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | ESP-54120172 ESP-54120015 2&quot;-FG-B10-0037-NI | 1171c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
FLR | PN-TA-5412001-05 lines to be modelled as per P&ID I-DE-3010.2S-5412-944-S2N-003. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | FLR |  | PN-TA-5412001-05 | 1172c | 15/01/2026 |  |  | PB - Operation | None |  | None | None
FLR | Flare Ignition Skid and Nitrogen bottles location to be evaluated - PB considers that the skid must be relocated to an easily accessible location, as close as possible to the first level of the topside. Access and operation of this skid are required in emergency situations when the flare is out and all other ignition methods have failed. In this scenario, the presence of a gas cloud coming from the flare tip is expected, which may make access to the location unsafe. Currently, the only access to this skid is a 9-meter vertical ladder, which requires the use of a fall-arrest harness and is considered work at height. The nitrogen bottles must also be placed in a location where refilling and replacement are possible. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | FLR |  | PN-TA-5412001-05 N2 BOTTLE RACK | 1173c |  |  |  | PB - Operation | None |  | None | None
FLR | PIT to be located on Piperack | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | FLR |  | PIT-5415002 | 1174c | 15/01/2026 |  |  | PB - Operation | None |  | None | None
FLR | Confirm that the panels can resist the heat at the location close to flare tips | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | FLR |  | JBC-5412-801 JBC-5412-803 JBC-5412-810 JBC-5412-811 JBC-5412-820 JBC-5412-821 | 1175c |  |  |  | PB - Operation | None |  | None | None
FLR | Vent tips to be separated by a minimum distance in order to allow safe mainrtenance operation - location to be different based on Safety Study. Vent outlet shall have a curvature to avoid rain water accumulation and it shall be taken into account in Gas Dispersion Analysis. | None | None | SAF | OPEN |  | None |  | None | None | PIP | None | None | FLR |  | JBC-5412-801 | 1176c |  |  |  | PB - Operation | None |  | None | None
FLR | Line missing. Valve to be located as near as possible to process line and accessible to the operator. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | FLR |  | VALV-54150155 VALV-54150518 1&quot;-DO-E8-0104-PP - CO2 | 1177c | 15/01/2026 |  |  | PB - Operation | None |  | None | None
FLR | TITs to be modeled . PSE catalogue to be updated. | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | FLR |  | TIT-5415004-1 TIT-5415004-2\ | 1178c |  |  |  | PB - Operation | None |  | None | None
FLR | Location of the Flame Arrestor to be evaluated considering access by ladder. Note 1 of P&ID to be considered - IT SHALL BE FORESEEN FACILITIES FOR ACCESS AND CLEANING WITH AIR AND FRESH WATER | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | FLR |  | XSE-5415004-1 and XSE-5415004-2 | 1179c | 15/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Check FE category and raise the line min 1m based on that. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FG-0620 FG-0123 FG-0121 FG-0122 1&quot;-F-B19-0119-NI 2&quot;-F-B19-0684-NI 1&quot;-F-B3N-0727-NI 2&quot;-F-B3N-0846-NI | 1180c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Model the lines associated with FGRU package as per P&ID I-DE-3010.2S-5412-944-S2N-004 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | UC-5412001 | 1181c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Update FE platform and handrail | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FE-5412027 | 1182c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
3 | FGRU vendor to update handrails and safety bars at missing locations. Ladders height to be higher than handrails as per standard detail. | Awaiting a response from Vendor GARO | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M-01 |  | UC-5412001 | 1183c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Lines to be supported | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 10&quot;-PC-B16N-0055-NI 6&quot;-F-B9-0793-NI | 1184c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model all lines related to Utility Stations for M01 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | None | 1185c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Analyser tie-in lines (flare lines), analysers, and panels to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 2&quot;-F-B3N-0481-NI 2&quot;-F-B3N-0755-NI | 1186c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Low point drain to be modelled and block valve to be as close as possible to header. Locate at the lowest point and update P&ID | Note 7 is already provided in P&ID. Piping to raise PUN for any change in tap-off location. | None | PRO | RE-OPEN | 08/01/2026 | None |  | None | None | PIP | None | NO PIPING DCN TO ISSUE | M-01 |  | VALV-13500253 | 1187c |  | 0 | 0 | PB - Operation | None |  | None | None | 11/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
3 | Valve levers to be reoriented to avoid interference | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | VALV-13500102 VALV-13500114 VALV-13500117 | 1188c | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
4 | Ensure sufficient space is provided for hose connection at utility stations. Orientation cannot be upward. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | VALV-13500027 VALV-13500034 VALV-13500020 VALV-13500042 VALV-13500026 VALV-13500048 VALV-13500078 VALV-13500008 | 1189c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Coaming to be adjusted to cover drain and utility connections. Coaming to be continuous through access route - quarter pipes not required. | None | None | STR | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | None | 1190c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Penetrations for all lines to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FG-0794 FG-0767 | 1191c | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | Instrument orientation on water lines to be updated considering liquid service | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | W-0935 W-0936 | 1192c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Removable spool length to be shortened | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | W-0653 W-0937 | 1193c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Drain valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | VALV-13500068 VALV-13500067 2&quot;-W-B10-0653-NI | 1194c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Low point drain to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | W-0935 | 1195c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Supports to be modelled for Cooling Water lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | None | 1196c | 23/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | 3% slope to be provied at the marked portions (no pocket line) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 6&quot;-FG-B10-0767-NI 6&quot;-FG-B10-0794-NI | 1197c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | PITs to be modelled and sufficient clearance to be provided between Instrument connections | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | PIT-1350002A, PIT-1350002B | 1198c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Vent valve to be mounted directly non nozzle. Access is not required to be provided | 02-01-26-Model updated as per DR90 comment .(No access required ) and ladder from platform removed as per DR90-1200C | None | PIP | Pending PB Reply | 01/01/2026 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | no piping dcn required | M-01 |  | VALV-13500017 | 1199c | 13/02/2026 | 1.00000000000000 | 6.00000000000000 | PB - Engineering | True | 09/01/2026 | True | None | 04/01/2026 | 05/01/2026 | 11/01/2026 | 11/01/2026 | 05/01/2026 | 04/01/2026
3 | Ladder to be removed - vessel cleats may remain. Access not required at top of vessel. | Ladder removed | KBR | STR | Pending PB Reply | 30/12/2025 | None |  | None | None | STR | None | None | M-01 |  | V-1350001-LADDER-3 | 1200c | 29/01/2026 | 2.00000000000000 | 6.00000000000000 | PB - Engineering | None |  | None | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
3 | Reserve volume for maintenance access to be modelled in front of the LITs | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | LIT-1350004/1350002 | 1201c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Vent and drain valves to be modelled for LG | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | LG-1350003 | 1202c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Drain to be located inside coaming without changing coaming | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | VALV-13500094 | 1203c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | FO to be modelled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FO-1350010 | 1204c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve access to be evaluated and updated accordingly | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | VALV-13500131 VALV-13500134 | 1205c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Removal support to be added for FE | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FE-1350006 | 1206c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Update sampling connection tapping as per note 30 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | P-0814 | 1207c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Verify the access for TIT and gap between XV and TIT | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | P-0814 | 1208c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Instruments to be modelled | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FIT-1350006 PIT-1350006 | 1209c |  |  |  | PB - Operation | None |  | None | None
4 | Analyser cabinet, valves, lines, insruments and panels to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | AIT-1350002-1 AIT-1350002-2 AIT-1350002-3 | 1210c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Ensure valve handwheel is free of interference. Provide valve handwheel volume | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | P-0814 | 1211c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Check and provide minimum spool between valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | P-1011 | 1212c | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | Add support for UC line | 02-01-26-Support added in line. | None | PIP | Pending PB Reply |  | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | no piping dcn required | M-01 |  | 3"-P-B10-1859-NI | 1213c | 20/02/2026 |  | 6.00000000000000 | PB - Engineering | True | 09/01/2026 | True | None |  | 05/01/2026 | 11/01/2026 | 11/01/2026 | 05/01/2026
3 | 3&quot;-P-B10-1010-NI- No pocket and Slope requirement - The highlighted branch has a pocket (AFT position) - Verify were the No pocket requiriment begins, as the line goes up downstream the SDV-1350002 - To implement slope towards the line on the piperack | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 3"-P-B10-1010-NI | 1214c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Piping to be modelled as per P&ID I-DE-3010.2S-1350-944-S2N-002 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 1/2&quot;-W-B3N-3738-NI 2&quot;-DA-B9-3555-NI 2&quot;-DA-B9-3556-NI 2&quot;-DA-B9-3557-NI 2&quot;-PC-B9N-2795-NI 1/2&quot;-PC-B17-2395-NI 1&quot;-IA-B3-0812-NI 1&quot;-IA-B3-0860-NI 2&quot;-W-B3-0747-NI 4&quot;-W-B10-0698-NI 4&quot;-W-B10-0746-NI 1/2&quot;-DFC-B3N-2021-NI | 1215c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Line to run straight as much as possible to avoid pockets | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | DFC-2021 | 1216c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Instruments to be modelled and update FE catalogue | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | FIT-1350007, PIT-1350007 | 1217c |  |  |  | PB - Operation | None |  | None | None
2 | Avoid low point in the area and evaluate pipe rack routing and confirm with Process | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | PC-0208 | 1218c | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
1 | Lines to be modelled. Height of instruments to be raised by 1m as per ergonomic requirement. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | F-0187 F-0188 | 1219c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Forecastle area break to be updated on P&ID for these lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 5241002A/B ESP-52418720 / 52418820 3&quot;-SA-B10-0013-NI 3&quot;-SA-B10-0014-NI 2&quot;-BG-B10-0023-NI | 1220c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Missing all the lines and Tie-ins PSVs-5241810A/B not modelled 1&quot;-IA-B3-1165-NI 1&quot;-IA-B3-1166-NI 3&quot;-BG-B10-0022-NI And interconnection from the skid to the N2 Bottles Lines BG-0369 until BG-0385 I-DE-3010.2S-5241-944-S2N-00 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 5241810A/B 1&quot;-IA-B3-1165-NI 1&quot;-IA-B3-1166-NI 3&quot;-BG-B10-0022-NI BG-0369 until BG-0385 | 1221c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Handwheel access to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | VALV-52410036 VALV-52410510 | 1222c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Coaming and grating to be provided and lines to slope toward nozzle. Check with vendor that sufficient slope is provided at collection basin. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | 2"-DA-B9-3558-NI / 3559 / 3560 | 1223c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | WEEP HOLE SHALL BE PROVIDED AT PSV OUTLET LINE TO ENSURE ACCUMULATED WATER IS DRAINED. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | BG-0768 BG-0767 | 1224c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | LG from HP Flare Drum nozzle N7A is blocking accessway | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M-01 |  | LG-5412004 | 1225c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Gutter nozzle arrangement to be aligned with Process wrt to the height limit from bottom of gutter and distance from the end of the gutter. | None | None | PIP | OPEN |  | None |  | None | None | PRO | None | None | M-01 |  | None | 1226c | 30/01/2026 |  |  | PB - Engineering | None |  | None | None
FLR | Deck shield structure on top of Flare Tower to be modelled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | FLR |  | None | 1227c | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Actuator size to be updated as per latest vendor information | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | SDV-1233001-1 | 1228c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Hydrostatic vent to be flanged | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-0477 P-0819 | 1229c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | CIP point detailing to be completed - model FI, piping and valve. Typical for M06 CIP. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | CIP-12330001 CIP-12330002 CIP-12330051 CIP-12330052 CIP-12330003 CIP-12380003 CIP-12380002 CIP-12380004 CIP-12380005 | 1230c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Drain to be from bottom of header pipe. List of affected valves to be provided by KBR/SEATRIUM | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330999 VALV-12330056 VALV-12330937 VALV-12330097 VALV-12330852 VALV-12330840 VALV-12330543 VALV-12330475 VALV-12330389 VALV-12330788 VALV-12330209 VALV-12330713 VALV-12331226 VALV-12330102 | 1231c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Slope AFT to FWD to be maintained on these lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | P-0359 4&quot;-P-E6N-0178-NI 4&quot;-P-E6N-0207-NI 4&quot;-PC-E3N-0484-NI 3&quot;-P-H6N-0926-HC 3&quot;-P-H6N-0927-HC 2&quot;-HWP-C4-0148-HC 10&quot;-F-C4-0879-NI 10&quot;-F-C4-0878-NI 3&quot;-PC-E3N-0356-NI 4&quot;-P-E6N-0359-NI | 1232c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Sampling point routing to be updated to ensure nearby valve can be operated without interference | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-2499 | 1233c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Confirm with KBR/Seatrium Instruments that PDIT valve orientation up is acceptable or update to downward if required | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330175 VALV-12330193 | 1234c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model a reserve volume square box 500mm in front of LITs for maintenance space | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | LIT-1233008 / 11 / 12 / 13A/B | 1235c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Utility connection block valves to be located as near as possible to nozzle. PB confirms that additional means of access is not required to be provided. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330216 / VALV-12330148 | 1236c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Confirm with Process and Safety that SDV position is acceptable considering distance between SDV and Vessel. Current position is more than 15m from Vessel. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | SDV-1233004/05/06/07 | 1237c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Low point drain connection to be provided | Low point drain modelled | KBR | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PIP | None | None | M-06 |  | PC-0891 | 1238c | 23/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
1 | Routing to be updated to avoid pocket | Jan-07 Model updated, pocket has been removed | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | no piing dcn required | M-06 |  | PC-8098 | 1239c |  | 0 | 2.00000000000000 | SEA/KBR | True | 09/01/2026 | True | None | 09/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
1 | Minimum slope to maintained for PSV lines towards equipment nozzles. Should have 1% slope from FWD to AFT liquid flow to the vessel, And 3% slope from AFT to FWD liquid slop to vessel | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-8098, PC-8069, PC-8125 3&quot;-PC-E19N-0876-HC 3&quot;-PC-E19N-0879-HC | 1240c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
1 | Filter element removal volume to be modelled | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | FT-1233001A/B | 1241c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | Provide opening/cut-out for LG visibility | None | None | STR | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-2348-N7A | 1242c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | PDIT tapping orientation to be updated considering fluid type, as per standard detail. Typical for both exchangers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330141 | 1243c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Re-orient cleaning connection downward to act as low point drain. Typical for both exchangers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330322 | 1244c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Re-orient utility connection downward to act as drain. Typical for both exchangers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330209 VALV-12330258 | 1245c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Slope to be provided. Typical for both exchangers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1246c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Valves to be updated to DBB. PB wants to check the changes caused in the surroundings by the valve replacement. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350158 VALV-51350922 VALV-51350171 VALV-51350925 | 1247c | 23/01/2026 |  |  | None | None |  | None | None
3 | Valves to be updated to DBB. PB wants to check the changes caused in the surroundings by the valve replacement. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350169 VALV-51350253 VALV-51350256 VALV-51350167 | 1248c | 23/01/2026 |  |  | None | None |  | None | None
4 | Valves to be updated to DBB. PB wants to check the changes caused in the surroundings by the valve replacement. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330945 VALV-12330051 VALV-12330949 VALV-12330032 | 1249c | 23/01/2026 |  |  | None | None |  | None | None
5 | Valves to be updated to DBB. PB wants to check the changes caused in the surroundings by the valve replacement. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330460 VALV-12330423 VALV-12330270 VALV-12330375 VALV-12330576 VALV-12330578 VALV-12330680 VALV-12330699 VALV-12330670 VALV-12330711 VALV-12330690 VALV-12330589 | 1250c | 23/01/2026 |  |  | None | None |  | None | None
5 | MIT tie-in piping to be modelled. Typical for M06 MIT. P&amp;ID Note to be considered - TIE IN POINT AT ANALYSER VENDOR END SHALL BE 1/2&quot; OD. FOR FURTHER DETAILS REFER VENDOR P&amp;ID. | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | MIT-1233007 MIT-1233926 MIT-1233006A MIT-1233006B MIT-1233950 MIT-1233007 MIT-1233006C | 1251c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Handrail to be opened to connect adjacent platform space | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1252c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Drain to be modelled at lowest point between the block valves | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330757 VALV-12330758 | 1253c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Deck penetration to be modelled at elbow | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | FG-0040 | 1254c | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
6 | Drain to be changed to vent | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350206 | 1255c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
6 | FE size increase to 20". Ensure sufficient space for handling and escape routes. | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FE-1233047 | 1256c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
2 | P&ID I-DE-3010.2S-1233-944-S2N-003 Note 13 to be updated - piping arrangement is more than 2m for PSE. | Note 13 in Master P&ID 1233-003 is marked up.. The text "PIPING DISTANCE UP TO 2 METERS" is deleted. Piping to refer the latest P&ID master. | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M-06 |  | None | 1257c |  | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
3 | Internals removal volume to be updated | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | FT-1233003A/B | 1258c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Deluge line to be rerouted to avoid filter opening volume | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FT-1233003A/B | 1259c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Scaffolding volume for filter access to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FT-1233003A/B | 1260c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Valve lever operation to be clear of flange | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330870 | 1261c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Route the sampling line without pocket | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-2489 | 1262c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Safe location of AIT-1233009 to be updated in model | None | None | SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | AIT-1233009 | 1263c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Material handling volume for Filter internals removal to be updated | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | FT-1233002A/B | 1264c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Model reserve volume for standing space at top of filter during maintenance - 1500mm height, 500mm wide. | None | None | HAND | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FT-1233002A/B | 1265c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
5 | N7 PG valve orientation to be updated to give more clearance | Jan-08 Valve updated | KBR | PIP | Pending PB Reply | 07/01/2026 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | no piping dcn required | M-06 |  | PG-1233042B | 1266c | 16/01/2026 | 0 | 1.00000000000000 | PB - Operation | True | 09/01/2026 | True | None | 10/01/2026 | 10/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
5 | Slope to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-0780 PC-0789 | 1267c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
7 | Take bypass branches above deck level | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1268c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
5 | High point vent ot be provided | High point vent modelled | KBR | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PIP | None | None | M-06 |  | PC-0778 | 1269c | 16/01/2026 | 0 |  | SEA/KBR | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
5 | FE to be updated with vendor details. Straight length/flow straightener requirement to be confirmed. FE position to be adjusted to meet downstream straight length requirement (17U/7D) | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | FE-1233048 | 1270c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | PIT orientation to be updated for access from stair | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PIT-1233047 | 1271c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valve to be relocated to downstream of check valve VALV-12330509 at low point | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330312 | 1272c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Line to branch into top as per P&amp;ID. Confirm with Process that block valve location below branch connection is acceptable. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | P-0463 VALV-12330726 | 1273c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
6 | Intrument to be updated in model | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | XE-1233006 | 1274c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Low point drain to be provided | Low point drain modelled | KBR | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PIP | None | None | M-06 |  | P-0819 | 1275c | 16/01/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
1 | Quarter cut pipe should match the direction of escape route | Jan-08 Model updated | KBR | PIP | Pending Seatrium Reply | 07/01/2026 | None |  | None | None | SAF | None | None | M-06 |  | None | 1276c |  | 0 |  | PB - Operation | None |  | None | None | 10/01/2026 |  |  |  |  | 11/01/2026
1 | Marked quarter pipe is not required. | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1277c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Missing ladders to be modelled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1278c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Firelocker to be rotated toward escape route as per Safety Plan. Equipment numbering to be made consistent between model and Safety Plan. | Firelocker rotated toward escape route as per Safety Plan. | KBR | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M-06 |  | Z-H-5423039 Z-H-5423040 | 1279c | 06/02/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
1 | Hydrant piping penetrating coamed area to be evaluated by Safety. Hydrant location to be updated on Safety Plan as per model. Equipment numbering to be made consistent between model and Safety Plan. | Jan-08 Hydrant pipe routing updated | KBR | PIP | Pending Seatrium Reply | 07/01/2026 | None |  | None | None | SAF | None | None | M-06 |  | H-5423039 H-5423040 | 1280c | 23/01/2026 | 0 |  | PB - Operation | None |  | None | None | 10/01/2026 |  |  |  |  | 11/01/2026
1 | Equipment support missing. Extinguisher position to be updated to avoid onstruction by coaming. Extinguisher operation volume to be modelled - typical for M06 Extinguishers. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5428090 Z-5428123 | 1281c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | EEBD supports to be modelled. EEBD operation volume to be modelled - typical for M06 EEBD | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5434015 Z-5434047 Z-5434016 Z-5434017 Z-5434018 Z-5434052 | 1282c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Safety shower piping to be modelled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5434342 Z-5434343 Z-5434344 Z-5434486 Z-5434345 Z-5434346 | 1283c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Coaming to be updated as per standard detail at quarter pipe location | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1284c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment support missing. Extinguisher position to be updated to avoid onstruction by coaming. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5428091 | 1285c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment location on Safety Plan to be updated as per model | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5428484 | 1286c |  |  |  | PB - Operation | None |  | None | None
1 | Equipment location on Safety Plan to be updated as per model | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5428089 | 1287c |  |  |  | PB - Operation | None |  | None | None
1 | Cage height to match top of ladder height. Fall arrestor to be provided for ladder more than 5m high. Typical for M06 ladders. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1288c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Cage height from deck to be 2m or 2.1m for ladder in escape routes. Typical punch for M06 ladders. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1289c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure ladder access area is clear of obstruction - Typical for M06 ladders | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1290c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure valve lever is clear of ladder. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | VALV-12380035 | 1291c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Kickplate to be modelled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1292c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Extinguisher not required at this location as per Safety Plan | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5428096 | 1293c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Hydrant pipe support to be modelled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | H-5423041 | 1294c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Missing kickplate to be modelled. Typical for M06 missing kickplates | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1295c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Safety plan escape route to be updated as per 3D model | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1296c |  |  |  | PB - Operation | None |  | None | None
2 | Hydrant operating volume to be moved to front of hydrant | Hydrant operating volume moved to front of hydrant | KBR | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M-06 |  | H-5423219 | 1297c | 13/02/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
2 | Structural support to be modelled and handrail to be cut back for access. | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-H-5423219 | 1298c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Valve handwheel to be rotated toward excape route and access platform to be deleted | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350230 | 1299c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Equipment location to be adjusted to have clear space for operation | Equipment location adjusted to clear space for operation | KBR | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M-06 |  | Z-5428098 | 1300c | 13/02/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
2 | Handrail to be extended as marked and kickplates to be completed for both platforms | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1301c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Update handrail to chamfered design | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1302c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Piping within head height above ladder to be rerouted | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FW-2007 FW-2008 | 1303c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Handrail to be updated considering bracing is temporary | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1304c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Provide top rail of handrail across the gap | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1305c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Safety bar to be provided at top of ladders - typical for M06 ladders | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1306c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Guardrail to be provided | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1307c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Gap at handrails (handrail to handrail, or handrail to structure) to be as per standard details (typical 75mm, max 120 mm) typical punch for M06 | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1308c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Quarter cut pipe not required at marked locations | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1309c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Ensure clear space for escape route - coaming to be adjusted | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1310c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Esacape route volume to be modelled | Esacape route volume modelled | KBR | PIP | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | SAF | None | None | M-06 |  | None | 1311c | 13/02/2026 | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
3 | M09 Escape route volume to be modelled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1312c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Instrument manifold blocking opening of firelocker door | None | None | CSE | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-H-5423044 PDA-M06-E-04 | 1313c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Extinguisher to be relocated to area with clear access | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5428486 | 1314c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Provide guard rail on access platform below piping | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1315c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handrails to be provided on access platforms - typical for M06 access platforms | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1316c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Safety bar required on both sides. Handrail to be removed. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1317c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
3 | 200mm clearance to be provided behind ladder as per standard detail | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1318c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Ladder position to be updated | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1319c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handrail at interconnection to be aligned | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1320c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Extinguisher to be relocated to area with clear access | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5428128 | 1321c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Penetrations without cable trays to be removed | None | None | CSE | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | IT-M06-PEN-419 IT-M06-PEN-423 | 1322c |  |  |  | PB - Operation | None |  | None | None
5 | Safety Plan to be updated with hook-up stair as per 3D model | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1323c |  |  |  | PB - Operation | None |  | None | None
5 | Kickplate to be outside handrail to avoid obstructing escape route | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1324c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Equipment to be modelling to be updated as EEBD | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5434048 | 1325c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Handrail to be provided at top of ladder | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1326c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Kickplate and guardrail to be provided below piping on access platform. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1327c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
6 | Ensure 1000m clear space for escape route | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1328c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
6 | EEBD to be moved to be clear of obstruction | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | Z-5434049 | 1329c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
6 | Equipment tag numbers to be updated as per Safety Plan | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | H-5423205 Z-H-5423205 H-5423206 Z-H-5423206 | 1330c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
6 | Escape route volume to be modelled on ladder. Ladder to be updated on the Safety Plan drawing. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1331c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
7 | Hydrant pipe support and fire locker supports to be modelled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | H-5423250 Z-H-5423XXX | 1332c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
7 | Safety Plan to be updated with Vacuum Breaker numbering as per P&ID. Typical for both vacuum breakers. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | PD-M06-L7-100051 PD-M06-L7-100381 | 1333c |  |  |  | PB - Operation | None |  | None | None
7 | Hydrant operating volume to be moved to front of hydrant. Hydrant pipe support to be modelled | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | H-5423249 | 1334c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
7 | Equipment tag number to be updated as per Safety Layout | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | H-5423249 Z-H-5423249 | 1335c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
7 | Escape route volume to be modelled on stair landings (typical for M06 stair landings) | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 1336c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Instrument stand and deluge piping to be relocated and minimum access to be provided between filters | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FT-1233001A / FT-1238001B 1&quot;-FW-B7-1989-NI PDIT-1238012B LIT-1238008B | 1337c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Modelling to be updated for Sampling Box outlet lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 2&quot;-F-B6N-1739-NI 2&quot;-F-B6N-1740-NI 2&quot;-F-B6N-1743-NI 2&quot;-F-B6N-1744-NI 1&quot;-IA-B3-1123-NI 1&quot;-IA-B3-0103-NI | 1338c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Utility connection to be lowered | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330686 | 1339c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Valve to be reoriented to be within the coaming | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330710 | 1340c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Drain valve to be rotated to provide more clearance | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330637 | 1341c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | LIT tag numbers to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330560 VALV-12330704 PG-1233041 LIT-1233029 LIT-1233030 | 1342c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure it is possible to view the LG | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | LG-1238002 | 1343c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Cable tray supports to be offset to provide clear access. Portable access volume to be modelled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FE-1233053 | 1344c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Avoid pocket in the line and removable spools to be modelled as per P&ID Note 10. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FE-1233053 | 1345c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Provide clear access for TIT | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | TIT-1233019 | 1346c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Modelling to be fixed - elbow instead of tee | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1347c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Sampling connection to be re-oriented considering sampling quill. Ref. I-ET-3010.00-1200-588-P4X-001_E | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-12330126 ESP-12330127 ESP-12330124 ESP-12330123 ESP-12380107 ESP-51350103 ESP-12380105 ESP-12258023 ESP-12258027 ESP-12258031 ESP-12258035 | 1348c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Block valve on sampling line to be relocated close to sampling connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-12330138 | 1349c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Valve to be re-oriented for access | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330554 | 1350c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Elbow to be removed and ensure bolt removal is possible | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1351c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | UC block valve to be located as close as possible to nozzle. Typical for the listed equipment. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-1233001 V-UT1233001A/B/C/D | 1352c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | LIT arrangement to be updated as per sketch. Height of the LL nozzle is heigher than the LL - Nozzle of LIT instrument shall be 100mm lower than LL (350mm) and 100mm higher HH (1050mm) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1353c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain position to be downstream of SDV | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12331339 | 1354c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Provide access to the valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330083 | 1355c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
3 | FIT details to be updated as per vendor information. Verify the space for the equipments and there is no access for the instruments operation | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FIT-1233052 | 1356c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Sampling connection to be relocated as upstream of branch connection to be representative for both exchangers (A/B). | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330149 | 1357c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Telecom post to be relocated for Sampling valve access, | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | SPP-M06-00008 | 1358c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Slope to be provided (Free draining to FWD). Change from drain to vent (VALV-12330204/ 12330206/ 12330232 /VALV-12330233) for filling operation. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 6&quot;-HWP-C4-0142-HC 6&quot;-HWP-C4-0141-HC 6&quot;-HWP-C4-0144-HC 6&quot;-HWP-C4-0145-HC | 1359c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Utility connection to be in horizontal | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330215 | 1360c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Spectacle blind to be reoriented to provide clear valve access and remove pinch point | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-12330011 | 1361c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Piping arrangement to be updated considering space for hose connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | HWP-0005 | 1362c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | PDIT orientation to be downwards as per standard detail | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PDIT-1233002B | 1363c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
3 | Penetration sleeve height to be updated to match coaming height | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PG-M06-L3-104382 | 1364c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
3 | Vent to be updated to drain | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330343 | 1365c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | CIP-12330003 and FI-12330003 to be modelled. Straight length requirement for CI point to be met. 2m to be available for maintenance access. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | CIP-12330003 FI-12330003 CIP-12330001 CIP-12330002 CIP-12330051 CIP-12330003 CIP-12380003 CIP-12380002 CIP-12380004 CIP-12380005 | 1366c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Valves to be updated as drains. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330875 / 876 / 734 /735 | 1367c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Drain required downstream check valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330071 | 1368c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Provide clear access for PDIT and provide weld clearance between TEE and pipe support. Block valve to be as close as possible to process pipe. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PIT-1233016 VALV-12330150 | 1369c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Liquid state (L/V) to be clarified with Process and update orientation if required | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PDIT-1233018A | 1370c | 16/01/2026 |  |  | SEA/KBR | None |  | None | None
2 | Low point drain to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 6&quot;-HWP-C4-0146-HC 3&quot;-HWP-C4-0024-HC 3&quot;-HWP-C4-0137-HC 3&quot;-HWP-C4-0023-HC | 1371c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12331302 VALV-12331303 VALV-12331300 VALV-12331301 | 1372c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Lines to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 2&quot;-F-B9-2028-NI 2&quot;-F-B9-2029-NI 8&quot;-F-B19N-2022-NI 2&quot;-F-B9-2030-NI 2&quot;-F-B9-2031-NI | 1373c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Gooseneck to be provided at vent discharge. Process to confirm that P&amp;ID I-DE-3010.2S-1233-944-S2N-007 note 25 is met. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 2&quot;-F-B6-0967-NI 2&quot;-F-B6-1183-NI | 1374c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Avoid pocket on the line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | F-0967 | 1375c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | TP locations to be aligned Typical for compressor skid TPs | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | W-0547 W-0630 W-0631 W-0632 | 1376c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Valve to be updated as DBB as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330426 | 1377c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Portable stool to be provided for Valve access, exclusively for this access platform. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | VALV-12331299 | 1378c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Valve catalogue to be updated based on latest information from vendor | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12331299 | 1379c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | PDIT orientation to be updated for liquid service as per standard detail | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PDIT-1233017 PDIT-1233049 | 1380c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Handrail to be updated | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | None | 1381c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Drain to be changed to vent | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12330750 | 1382c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Bolts and bolt removal volume to be aligned with Piping | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-0231 | 1383c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Elbow to be removed from drain connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | HWP-0156 | 1384c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | TIT to be modelled. Verify if it has to be on the header (without acces, or if can be closer to the LEVEL 4 with access | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | TIT-1233052 | 1385c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Vent to be updated with flanges | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | "2""-PC-E19N-1136-HC 2""-PC-E19N-1138-HC 2""-PC-E19N-1081-HC | 1386c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | AFT to FWD slope to be maintained on PSV lines at marked locations. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 2&quot;-PC-E19N-2675-HC 2&quot;-PC-E19N-1131-HC 2&quot;-PC-E19N-1101-HC 2&quot;-PC-E19N-1137-HC | 1387c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Vendor information for Reinjection Gas Heaters TIT remote panels boxes to be confirmed and modelled | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | None | 1388c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Confirm with Process to relocate TIT to marked location. TIT to be tapped directly on process line. Model TIT extraction volume | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | TIT-1233051 10&quot;-PC-E19N-0574-HC | 1389c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Line routing to be completed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-0001 | 1390c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Actuator size to be updated as per latest vendor information and ensure clear of interference | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | SDV-1233901 | 1391c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Stagnant gas flow during adsorption in the other 2 vessels. Possibility of condensation and liquid accumulation upstream of the XVs. The condensate formed will be carried to the bed when one of these vessels enters adsorption. Confirm: how long the insulation will be able to retain heat and prevent condensation. Evaluate: installation of an automatic air vent upstream of the XVs to remove condensate prior to opening the XV P&amp;ID NO: I-DE-3010.2S-1233-944-FI4-101 | There is a bleed valve (VALV-12338xxx) upstream the XV which can be used to remove condensate if formed. Also bleed valve VALV-12338057 in bypass of XV can also be used. Hence No change is envisaged and considered closed. | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M-06 |  | PC-8061 | 1392c |  | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
4 | Avoid pocket on the XV bypass line in line with P&amp;ID note 18. Routing to be updated to avoid elbows as discussed with PB Material Handling team. Typical for all 4 adsorbers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-8147 | 1393c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Modify the drain valve and remove elbow | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12338051 | 1394c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | FO tag number update as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-8093 | 1395c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Spacer to be modeled as per P&ID - typical for all 4 adsorbers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-12338003 | 1396c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Manual Override panel to be accesible (Verify with vendor the model and location of panel) And provide portable step if necessary. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | XV-1233922A / XV-1233920A | 1397c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Tapping orientation to be made similar - bottom 45deg | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-8068 | 1398c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Block valve to be located as close as possible to vessel nozzle. PB confirms that these valves should change to category 3. Avoid pocket on inlet of sampling box. Typical for all 4 adsorbers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12338067 | 1399c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Line modelling to be completed. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-UT-1233001A-N9 | 1400c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Line to slope towards panel - Can not have pocket. - No access need an addtional valve on panel. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | Valv-12338077 SC3 -2258023 | 1401c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Confirm with vendor if drain can be added on blind flange as marked. There is no drainage point for the outlet line, possibility of condensation, and to free the vessel to opening. All the slope of lines direct to these point. Typical for all 4 adsorbers. | Awaiting a response from Vendor NOV. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M-06 |  | V-UT-1233001A/B/C/D | 1402c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Vendor to provide hinge or davit for blind flange to handle blind flange opening at N6A/B. Typical for all 4 adsorbers. | Awaiting a response from Vendor NOV. | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M-06 |  | V-UT-1233001A/B/C/D | 1403c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Clear space required in front of Adsorber D manway considering stretcher size | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-UT-1233001D | 1404c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
6 | Provide clear access for bypass valves. Update DBB valve handwheels. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1405c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
6 | Slope to be provided for adsorber PSV lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 6&quot;-PC-E32N-8112-HC 6&quot;-PC-E32N-8083-HC 6&quot;-PC-E32N-8166-HC 6&quot;-PC-E32N-8139-HC | 1406c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Spacers to be modelled. Spacer cannot be used on the DBB due to bolt type. Typical for all 4 adsorbers | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-12338007 / 12338025 / ESP12338017 | 1407c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | T-type strainer to be updated as per vendor latest info including drain. Bolt removal to be verified. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-12338074 ESP-12338072 | 1408c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | FIT and valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FE-1233047A/B FE-1233050 FE-1233051 | 1409c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | TIT and PIT tags to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | C-UC-1233001A/B PIT-1233081A PIT-1233082A TIT-1233055A TIT-1233056A | 1410c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Low point drain to be provided. Cleaning connection to be modeled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FV-1233047A/B | 1411c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | PDIT tag number to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12338665 | 1412c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | TEs to be modeled. Typical for both compressors. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | TE-1233050 TE-1233051 | 1413c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Valves to be reoriented to provide access. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12338647 VALV-12338646 VALV-12330431 VALV-12330430 | 1414c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Check valve number to be updated as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-8360 | 1415c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Secondary escape route to be 1m width | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1416c |  |  |  | PB - Operation | None |  | None | None
1 | Coaming to be updated as marked | Coaming updated | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | STR | None | None | M15 |  | None | 1417c | 22/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Extinguisher volume to be modeled with 2.1m height - typical for M15 Extinguishers Extinguisher position to be adjusted away from bracing. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1418c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment tag number to be updated as per Safety Layout | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1419c |  |  |  | PB - Operation | None |  | None | None
1 | Gap at handrails (handrail to handrail, or handrail to structure) to be as per standard details (typical 75mm, max 120 mm) typical punch for M15 | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-14 |  | None | 1420c | 08/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Add top rail above the valve - typical for all filter platforms | Handrail updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1421c | 04/02/2026 | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
1 | Safety cage is not required considering platform height. Safety bar to be provided. Gap at handrails to be as per standard details (typical 75mm, max 120 mm) | None | None | STR | OPEN |  | None |  | None | None | MECH | None | None | M15 |  | None | 1422c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Provide lower top rail below the piping | Handrail updated | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | STR | None | None | M15 |  | None | 1423c | 08/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Provide handrail as marked | Handrail updated | KBR | STR | Pending PB Reply | 25/12/2025 | None |  | None | None | STR | None | None | M15 |  | None | 1424c | 08/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Missing kickplate to be modelled. Typical for M15 missing kickplates | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M15 |  | None | 1425c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Missing kickplate to be modelled. | kick plate updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1426c | 29/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
1 | Check feasibility of providing removable handrail | No feasibility to provide handrail | KBR | STR | Pending PB Reply | 06/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1427c | 11/01/2026 | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
1 | Add handrail at the gap as marked | Handrail updateed | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | STR | None | None | M15 |  | None | 1428c | 12/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
1 | Ladder volume to be extended considering head height. Safety cage is not required considering platform height. Typical punch for M15 ladders | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M15 |  | None | 1429c | 04/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Quarter pipe direction to match direction of escape route - FWD, PORT, and STBD side | Coaming updated | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | STR | None | None | M15 |  | None | 1430c | 12/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
2 | Quarter pipe direction to be flipped to match escape route driection. Coaming to be updated to suit quarterpipe position. | Coaming updated | KBR | STR | RE-OPEN | 25/12/2025 | None |  | None | None | STR | None | None | M15 |  | None | 1431c | 12/01/2026 | 3.00000000000000 | 10.0000000000000 | PB - Operation | None |  | None | None | 28/12/2025 | 31/12/2025 | 02/01/2026 | 04/01/2026 | 31/12/2025 | 28/12/2025
2 | Coaming to be adjusted to provide clearance for hydrant operation | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M15 |  | None | 1432c | 12/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Ensure extinguisher operating space is clear of sample cabinet obstruction | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1433c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Equipment modelling to be updated as per Safety Layout. Extinguisher to be moved away from column for better access. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1434c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Junction box position to be adjusted away from Extinguisher access space | None | None | ELE | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1435c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Shift the extinguisher closer to the coaming | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | Z-5428398 | 1436c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Handrail to be provided on stair | Stair handrail updated | KBR | STR | Pending PB Reply | 04/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1437c | 08/01/2026 | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
2 | Handrail to be modelled between bracing and column | Handrail updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1438c | 04/02/2026 | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
2 | Top rail to be provided over piping | Handrail updated | KBR | STR | Pending PB Reply | 04/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1439c | 04/02/2026 | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
3 | Safety equipment in vendor scope to be incorporated into Safety Plan Drawing - typical for M15. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1440c |  |  |  | PB - Operation | None |  | None | None
3 | Extinguisher to be aligned on column | None | KBR | SAF | OPEN |  | None |  | None | None | STR | None | None | M15 |  | Z-5428102 | 1441c | 04/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handrail bar to be modelled | Bottom rail updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1442c | 04/02/2026 | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
3 | Ensure ladder access space is clear of coaming | coaming updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1443c | 04/02/2026 | 3.00000000000000 | 0 | PB - Operation | None |  | None | None | 07/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 07/01/2026
3 | Cage height from deck to be 2m or 2.1m for ladder in escape routes. Top of cage to be matched with top of ladder. Typical punch for M15 ladders. | Ladder updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1444c | 04/02/2026 | 3.00000000000000 | 0 | PB - Operation | None |  | None | None | 07/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 07/01/2026
4 | Ensure escape route is clear of obstruction from handrails | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1445c | 04/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Reduction of escape route width less than 1m to be evaluated, due to obstruction of vendor piping | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1446c |  |  |  | PB - Operation | None |  | None | None
4 | Ensure escape route is clear of onstruction from coaming | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1447c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Missing handrails to be modeled | Handrail updated | KBR | STR | RE-OPEN | 04/01/2026 | None |  | None | None | STR | None | None | M15 |  | None | 1448c | 04/02/2026 | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
5 | Model escape route volume on the ladder | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1449c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Quarter cut pipe direction to be updated to match direction of escape route. | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1450c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Quarter cut pipe direction to be updated to match direction of escape route. | None | KBR | STR | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1451c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Extinguisher to be moved closer to the safety path | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1452c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Extinguisher to be relocated to area with clear access | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | None | 1453c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Handrail height to be increased due to ladder within 1.5m, as per standard detail. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M15 |  | None | 1454c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Quarter cut pipe direction to be updated to match direction of escape route. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M15 |  | None | 1455c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Check whether the speaker can be mounted upwards because of falling equipment. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | COR-5518086B | 10813c | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Relocate speaker to edge for better cabling | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | SPP-M06-00016 | 10814c | 27/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Evaluate the location of WLAN | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | PA-5517012 | 10815c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Relocate the speaker | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | COR-5518086B | 10816c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Modify the tray based on the mark up | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | TT-M06-L-E-TRAY-10004 TT-M06-S-B-TRAY-00003 TT-M06-L-E-TRAY-00003 | 10817c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Shift the CCTV from Level 1 to Level 6 | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | CAM-5514020 | 10818c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Check the assessibility and evaluate the location | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | COR-5518088A | 10819c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate the BLE with the L type | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | BLE-5511100 | 10820c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate the speaker to edge | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | COR-5518105A | 10821c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Evaluate the location of WLAN | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | PA-5517029 | 10822c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Move the BLE to another face | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | BLE-5511102 | 10823c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate the CCTV to pole mount as per mark up | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | CAM-5514022 | 10824c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Shift the lighting to the edge | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | SPP-M06-00117 | 10825c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate the beacon that is overlapping | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LSE-5518013B | 10826c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate the lighting to the edge of the column for better cabling | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | SPL-M06-00123 | 10827c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Relocate the BLE to L type | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | BLE-5511106 | 10828c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Evaluate the speaker location | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | COR-5518095A | 10829c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Shift the CCTV from Level 4 to Level 7. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | CAM-5514024 | 10830c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
None | Swap the position of the speaker and the lighting | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | SPL-M06-00432 SPP-M06-00043 | 10831c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Change the support type to a longer one | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | PA-5517014 | 10832c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Shift the BLE to another face of the column | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | BLE-5511112 | 10833c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 6 | Relocate the speaker to edge of the column | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | COR-5518102A | 10834c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 7 | Change the BLE to L type | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | BLE-5511113 | 10835c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
Level 7 | Telecom Secondary Tray and supports are missing. General for M06 Modules. | 1/7/26 - Item punchlist is Telecom and not Instrument to clear. | None | TEL | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PA-5517098 | 10836c |  |  |  | PB - Operation | None |  | None | None
None | Vendor to proivide within skid cable tray routing. Vendor need to align with Topside cable tray Tie-in. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | IT-M06-S-I-TRAY-01008 | 10837c |  |  |  | SEA/KBR | None |  | None | None
None | Vendor RIO panel to to align with MCT | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | IT-M06-S-I-TRAY-01023 | 10838c |  |  |  | SEA/KBR | None |  | None | None
General | Main cable tray clash with 6 inch and below 6 inch pipes. Need to be resolved by Piping discipline. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | General | 10839c |  |  |  | SEA/KBR | None |  | None | None
None | Evaluate cable trays connect to JB. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | IT-M06-S-S-TRAY-02004 | 10840c |  |  |  | SEA/KBR | None |  | None | None
None | Confirm penetration opening is according to structural standard. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | IT-M06-PEN-230 | 10841c |  |  |  | SEA/KBR | None |  | None | None
None | Provide dropper tray for the JBs and horizontal tray to maintain minimum gap | None | None | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | JBC-1416-006 | 10842c |  |  |  | PB - Operation | None |  | None | None
General | E&I Trays between Gap need to maintain minimum clearance (Typical) | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | General | 10843c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Pipe is clashing with JB dropper tray. | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | IT-M06-S-S-TRAY-03007 2&quot;-PC-E32N-0750-PP | 10844c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Cable tray to algin to center of JB and optimise the bending | None | None | CSE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | IT-M06-S-I-TRAY-03021-TRAY | 10845c |  |  |  | SEA/KBR | None |  | None | None
General | E&I trays provide combined support. Typical for M06. | None | SEA | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | General | 10846c |  |  |  | SEA/KBR | None |  | None | None
Level 4 | JB cable ladder have too many bends, the design to be checked for the bending radius and tray to be optimized to avoid too many bends at too short distance | None | PB Ops | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | JBC-1416-005 | 10847c |  |  |  | SEA/KBR | None |  | None | None
Level 5 | JB horizontal cable tray needs to be updated | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-06 |  | IT-M06-S-S-TRAY-04002 | 10848c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Shorten the cable tray and align back cable tray with the front tray | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | TT-M07B-L-E-TRAY-00004 TT-M07B-S-A-TRAY-00005 | 10849c | 26/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Shorten the cable tray | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | TT-M07B-L-E-TRAY-00006 TT-M07B-S-A-TRAY-00003 | 10850c | 26/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Relocate the camera based on PB Operations team recommendation | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | CAM-5514032 | 10851c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Relocate the camera based on PB Operations team recommendation | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | CAM-5514031 | 10852c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Evaluate this speaker for better cabling | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | COR-5518127A COR-5518127B | 10853c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Evaluate this speaker for better cabling | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | COR-5518128A | 10854c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Relocate the speaker higher | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | COR-5518132B | 10855c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Move the camera to another face | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | LSE-5518021A | 10856c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Evaluate the location of this WLAN access point | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | PA-5517017 | 10857c | 26/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Mount BLE to the column | 8/1/26 - BLE-5511131 is a Telecom item and not instrument to resolve. | PB | TEL | OPEN |  | None |  | None | None | INST | None | None | M07B |  | BLE-5511131 | 10858c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Shift instrument to the edge of the column | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | SPI-M07B-719 | 10859c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 3 | Relocate the camera based on PB Operations team recommendation | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | CAM-5514034 CCD-5514109 | 10860c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 4 | Relocate the speaker as per the mark up | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | COR-5518143B | 10861c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 5 | Rotate the speaker direction as per the mark up | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | COR-5518146A COR-5518147A | 10862c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
General | Secondary trays are missing for Telecom equipment. General for M07B. | None | SEA | TEL | OPEN |  | None |  | None | None | Vendor | None | None | M07B |  | General | 10863c |  |  |  | SEA/KBR | None |  | None | None
Level 1 | Not enough space to install MCT. Installation space to be resolved. Vendor tray to suit the cable entry plan/bending, avoiding blockage to MCT location. | Awaiting a response from Vendor Siemens. | PB Ops | MECH | OPEN |  | None |  | None | None | Vendor | None | None | M-07B |  | E-M07B-H-MCT-003 | 10864c | 17/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Vendor to resolve the handrail and tray tie-in location interference. Vendor model to be updated accordingly. | M-07A/M-07B Injection gas compressor LV Cable tray Tie-in location vendor handrail clash and Vendor STP model is updated. | SEA | ELE | Pending Seatrium Reply | 05/01/2026 | None |  | None | None | ELE | None | None | M-07B |  | ET-M07B-L-N-TRAY-10051 | 10865c | 19/02/2026 | 2.00000000000000 |  | PB - Operation | None |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
Level 1 | Ensure alignment of cable tray to the deck penetration, aligned to the tie-in information from the panel vendor. | None | SEA | CSE | OPEN |  | None |  | None | None | Vendor | None | None | M07B |  | EC-M07B-L-N-TRAY-20004 | 10866c |  |  |  | SEA/KBR | None |  | None | None
Level 1 | Vendor to provide the final confirmation on tie-in information for electrical cables for RTU panels (Instrumentation/CSE related). | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-07B |  | EC-M07B-L-N-TRAY-20002 | 10867c | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Relocate JB (CXN-L-M07B-002) to port-side flange face of the column. | None | SEA | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-07B |  | LNO-215-01-M07B-003 LNO-215-01-M07B-004 | 10868c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Provide sub-tray to lighting fixture (LES-302-02-M07B-002). | Sub Tray provided. | SEA | ELE | RE-OPEN | 24/12/2025 | None |  | None | None | ELE | None | None | M-07B |  | LES-302-02-M07B-002 | 10869c |  | 12.0000000000000 | 2.00000000000000 | SEA/KBR | None |  | None | None | 27/12/2025 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 28/12/2025
None | For better maintenance access, adjust floodlight position upward, near stairway location (800mm up and 150mm closer to stairs location). | Light Fixture location updated. | SEA | ELE | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | SPL-M07B-00031 | 10870c |  |  |  | SEA/KBR | None |  | None | None
Level 2 | Pipe to be relocated to ensure lighting access space is available. | None | PB Ops | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-07B |  | LEM-331-02-M07B-005 | 10871c | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Ensure glanding and cable termination space is available with no obstruction. | Light Fixture location updated to ensure sufficient space provided for cable termination. | SEA | ELE | RE-OPEN | 24/12/2025 | None |  | None | None | ELE | None | None | M-07B |  | LES-302-05-M07B-001 | 10872c |  | 12.0000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 27/12/2025 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 28/12/2025
Level 3 | Light location to be adjusted accordingly due to nearby pipe. | Light fixture mounting type updated. | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-07B |  | LNO-215-08-M07B-003 | 10873c | 19/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | Delete the coaming as drain box is provided | None | KBR | PIP | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-07B |  | None | 20283c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | 1.Model Handling Route/ path on the piperack. 2.Instrument item to be removed from handling path. 3. shift telecom item away from handling route. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-05B |  | TEL-5516004 SPI-M05B-133 | 20284c |  |  |  | PB - Operation | None |  | None | None
1 | Model Handling Route/ path on the piperack. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-15 |  | None | 20285c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Delete the coaming as drain box is provided | None | KBR | PIP | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-14 |  | None | 20286c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Model Handling Route/ path on the piperack. | Handling route/volume is modelled | KBR | HAND | Pending PB Reply | 05/01/2026 | None |  | None | 09.01.25_B0RG_CLOSE | HAND | None | 9Jan2026_Cleared. | PPRK-M-16 |  | None | 20287c | 06/01/2026 | 3.00000000000000 | 0 | PB - Operation | True | 09/01/2026 | True | None | 08/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
1 | Model Handling Route/ path on the piperack. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-14 |  | None | 20288c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Shift the Escape route towards the STARBOARD direction till the staircase. (approx 490mm) | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-13B |  | None | 20289c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Electrical and Telecom to confirm the marked up items can be shifted towards the STARBOARD side for the easae of hadnling. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-13B |  | None | 20290c |  |  |  | PB - Operation | None |  | None | None
4 | Drain Gutter to size to be increased. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-10A |  | None | 20291c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Coaming to match/connect with Drain box and Handling route. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-15 |  | None | 20292c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1.Removable coaming with Drain Gutter to be provided . 2. quarter inch pipe cannot be used at this location due to Bundle handling. | None | KBR | PIP | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-10B |  | None | 20293c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Drain Gutter to match the dimension of removable coaming area / Handling route. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-10C |  | None | 20294c | 12/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Model Handling path on the PPRK. (refer both snapshot) | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | PPRK-M-07A/B |  | None | 20295c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Motor/gearbox handling simulation to be inline with the equipment. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20296c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Rotate the Light similar to Skid UC-1252001B | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | LEM-331-01-M07B-003 UC-1252001B | 20297c |  |  |  | PB - Operation | None |  | None | None
1 | Pipe support shall be made special support & beam clamp to be mounted on the pipe support. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | SP-M07B-09463 | 20298c | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1 | 1. Camera clashing with handling volume. 2. Speaker &amp; light are too close to handling obstruction. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | UST-M07B-101-004 , COR-5518127B , LEM-330-01-M07B-003 | 20299c |  |  |  | PB - Operation | None |  | None | None
1 | Add removable flange for the sprinkler line. (Dealing with bundle handling) | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20300c | 09/02/2026 |  |  | PB - Operation | None |  | None | None
1 | 1. Camera to be shifted, clashing with bundle handling volume. 2. Speaker &amp; buzzer to be elevated/ shifted, too close to bundle handling volume. (Typical for both M-07A/B) | None | KBR | TEL | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | CAM-5514031 , COR-5518127A , LSE-5518018A | 20301c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Handling route and Handling path mis-align with each other. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20302c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Monorail handling volume to be modelled throughout the transfer volume. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | None | 20303c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Padeye to be shifted as marked & obstruction volume to be updated. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12520219 | 20304c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Padeye to be shifted as marked & obstruction volume to be updated. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12520291 | 20305c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Handling obstruction , beam clamp , padeye to be deleted. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20306c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Valve Handling using Padeye to be modelled.SDV-1252009B-1 , SDV-1252009A-1 | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | SDV-1252009B-1 (M-07B) SDV-1252009A-1 (M-07A) | 20307c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Pipe line and sprinkler line to be shifted to clear space for Heater handling (too close). 2"-PC-J12N-2627-HC , 2"-P-H3N-2019-HC , 1"-FW-B7-1408-NI, 1"-FW-B7-1332-NI. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20308c | 09/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Add missing handling volumes. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20309c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handling path to be updated, clashing with pipeline. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20310c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Camera and light to be shifted away from valve handling volume. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | CAM-5514034 LNO-215-11-M07B-005 UST-M07B-301-008 | 20311c |  |  |  | PB - Operation | None |  | None | None
3 | Electrical cable tray to be re-routed to clear clash with valve handling volume. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | SDV-1252022B-1 | 20312c |  |  |  | PB - Operation | None |  | None | None
3 | Valve handling using A-Frame to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12521279 | 20313c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
3 | 1. Extend the monorail handling volume and hatch volume. 2. Electrical cable tray with monorail handling volume. 3.Shift the monorail stopper till the light fixture. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-07A/B |  | None | 20314c |  |  |  | PB - Operation | None |  | None | None
4 | Provide flange for sprinkler line , clashing during PCHE handling. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20315c | 09/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1. Crane pick up zone shall be shifted towards the PORT side to clear monorail support structure clash. 2. Light fixture, speaker &amp; emergency buzzer to be shifted away from crane pick up zone. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20316c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Handling path / obstruction volume to be modelled in line for Level 4. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20317c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Add flange to the sprinkler line as marked. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | P-UC-1252001B | 20318c | 09/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1. Valve handling to be re-studied, valve weight increased above 5MT. 2. Handling path clashing with piping to be cleared. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12311655 | 20319c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1. Provide flange at mark up location for valve handling. 2. The pipe support obstructing valve handling path, shift the support towards PORT side. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | HV-1231003C VALV-12311467 | 20320c | 09/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Change padeye to beam clamp. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12311179 | 20321c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve shall be handled by using A-Frame. A-Frame to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12310265 | 20322c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve shall be handled using padeye. Weight increase to more than 5MT | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12311420 | 20323c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve handling to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | SDV-1231070C-1 SDV-1231070D-1 | 20324c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Pipe line to be shifted towards STARBOARD side to clear space for chain hoist hook up on pad eye (12&quot;-P-H3N-2081-PP ).VALV-12311472 | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12311472 | 20325c | 11/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1.check to shift the line to clear Handling volume clash 16&quot;-P-G3N-2064-PP .(line too close). 2. rotate the padeye 90 deg in line to swing direction.HV-1231067C | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | HV-1231067C | 20326c | 11/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve shall be handled by using Pad eye, valve Weigth increased above 5 Ton. VALV-12310322 | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12310322 | 20327c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1. Padeye shall be rotated by 90 deg. 2. Electrical cable tray clash shall be cleared. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12310229 | 20328c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Padeye to be rotated by 90 Deg. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12311592 | 20329c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Pad eye to be rotated by 90deg. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12311574 HV-1231067D HV-1231003D. | 20330c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Pipelines to be shifted away from handling volume. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20331c | 11/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1.provide flange for spool removal during valve handling. 2.clear cable tray clash with swing volume.VALV-12311342 , HV-1231003D. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12311342 HV-1231003D | 20332c | 11/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Valve shall be handled using padeye. Weight increase to more than 5MT | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12311396 | 20333c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
4 | 1. Rotate the padeye by 90deg. 2.pipe line to be shifted away from handling swing volume 6&quot;-F-B9-XXX3-NI . | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | VALV-12311340 | 20334c | 11/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Missing Handling path to be modelled. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20335c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Shift the instrument item away from valve handling direction. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | AST-CO2-M07B-501-009 | 20336c |  |  |  | PB - Operation | None |  | None | None
5 | Model turning radius. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | None | 20337c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
5 | 1. Model scaffolding handling volume. 2. Shift the telecom item from handling route. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | PA-5517020 | 20338c |  |  |  | PB - Operation | None |  | None | None
5 | Scaffolding volume to be provided. BDV-1231002D | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-07B |  | BDV-1231002D | 20339c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Update handling path turning radius route and volume. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20340c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | INST JB JBI-1416-006 support SPI-M06-01001 to be relocate to avoid the clash with handling path | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | JB JBI-1416-006 SPI-M06-01001 | 20341c |  |  |  | PB - Operation | None |  | None | None
1 | Tubing FV-1233048B to be moved towards AFT side to provide the minimum clearance of 100mm from handling swing volume | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | FV-1233048B | 20342c |  |  |  | PB - Operation | None |  | None | None
1 | 1. Update the simulation study of compressor and motor using slings instead of spreader bar. 2. Simulation study to be in lower height position. Applicable for both compressor | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | UC-1233001A/B | 20343c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Gas detector post DS-S04-7-0745 to be removable type for maintenance of compressor motor. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | DS-S04-7-0745 | 20344c |  |  |  | PB - Operation | None |  | None | None
1 | Reserve the handling volume for heat exchanger removal. Applicable for UC-1233001A and B. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | UC-1233001A/B | 20345c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Steps to be removable during maintenance of compressor motor. | All 3 removalbe stools per compressor supplied by vendor is removable type. | None | MECH | Pending PB Reply | 04/01/2026 | None |  | None | 09.01.25_B0RG_CLOSE | HAND | None | 9Jan2026_Cleared. | M-06 |  | UC-1233001A/B | 20346c | 03/01/2026 | 4.00000000000000 | 0 | PB - Operation | True | 09/01/2026 | True | None | 07/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 07/01/2026
1 | Pipe support to be removable and ensure no clash with handling trolley during maintenance of compressor motor. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | UC-1233001A/B | 20347c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Model lifting lugs of top cover as per vendor drawing. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | V-1233002 | 20348c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipe support beam (Beam-6-6097) to be clear away from beam clamp for handling. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | Beam-6-6097 | 20349c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | 1. Model scaffolding volume for top cover access to remove. 2. Confirm with piping for the vessel trim valve removal prior for maintenance. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | V-1233002 | 20350c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Check the valve weight and update the A-Frame Length accordingly. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | VALV-12338630 VALV-12338617 | 20351c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Current control valve height is clashing with A-frame. The valve in 3D model height need to be align with vendor drawing. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | FV-1233048A FV-1233048B | 20352c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
1 | INST Tray IC-M06-S-I-TRAY-02002-TRAY-0007 to be modified away from handling dropzone volume | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | IC-M06-S-I-TRAY-02002-TRAY-0007 | 20353c |  |  |  | PB - Operation | None |  | None | None
2 | Handling radius to be added as per handling drawing. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20354c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Current valve height is clashing with lifting beam. The valve in 3D model height need to be update as per vendor drawing. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | XV-1233923A XV-1233923B XV-1233924D XV-1233923D | 20355c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Handling lifting beam and beam clamps to be align with valve center. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | OFBM-M06-2007-1MT VALV-12338230 | 20356c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
2 | INST cable Tray to be elevated as maximum for valve handling using A-Frame and discussed together with handling team. | None | None | CSE | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | IT-M06-S-I-TRAY-02012 IT-M06-S-S-TRAY-02013 | 20357c |  |  |  | PB - Operation | None |  | None | None
2 | Model handling transfer volume for valve using A-Frame. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | XV-1233924D XV-1233923B | 20358c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
2 Mezz | Light fixture to be relocated away from valve handling using hydraulic stacker. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | LNO-213-07-M06-002 | 20359c |  |  |  | PB - Operation | None |  | None | None
2 Mezz | Access Platform shall be removable type for valve handling using stacker. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | ACC PLTF-05 VALV-51350230 | 20360c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 Mezz | Handling Lift beam vertical column to be moved towards west to avoid the clash with tray. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | OFBM-M06-2103-3MT | 20361c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
2 Mezz | Three supports for the INST tray are located very near inbetween. Check and remove the support ISPT-M06-02269 to avoid the clash with beam clamp for valve handling. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | ISPT-M06-02269 | 20362c |  |  |  | PB - Operation | None |  | None | None
2 Mezz | Elevate the Handling Lift beam OFBM-M06-2105-3MT to match with staircase platform below. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | OFBM-M06-2105-3MT | 20363c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Provide the handling solution for the accumulator cylinder. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | UC-1233001A/B | 20364c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Add break-up flanges in Fire water line at marked location for removal during maintenance of Vessel Skid-2 chiller plate pack-A AFT side. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | 2"-FW-B7-1999-NI | 20365c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Update the simulation study of the chiller plate pack with deck trolley without clashing with Coaming. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20366c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Sampling box clash with handling path to be relocated. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | SC3-C2/ESP-12330126 | 20367c |  |  |  | PB - Operation | None |  | None | None
2 | Pipe to be moved south to avoid the clash with handling path. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | 10"-PC-E32N-8162-HC | 20368c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Permanent davit to be moved towards north to provide the better location for dropping the chiller plate pack from M06 to M04. Update the davit operational volume and drop zone volume to avoid the clash with INST Tray & ELE light. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20369c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2 | ELE light to be relocated away from handling drop zone of permanent davit. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20370c |  |  |  | PB - Operation | None |  | None | None
2 | Provide the removable handrail for handling the M06 Maintenance component to drop in M04 using permanet davit. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20371c | 01/03/2026 |  |  | PB - Operation | None |  | None | None
2 | Instrument item to relocate to clear clash with the plate pack handling path. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | SPI-M06-271 | 20372c |  |  |  | PB - Operation | None |  | None | None
2-Mezz | Handrail, kickplate and socket to update to removable type for chiller plate pack maintenance. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | OFHR-M06-000079 OFHR-M06-000080 | 20373c | 01/03/2026 |  |  | PB - Operation | None |  | None | None
2-Mezz | Monorail stopper to be relocated align with the bracing for trolley hoist approach. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20374c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2-Mezz | Piping to re-route as marked based on the latetst tie-in point to avoid the clash with handling pad eye structure. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | 6&quot;-F-B10-1747-NI 6&quot;-F-B10-0547-NI 4&quot;-RF-B9-0011-CC | 20375c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Update the simulation study of chiller plate pack A located at FWD side to be moved towards starboard side using trolley hoist. Then further transfer using Pad eye chain hoist and beam clamp chain hoist to avoid the clash with the existing pipe spool located at portside. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20376c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Hatch cover to be updated in 3D model instead of temporary beams and plating. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20377c | 01/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Handrail along with the kickplate to be removable type and presented correct naming at the selection tree. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20378c | 01/03/2026 |  |  | PB - Operation | None |  | None | None
3 | As discussed with PB operation team, due to the weight, pulling post to be deleted in 3D model. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20379c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handling obstruction volume to be align with hatch area. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | VALV-12330737 | 20380c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
3 | As discussed with PB operation team, due to valve weight lesser than 300kg, delete the lift beam. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | OFBM-M06-3014-1MT | 20381c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Sampling box to be relocated away for valve access and removal. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | SC3-C4/ESP-51350104 | 20382c |  |  |  | PB - Operation | None |  | None | None
3 | Add break-up flanges in the Fire water line for valve removal. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20383c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Provide the handling solution for Flow Element. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | FE-1233046 | 20384c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2-Mezz | Two Handrail to be removable for condensor plate pack maintenance and handling movement. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | OFHR-M06-000076 OFHR-M06-000077 | 20385c | 01/03/2026 |  |  | PB - Operation | None |  | None | None
2-Mezz | Model pulling post (supplied by vendor) for the condensor plate pack-B removal | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20386c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2-Mezz | Reserve handling volume for the actuator removal. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | MB-19799-01-04-04-00-14-150 | 20387c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
2-Mezz | Electrical light fixture and post to be relocated away for handling of actuator | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | LEM-327-03-M06-002 | 20388c |  |  |  | PB - Operation | None |  | None | None
3 | Add break-up flanges in the Fire water line for bundle removal. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | P-1233006A/B | 20389c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Pulling post location and design to be validated by structural for handling of bundle. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | PP-M06-3002-2MT PP-M06-3003-2MT | 20390c | 01/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Connect the handling way route and volume | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20391c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Pulling post located in escape path. Structural to consider the pulling post as flush type. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | PP-M06-3004-1MT | 20392c | 01/03/2026 |  |  | PB - Operation | None |  | None | None
3 | Filter removal volume and scaffolding access volume to be modelled. (Scaffolding volume height to be inline with filter removal volume height) | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | FT-1233003A FT-1233003B | 20393c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Pipe support trimmer beam to be deleted in permanent hatch opening area. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | BM-BR-WH200X35.9-erarchy BM-W200x22.5-IMMER-1 | 20394c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Model the handling volume for the pipe spool. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | 18"-PC-E3N-0474-NI | 20395c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Handrail to be removable for actuator valve SDV-1233001-1 handling. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | OFHR-M06-000200 | 20396c | 02/03/2026 |  |  | PB - Operation | None |  | None | None
4 | Extend the lift beam towards starboard side and relocate the beam clamp for valve handling. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | VALV-12330948 | 20397c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Add Loading / unloading area in Level-4 for valve handling as proposed. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20398c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Filter removal volume and scaffolding access volume to be modelled. (Scaffolding volume height to be inline with filter removal volume height) | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | FT-1233002A FT-1233002B | 20399c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Add break-up flanges in Fire water line at marked location for Equipment. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | P-5135001 | 20400c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Add break-up flanges in Fire water line at marked location for Equipment. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | P-1238001A/B | 20401c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Flange to be shifted as per markup to provide handling clearance for the equipment lifting. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | 6"-P-H6N-0715-HC | 20402c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Portable stool for access to be provided | Portable stool provided to access the filter screen | KBR | PIP | Pending PB Reply | 30/12/2025 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | ESP-51250009 | 1456c |  | 2.00000000000000 | 6.00000000000000 | PB - Operation | None |  | None | None | 02/01/2026 | 04/01/2026 | 06/01/2026 | 06/01/2026 | 04/01/2026 | 04/01/2026
1 | Coaming to be extended to include the strainers | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | None | 1457c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure that valve is provided on strainer drain - typical for hot water circulation pumps and hot water dump cooler pumps | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | ESP-51250009 | 1458c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Coaming to be extended to include the strainers | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | None | 1459c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
1 | FIT to be modelled | FIT-5125002 and FIT-5124003 are modelled. | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | FIT-5124003 FIT-5125002 | 1460c |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
1 | Tundish ND to be 2&quot; more than discharge line ND. Typical for all M15 tundish. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 4&quot;-DA-B22-2758-PP 4&quot;-DA-B22-2760-NI | 1461c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | I-DE-3010.2S-5125-944-S2N-001 Note 39 to be removed for VALV-51250090 since it is a ball valve. | None | None | PRO | OPEN |  | None |  | None | None | PRO | None | None | M15 |  | VALV-51250090 VALV-51240252 | 1462c |  |  |  | PB - Operation | None |  | None | None
4 | Valves and lines to be modelled as per P&amp;IDs. Module demarcations to be updated as necessary. I-DE-3010.2S-6825-944-S2N-002 I-DE-3010.2S-6825-944-S2N-003 | None | None | PRO | OPEN |  | None |  | None | None | PIP | None | None | M14 |  | None | 1463c |  |  |  | PB - Operation | None |  | None | None
5 | Utility connection block valve to be located as close as possible to nozzle. PB confirms that access is not required to be provided. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | V-5125001 | 1464c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Closed drain block valve to be located as close as possible to nozzle. PB confirms that access is not required to be provided. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | V-5125001 | 1465c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Hot water lines discharge to be lower than top of tundish to avoid hot water spillage. Verify with Safety if it should be away from Safety Path. Typical for Hot Water Tundish arrangement. | Line lowered and tundish size increased by 2" higher to avoid spillage. | KBR | PIP | Pending PB Reply | 05/01/2026 | None |  | None | None | PIP | None | None | M15 |  | DA-2760 W-0645 | 1466c |  | 1.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
5 | Size and position of the LG and LIT (LG higher than the equipment), tie-in points to be verified | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M15 |  | V-5125001 | 1467c |  |  |  | PB - Operation | None |  | None | None
5 | Access to be provided for the Utility Connection valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51250106 | 1468c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valves to be mounted directly on nozzle similar to VALV-51250096 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51250155 VALV-51250137 VALV-51250142 | 1469c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Gas detector to be provided as per P&ID Note | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | W-3067 | 1470c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valves to be arranged in horizontal to avoid dead leg | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51250518 VALV-51250053 | 1471c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valve to be arranged in horizontal to avoid dead leg | Valve moved to horizontal to avoid dead leg | KBR | PIP | Pending PB Reply | 05/01/2026 | None |  | None | None | PIP | None | dcn required | M15 |  | VALV-51250076 | 1472c |  | 1.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
4 | Check valve to be located above the deck and connect to the header above Level 5 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51250048 | 1473c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Low point drain to be provided or check feasibility of rerouting the line above Level 5 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 1"-HWU-B4-0002-HC | 1474c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Remove the vent valve on line CNI-0614 and replace with flange and blind, Add a vent connection with valve close to nozzle for line CNI-0613 and W-0268. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | V-5125003 | 1475c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Remove the vent valve and replace with flange and blind, Add a vent connection with valve close to nozzle typical with Punch 1476c. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | V-5124003 V-5125002 V-5124002 | 1476c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Provide slope at least 2% | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | CNI-0613 | 1477c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain valve and blind flange to be provided on the strainer | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | ESP-51250025/026 | 1478c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | PITs to be in horizontal | PIT and PDIT's are oriented in horizontal. | KBR | PIP | Pending PB Reply | 08/01/2026 | None |  | None | None | PIP | None | NO Piping DCN required | M15 |  | PDIT-5125001 (wrong TAG) PIT-5125044 | 1479c | 23/01/2026 | 0 | -1.00000000000000 | PB - Operation | None |  | None | None | 11/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
1 | Cleaning connection to be located between spectacle blind and exchanger | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | HWU-0015 | 1480c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valve is missing on analyser tapping | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | BG-0015 | 1481c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Model the FIT tags at the pressure connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | FE-5125008 FIT-5124006 | 1482c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Valve and lines to be modeled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51250726 HWP-0965 HWP-0966 HWP-0967 | 1483c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Drain to be changed to vent | Drain valve changed to vent. | KBR | PIP | Pending PB Reply | 05/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | HWU-0108 | 1484c |  | 0 | 2.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 08/01/2026
2 | Orient the drain valve to vertical straight from header | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | HWP-0073 | 1485c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Model the missing valve on bypass line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51250533 | 1486c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Position of the outlet of the hot water PSV vent location discharge to be verified with Safety | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | F-0523 | 1487c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valves to be mounted directly on nozzle | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | V-5124001 | 1488c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Utility connection block valve to be located as close as possible to nozzle. PB confirms that access is not required to be provided. | Isolation valve moved close to the nozzle | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | V-5124001 | 1489c |  | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
5 | Closed drain block valve and spectacle blind to be located as close as possible to nozzle. PB confirms that access is not required to be provided. | Drain valve and spectacled blind are move closed to the nozzle. | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | dcn required | M15 |  | V-5124001 | 1490c |  | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
5 | Model the analyser connection as per the vendor | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | V-5124001 | 1491c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Size and position of the LG and LIT (LG higher than the equipment), tie-in points to be verified | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M15 |  | V-5124001 | 1492c |  |  |  | PB - Operation | None |  | None | None
5 | Tundish to be above platform level | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | DA-2758 DA-3519 | 1493c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | P&ID to be updated, instead of four blind flanges, only two required. Verify how to add to isometric BOM for the two blind flanges. Penetration sleeve to be modelled. Support to be rotated to the other side. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | SW-0179 | 1494c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
None | Lines require commissioning vent (flange and blind only) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 12&quot;-SW-B23-0179-NI 16&quot;-SW-B23-0143-NI 16&quot;-W-B10-0638-NI 16&quot;-W-B10-0635-NI | 1495c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Drain valve to be added downstream of the check valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 18"-SW-B23-0132-NI | 1496c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | No sampling panel is required. Provide 300mm clearance between the tundish and the needle valve outlet to collect the sample. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | ESP-51240201 / 51240202 ESP-51240153 ESP-51240196 ESP-51240002 | 1497c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Move the flushing connection for the plate type exchanger (non classified area) as marked and provide a vent upstream of the valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | SW-0029 | 1498c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
PPRK | Ensure sufficient weld clearance between support and pipe weld | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | SP-M15-PRK-00871 SP-M15-PRK-05626 | 1499c | 16/01/2026 |  |  | PB - Engineering | None |  | None | None
2 | 1. Process to verify the size of the hose to reduce to 6&quot; as current 8&quot; hose is difficult to handle. 2. Evaluate to change the size of the Seawater inlet line flushing valve size from 1.5&quot; to 3&quot;. Typical for all classified and non classified PHE. | 1. PB Operations & PB Process confirmed earlier about the sizes of the hoses. Hence no change is required. (Refer PB Process weekly meeting #489) 2. PB Operations & PB Process confirmed earlier about the 1.5" flushing valve size. Hence no change is required. (Refer PB Process weekly meeting #489) | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M15 |  | VALV-51240209 VALV-51240082 | 1500c |  | 0 |  | PB - Operation | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
2 | Model the AIT panel | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | SW-1320 | 1501c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Change the location to an accessible level. Check the feasibility to relocate in any location of overboard line. Ensure sampling nozzle as per PB memo. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | SW-0150 | 1502c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valves to be place in horizontal | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51240077 VALV-51240370 VALV-51240079 | 1503c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valve and spectacle blind to be located close to the nozzle | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51240073 | 1504c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve to be modeled as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51210130 | 1505c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Remove the sample panel and make the line shorter as much as possible | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | CN-0701 | 1506c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Instrument air to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 1"-IA-B3-1202-NI | 1507c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Flame arrestor tag to be updated and flame arrestor to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | XSE-5121501 | 1508c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Provide 45deg cut downward | Vent to Atmosphere,Provided with 45deg cut downwards | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | F-0601 | 1509c |  | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
1 | Provide pipe sleeve for all FRP. Space available in accessway is 500mm, accepted by PB Operations | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | DA-2766 | 1510c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Piping location to be adjusted inside the coaming | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | SW-0604 | 1511c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Relocate the instrument away from the coaming | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M15 |  | PDIT-5111009 | 1512c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
1 | Model the motor above the filter. The motor should be accessible from the platform | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | FT-5111001E | 1513c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Volume to be modelled for reserving platform for filter access. Lighting fixture to be relocated. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | LES-313-03-M15-006 LEM-352-01-M15-013 | 1514c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Process to verify the arrangement of the modelled outlet lines compared to the P&amp;ID. P&amp;ID shows flow in one direction and modelled arrangement has the flow spread. | None | None | PRO | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 46&quot;-SW-B23-0126-NI 46&quot;-SW-B23-0134-NI 6&quot;-SW-B23-0020-NI 18&quot;-SW-B23-0132-NI 6&quot;-SW-B23-0081-NI | 1515c |  |  |  | PB - Operation | None |  | None | None
1 | Low point drain to be provided after the check valve | low point drain provided after the chack valve | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | VALV-51110161 | 1516c |  | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
1 | In P&ID min distance is mentioned. Process to verify the distance between tapping location and confirm if it is ok. | None | None | PRO | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 6"-SW-B23-0048-NI | 1517c |  |  |  | PB - Operation | None |  | None | None
1 | Provide drain on the downstream of the check valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51110160 | 1518c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Model the gas detector as shown in the P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | None | 1519c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Ensure the LG is visible from the ladder, Model the vents and drains for stand pipe and LGs on this tank. All LGs to be inside the coaming. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | LG-5112006-2 | 1520c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Extend the coaming to the drain valves. | coaming updated | KBR | STR | Pending PB Reply | 05/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | None | 1521c | 19/01/2026 | 1.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
3 | Drain pit to move to the marked location following the coaming update | 03-01-26-Drain pit (M01-L3-DP2-002) moved as per D90 comment | None | PIP | Pending PB Reply | 02/01/2026 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | NO PIPING DCN REQUIRED | M-01 |  | None | 1522c | 27/02/2026 | 1.00000000000000 | 5.00000000000000 | PB - Operation | True | 09/01/2026 | True | None | 05/01/2026 | 06/01/2026 | 11/01/2026 | 11/01/2026 | 06/01/2026 | 05/01/2026
3 | Evaluate providing a drain pit at this location if the mouse holes on the skids are closed. | 03-01-25-Addtional drainpit added as per D90 Commnet | None | PIP | Pending Seatrium Reply | 02/01/2026 | None |  | None | None | PRO | None | None | M-01 |  | None | 1523c | 27/02/2026 | 5.00000000000000 |  | PB - Operation | None |  | None | None | 05/01/2026 |  |  |  |  | 05/01/2026
3 | Step access to the skids to be studied and provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | None | 1524c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Provision of portable steps by vendor for valve access to be confirmed. | Awaiting a response from Vendor GDK | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M-01 |  | Z-5241001A | 1525c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
None | Valve to be relocated away from SDV actuator | 03-01-26- FV-5412012 Model updated based on latest vendor GA .SDV clearence avaialble from valve. | None | PIP | Pending PB Reply | 02/01/2026 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | NO PIPING DCN REQUIRED | M-01 |  | VALV-54120116 | 1526c | 27/02/2026 | 1.00000000000000 | 5.00000000000000 | PB - Operation | True | 09/01/2026 | True | None | 05/01/2026 | 06/01/2026 | 11/01/2026 | 11/01/2026 | 06/01/2026 | 05/01/2026
5 | Provide access for valve handwheel | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350366 | 1527c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Valve to be reoriented considering hose access and hose volume to be modelled. Update UC position to act as drain also. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350043 | 1528c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Flange and nozzle mismatch to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | P-5135001 P-0932 | 1529c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | UC to be upstream of the spectacle blind. To be verified the TIT and PDIT located upstream of the spec blind or to follow the P&amp;ID and be located downstream. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-51350004 VALV-51350027 | 1530c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Drain valve upstream of PSEs to be changed to vents | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350039 VALV-51350007 | 1531c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
7 | PB recommmend to locate PSE on horizontal. To check with vendor and Stress analysis and update if possible. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PSE-5412047 | 1532c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
7 | Instrument to be modelled and update the tag number | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | TG-5135002 | 1533c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Bolt removal to be verified | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | SDV-5135028-2 | 1534c | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Small bore supports to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1535c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Ensure sufficent weld clearance. Minimum 50mm. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PC-8352 | 1536c | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
5 | Spectacle blind to be relocated closer to exchanger. Can be placed downstream the TIT-5135028. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-51350003 | 1537c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Provide drain upstream of FO | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FO-5135007 | 1538c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Orientation and TP of sampling point to be confirmed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-51350103 | 1539c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model a reserve volume square box 500mm in front of LITs for maintenance space | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1540c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Handwheel orientation to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350354 | 1541c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | TG-5135001 pipe to be flat on the botton (Free draining pipe) 3&quot;-P-C6-0462-NI THE TG-5135001 AND PIT-5135025 SHALL BE READABLE FROM GLOBE VALVE. To bring the the TIT closer and the PIT Visor post to the side of the valve (VALV-51350306) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | TG-5135001 3&quot;-P-C6-0462-NI VALV-51350306 | 1542c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Utility connection to be made into drain | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1543c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Vent without valve to be flanged. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-51350027 | 1544c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Provide 5D downstream of 6&quot;-FG-E6N-0020-NI. Sampling panel to be relocated as marked. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1545c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Requirement for 10" valve bypass to be confirmed by Process | 10" bypass valve is required. Hence no change. | None | PRO | Pending Seatrium Reply | 08/01/2026 | None |  | None | None | PRO | None | None | M-06 |  | VALV-51350641 | 1546c |  | 0 |  | SEA/KBR | None |  | None | None | 11/01/2026 |  |  |  |  | 11/01/2026
None | Change to drain valves | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1547c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | PIT orientation to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1548c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Avoid elbows on the drain connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1549c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Provide clear access to SDV | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | SDV-5135031 | 1550c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | High point vent to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1551c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Tapping point for UC to be taken close to spectacle blind. PIT orientation to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PIT-5135023 | 1552c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
7 | NOte 5 - 5 PSV SHALL BE LOCATED AS CLOSE AS POSSIBLE TO THE HEAT EXCHANGER OUTLET NOZZLE. Verify if the actual position can be acepted. More than 25m distance (23m height) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PSV-5135008 | 1553c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Drain lines to be shorter | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PV-5135017-2 PV-5135017-3 | 1554c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Tilt valve 45deg for accessibility | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350342 | 1555c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
6 | Piping arrangement from branch to be above the header piping or provide a drain on the low point. Check possibility to avoid bend on header piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 3"-FG-E6N-0020-PP | 1556c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
6 | Drain valves to be taken straight down in vertical | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350206 VALV-51350207 | 1557c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | CIP clearance volume to be modelled ITEM 5.4.4 ET I-ET-3010.00-1200-940-P4X-005 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1558c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Confirm that side and bottom connection is acceptable considering P&ID Note 38 for top connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-51350325 6&quot;-FG-B10-0806-NI 8&quot;-FG-B10-0124-NI | 1559c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Change to top connection to clear access for manual valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 4"-FG-B10-0021-HC | 1560c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
6 | Instrument tie-ins to be changed to the other side of the FE for access. TIT-5135013 to be modelled. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FE-5135013 | 1561c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Confirm the location of the PSV is acceptable considering P&amp;ID Note 4. SDV-1231066 are on the M05 and PSVs on M06 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PSV-5135007A/B | 1562c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Upstream straight length to be verified, it is duplicated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FE-5135013 | 1563c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Corrosion coupon modelling to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | XE-5135001 XE-5135002 | 1564c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Ensure slope is provided on the line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1565c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Valve handwheel orientation to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1566c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Valve handwheel orientation to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12380015 | 1567c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Corrosion coupon modelling to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | XE-1238001 XE-1238002 | 1568c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Verify with Process regarding note 18 on P&ID not met | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | SDV-1238003 | 1569c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Removable spool to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FE-1238006 | 1570c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Valve handwheel orientation to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12380045 | 1571c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Ensure valve lever can be operated and provide space for LIT maintenance | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | LIT-1238001 | 1572c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Locate sampling valve as close as possible to the piping | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12380198 | 1573c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Verify with the vendor on the orientation of purge unit and update if required | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | ESP-51350106 | 1574c | 22/01/2026 |  |  | PB - Operation | None |  | None | None
None | 2&quot;-F-B10-0455-NI - TO be from the botton to collect the liquid condensate 2&quot;-F-B10-0421-NI - To be connected from the top Of line 4&quot;-F-B10-0054-NI | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | 4"-F-B10-0054-NI | 1575c | 25/01/2026 |  |  | PB - Operation | None |  | None | None
None | LG bottom tapping should be above the centre line of SDV | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | SDV-5135026 | 1576c | 25/01/2026 |  |  | PB - Operation | None |  | None | None
None | LIT to be connected on the stand pipe | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | LIT-5135011 | 1577c | 25/01/2026 |  |  | PB - Operation | None |  | None | None
None | Representationn of FG to be checked and updated in model | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | FG-5135001 | 1578c | 25/01/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate drain to marked position to maximise drainage from the line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | VALV-51350294 | 1579c | 25/01/2026 |  |  | PB - Operation | None |  | None | None
None | Line from M07B to Piperack to be connected | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | PC-0218 | 1580c | 25/01/2026 |  |  | PB - Operation | None |  | None | None
None | Check possibility to relocate the sample box closer to the sampling point as marked | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | ESP-53360121 | 1581c | 25/01/2026 |  |  | PB - Operation | None |  | None | None
None | Sample station connections to be modeled as per the type indicated in the P&ID. Typical punch for M07B sample station. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | ESP-53360121 | 1582c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
None | Purging connections on LP/HP Flare lines within module to be modelled as per P&amp;IDs I-DE-3010.2S-5412-944-S2N-009 I-DE-3010.2S-5412-944-S2N-010 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | None | 1583c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
None | Move the air distribution manifold closer to the column | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | PDA-M07B-E-02 | 1584c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
None | Duplicated line to be deleted | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 1585c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Review and update support trimmer | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | SS-M07B-0086987 | 1586c | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Bolt removal to be verified | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | FV-1231042D BDV-1231002D PDIT-1231010C | 1587c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Check if gaskets are added between the flanges. Vent to be updated to flange with blind | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | FV-1231042D | 1588c | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
None | Valve catalogue to be updated for angle valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | None | 1589c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
None | Utility connection to Pipe Rack to be modelled. Coupling to be deleted and directly welded as per Piping Spec | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | 1"-P-H3N-0848-NI | 1590c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
None | Modify supprt to provide access to handwheel | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 1591c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Space to be allocated for cleaning the filters. Typical for all PCHE. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 1592c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Tubing to be removed from model | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | None | 1593c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
None | Model the accessway volume and ensure it is clear of obstruction by air distribution manifold | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 1594c | 11/02/2026 |  |  | PB - Operation | None |  | None | None
None | Panel orientation to be facing accessway | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | BDV-1252014B-1 | 1595c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
None | Requirement for commissioning vent (without valve) to be verified | None | None | PIP | OPEN |  | None |  | None | None | PRO | None | None | M07B |  | 12&quot;-P-E6N-0634-NI 8&quot;-P-E6N-0642-NI 12&quot;-P-H3N-2082-PP 16&quot;-P-H3N-2082-PP 16&quot;-P-G3N-2064-PP 16&quot;-P-H3N-2081-PP | 1596c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Panel orientation to be facing accessway | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | PV-1231126-1 XV-1231012D XV-1231012C | 1597c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
None | Block valve to be located as close as possible to vessel nozzle. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1598c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
None | Ensure manway opening of FT-1238001A is clear of obstructions by cable trays and tray supports | None | None | CSE | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1599c |  |  |  | PB - Operation | None |  | None | None
None | Ensure sufficient clearance between LG and Structure. Provide cut-out/opening for LG visibility. Ensure valve levers are clear of interference. | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | LG-1238006A LG-1238006B | 1600c | 02/03/2026 |  |  | PB - Operation | None |  | None | None
None | Verify with Process that the location of the SDV is acceptable considering P&ID note stating max distance from nozzle to be 1.5D | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | SDV-1238009A SDV-1238009B | 1601c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Provide sufficient clearance from blind flange to blind flange | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 1602c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Check lighting location to avoid gap with pipe support to be very close. Evaluate options whether to use a different mounting or use a shorter light fixture. | Light fixture support type is changed to have better clearance with pipe support | None | ELE | RE-OPEN | 24/12/2025 | None |  | None | None | ELE | None | None | M-07B |  | LNO-215-09-M07B-004 | 10874c |  | 12.0000000000000 | 2.00000000000000 | SEA/KBR | None |  | None | None | 27/12/2025 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 28/12/2025
Level 4 | Relocate light to nearby beam, mounting type for light fixture to suit accordingly. | Light fixture is moved from handrail and mounted in Beam | None | ELE | RE-OPEN | 24/12/2025 | None |  | None | None | ELE | None | None | M-07B |  | LEM-331-04-M07B-007 | 10875c |  | 12.0000000000000 | 2.00000000000000 | SEA/KBR | None |  | None | None | 27/12/2025 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 28/12/2025
None | Sub trays to be modelled from main tray run towards the panel. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | PN-5520106-01 PN-5520106-02 | 10876c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Piping trimmer to be removed if not required. Electrical trimmer to be added based on requirement of sockets location. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | SKN-M06-404 SKN-M06-414 | 10877c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Miscellaneous tray supports to be modelled by STR, based on ELE input. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | None | 10878c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Guard rail design and model to suit mode of cable entry to heaters, adequate space to be provided. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | ET-M06-L-N-TRAY-45001 | 10879c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Check and confirm acceptability of flange proximity to lighting panel. Piping/safety to advise. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | PCC-5263006A | 10880c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Ensure bolting locations have proper space for installation against the vertical steel bracing behind the support assembly. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | PCC-5263006B | 10881c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Check and relocate speaker inwards of the guard rail. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | COR-5518XXXB | 10882c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Deck penetration model to be provided. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | EC-M06-L-E-TRAY-47511 | 10883c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Avoid pole mounted installations outside guard rail. Mount the floodlight to nearby column. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LNO-213-20-M06-001 | 10884c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Check and provide adequate welding space for installing the supports. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LNO-213-20-M06-003 LNO-213-20-M06-004 | 10885c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Adjust floodlight position, light coverage should not be blocked by column. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LNO-213-17-M06-006 | 10886c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Floodlight shall be mounted properly to nearby pipe support or structure. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LES-300-10-M06-002 | 10887c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Provide/extend sub-tray to lighting fixture. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LNO-213-13-M06-001 LNO-213-01-M06-005 LEM-327-03-M06-003 LEM-327-04-M06-010 | 10888c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Relocate JB for increased and improved accessibility for maintenance. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LNO-213-15-M06-003 CXN-L-M06-033 LNO-213-04-M06-008 | 10889c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | JB too close to handwheel. Adjust JB position and elevate to enable safe operation of handwheel. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | CXN-L-M06-048 | 10890c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Floodlight too close to pipe. Check and adjust the location of floodlight, position to nearby available structures/supports. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LNO-213-12-M06-004 | 10891c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
General | Update the penetration to open on the skid-side face, and extend the tray connection up to the vendor interface point. Typical for all 3 compressors. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | General | 10892c |  |  |  | SEA/KBR | None |  | None | None
Level 1 | JB currently inaccessible; vendor to relocate JB to the opposite side for accessibility. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | None | 10893c |  |  |  | SEA/KBR | None |  | None | None
Level 1 | Vendor handrails are overlapping with the interface cable ladder. This clash shall be resolved by the vendor without any change to the agreed interface point. | Awaiting a response from Vendor Siemens. | None | MECH | OPEN |  | None |  | None | None | Vendor | None | None | M-07B |  | IT-M07B-S-I-TRAY-01008 | 10894c | 17/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | The penetration and cable tray shall be rotated to align with the vendor interface cable ladder direction. Note: In the event the vendor cable tray routing is not yet finalized, KBR shall coordinate with the vendor before rotating the KBR cable tray and penetration. Applicable for 2 train. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | None | 10895c |  |  |  | SEA/KBR | None |  | None | None
Level 2 | Tie-in is missing. The cable tray and penetration shall be modelled and aligned with the vendor interface point. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | Z-UC-1231002D-03 Z-UC-1252002B-03 | 10896c |  |  |  | SEA/KBR | None |  | None | None
Level 2 | The penetration is blocked by a trimmer. The trimmer is not serving any purpose in this area and shall be checked and removed. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | Copy of SP-M07A-0222_TRIMMER_L2 | 10897c |  |  |  | SEA/KBR | None |  | None | None
Level 2 | FRP Grating penetrations shall be modelled to allow securing by bolting and shall not be obstructed by any structural members. (Applicable to all grating penetrations.) | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | I-M07B-S-PEN-022 | 10898c |  |  |  | SEA/KBR | None |  | None | None
Level 3 | Junction boxes shall be located on main or secondary beams wherever possible to avoid the need for additional trimmers. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | SPI-M07B-03002 | 10899c |  |  |  | SEA/KBR | None |  | None | None
Level 3 | Review the option to place three JBs on one support and move the support to a secondary beam to avoid three trimmers. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | JBC-1417-203 | 10900c |  |  |  | SEA/KBR | None |  | None | None
Level 3 | RIO Panel MCT and KBR penetrations shall be aligned in the same direction. The penetrations shall accommodate all related cables, including electrical and network cables. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | PN-5520107B | 10901c |  |  |  | SEA/KBR | None |  | None | None
Level 3 | The vendor RIO Panel MCT is not visible in the 3D model. Please check and update the model accordingly. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | PN-UC-1231002C-02 PN-UC-1231002D-02 | 10902c |  |  |  | SEA/KBR | None |  | None | None
Level 4 | Penetrations are overlapping with equipment support doubler plates. This needs to be evaluated and resolved, as it will impact bolting. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | JBIF-1417-228 JBI-1417-903 | 10903c |  |  |  | SEA/KBR | None |  | None | None
Level 4 | Relocate the junction box as per the provided mark-up. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | JBI-1417-901 | 10904c |  |  |  | SEA/KBR | None |  | None | None
None | KBR to model and incorporate the necessary supports in accordance with the standard KBR typical drawings for all 90 deg Bends(Typ). | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | IT-M07B-S-S-TRAY-03010 | 10905c |  |  |  | SEA/KBR | None |  | None | None
None | Electrical and instrument trays are running parallel. A combined support can be used to reduce material wastage and save weight. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | ISPT-M07B-02026 | 10906c |  |  |  | SEA/KBR | None |  | None | None
None | Pipe clashing with trays need to be resolved | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | IT-M07B-S-I-TRAY-01016-TRAY-0103 | 10907c |  |  |  | SEA/KBR | None |  | None | None
None | Tray dropper clashing with pipe support. To verify and clear. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M07B |  | None | 10908c |  |  |  | SEA/KBR | None |  | None | None
Level 1 | The trays can be combined from the instruments up to the point where the cable ladder is to be diverted. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | LIT-1231003C | 10909c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | The tubing's are modeled incorrectly. They should connect to the tapping point no to the flange. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | FIT-1231003C-1 FIT-1231003C-2 FIT-1231003D-1 FIT-1231003D-2 FIT-1231004C-1 FIT-1231004C-2 FIT-1231004D-1 FIT-1231004D-2 FIT-1252006B-1 FIT-1252006B-2 | 10910c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Move the transmitter 175mm towards West side. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | PDIT-1231001D | 10911c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Move the transmitter towards west direction to be clear from JB frame and the tubing trays should be combined. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | PDIT-1231007D PDIT-1231034D | 10912c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Add a cable tray connection from the penetration to the instrument sanction tray. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | PIT-1231003C | 10913c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | 1. For liquid service, the instrument connection should be lower than the tapping point. 2. For gas service, the instrument connection should be higher than the tapping point. These installation requirements shall be implemented in all applicable areas. Where this arrangement cannot be maintained, KBR shall notify PB and obtain confirmation prior to implementation. Typical to all Instruments and Tappings to be check for the Modules M10B | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | PIT-1231009C PIT-1231024D | 10914c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Tubing penetrations are to be modeled for the missing area. Tubing should not share penetrations with cable trays. Tubing trays and cable trays must have separate penetrations. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | PDA-M07B-NE-01 | 10915c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
General | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all Instruments, JB and valves M07B. Also the Tray which running close to the deck is should be checked and routed above the coaming height. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | General | 10916c | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Relocate the instruments to ensure access to the valve handles is not obstructed. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | FIT-1231130D | 10917c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
None | Tubing trays can be combined, and the cable penetrations can also be consolidated into one. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | None | 10918c | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Move the transmitter little bit to North side. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | None | 10919c | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
None | The penetration shall be modelled away from structural members with a minimum clearance of 50 mm to allow space for welding. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | I-M07B-T-PEN-429 I-M07B-T-PEN-431 | 10920c | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | The instrument shall be attached to the pillar, and the cable tray shall be rerouted to the top instead of deck level. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | FIT-1233047 | 10921c | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Instruments shall be mounted on nearby beams wherever possible to save support material, tray length, and cable length. (Applicable wherever a beam is available nearby.) | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | LIT-5135005 LIT-5135006 | 10922c | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Check the possibilities to relocate the transmitter in the marked location. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PDIT-1233023B | 10923c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
None | Change the support type to single stanchion | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PDIT-1233025A | 10924c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | The instrument tray is routed both below the deck and from the top. This shall be evaluated to confirm why the cables are routed in two directions. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PDIT-1233025B | 10925c | 27/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | JB access is blocked by tubing. The tubing shall be rerouted to maintain clear access. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PDIT-1233035B | 10926c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
General | Cable tray and tubing penenetration to be modelled where ever missing. Penetrations should be followed as per structural guidelines.Typical comment for M06. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PDIT-1233933A | 10927c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Combine both tube trays. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PIT-1233085A PIT-1233085B | 10928c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Move the transmitter towards south side. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PIT-5135022 | 10929c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Penetration to be moved away from the tapping point. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | LIT-1238005A | 10930c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Flushing rings to be modelled for all the capillary type of tappings. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | LIT-1238005A | 10931c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
General | Trimmers to be provided where ever the structure is not available. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | General | 10932c | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Relocate the transmitter to the accessible location. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PIT-1233076 | 10933c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Mount two Electrical junction boxes together on left side beam, and use the opposite (Right) side of the beam for instrument mounting. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PIT-1233103 | 10934c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate instrument to avoid penetration in access way. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | TIT-1233941A | 10935c | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Model the Missing connection tray. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | TIT-1233944A | 10936c | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Mount the transmitter in the near by column wherever possible. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | TIT-1233944D | 10937c | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Relocate the instrument away from the deluge system and mount it near the pole structure to minimize support material. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PIT-1233031B | 10938c | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 4 | Check with MH team for this clash or relocate the Instrument. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PDIT-1238016 | 10939c | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 7 | Relocate the transmitter away from handle. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | TIT-1238021B | 10940c | 06/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Relocate the Instruments as this very close to the Piping. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PIT-5135011 | 10941c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Relocate the Instrument to avoid clash with pipe | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PIT-1233037B | 10942c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 5 | Analyzer panel locations shall be finalized, and the cable trays for both cables and tubing shall be modelled accordingly. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-06 |  | PN-AIT-1233001 PN-MIT-1233006A PN-MIT-1233006B PN-MIT-1233006C PN-AIT-1233009 PN-MIT-1233007 | 10943c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
None | JB too low, mounting details to follow minimum mounting height based on typical details. Resolve position/location of JB. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | SPACE HEATER JB | 10944c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Resolve access/maintenance space issues between JB 'CXE-L-M06-352' & instrument air manifold 'PDA-M06-E-01'. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | PDA-M06-E-01 | 10945c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Combine 2 JBs in 1 support. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | CXN-L-M06-011 | 10946c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Vendor to model correctly the lighting fixture and supports. | None | None | ELE | OPEN |  | None |  | None | None | Vendor | None | None | M-06 |  | LEM-327-03-M06-001 | 10947c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Relocate light away from TIT-5135009. Observe adequate clearance between the 2 items. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LES-300-01-M06-002 TIT-5135009 | 10948c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Change mounting type of floodlight to avoid welding/constructability issues. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | LNO-213-05-M06-004 | 10949c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Relocate the junction box to provide clear access between the piping. Also the light to be elevate up to provide a space for CCTV as this proper location for CCTV coverage. Based on PB operations team's recommendation | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | CXN-L-M15-011 LNO-226-03-M15-001 | 10950c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | CCTV to be relocated to the Light location for best coverage. Based on PB operations team's recommendation | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | CAM-5514091 | 10951c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Relocate the CCTV | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | CAM-5514092 | 10952c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Lower the speaker height, as the current location is blocked by the piping support. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | COR-5518412A | 10953c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Relocate the Speaker as per mark up to avoid the blocking of the Light | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | COR-5518413A | 10954c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1M | Relocate BLE for better accessibility | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | BLE-5511312 | 10955c | 26/01/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Relocate the BLE | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | BLE-5511314 | 10956c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Relocate the CCTC as per mark up based on PB operations team feedback for the best coverage. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | CAM-5514093 | 10957c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate the TIT to provide space for the camera for the best coverage, as per PB Operations team feedback. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | TIT-5125020 | 10958c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Evaluate whether the CCTV should be installed on an L-type support or pole mount. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | CAM-5514094 SPP-M15-00007 | 10959c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Move the speaker to the edge of column | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | SPP-M15-00040 | 10960c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Move the speaker to the edge of column | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | CAM-5514095 | 10961c | 26/01/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate the camera | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | CAM-5514096 | 10962c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 4 | Telecom Secondary Tray, Penetrations and supports are missing. General for M15 Modules. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | PA-5517057 | 10963c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
None | M15 Modules skid related telecom items which need to be modelled by Vendor is missing. Vendor should provide the 3D model. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | P84-VEOLIA_EMISSAO_M15_25-09-01.nwd | 10964c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 5 | CCTV to be relocated as per the mark up for best coverage as per PB operation team feeback. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M15 |  | CAM-5514097 | 10965c | 26/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | The electrical interface for the RIO panel is via bottom entry; therefore, this shall be updated to use the instrument penetration for routing the cables into the RIO panel. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | EC-M15-L-N-TRAY-00008 | 10966c |  |  |  | SEA/KBR | None |  | None | None
Level 1 | The instrument tray interface alignment is missing. KBR and the vendor shall model and align accordingly. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | UE-5121501 | 10967c |  |  |  | SEA/KBR | None |  | None | None
Level 1 | Instrument tie-ins are missing for all pumps at Level 1. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | General | 10968c |  |  |  | SEA/KBR | None |  | None | None
Level 1M | FRP Grating penetrations shall be modelled to allow securing by bolting and shall not be obstructed by any structural members. (Applicable to all grating penetrations.) | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | I-M15-S-PEN-014 | 10969c |  |  |  | SEA/KBR | None |  | None | None
Level 2 | KBR to model and incorporate the necessary supports in accordance with the standard KBR typical drawings for all 90 deg Bends(Typ). | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | IT-M15-S-I-TRAY-01001 | 10970c |  |  |  | SEA/KBR | None |  | None | None
Level 2 | Electrical and instrument trays are running parallel. A combined support can be used to reduce material wastage and save weight. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | ESPT-M15-20133 | 10971c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
4 | Electrical cable tray to be shifted inside the platform for handling of exchanger bundle using pedestal crane. | None | None | EIT | OPEN |  | None |  | None | None | EIT | None | None | M-06 |  | ET-M06-L-E-TRAY-40208 | 20403c |  |  |  | PB - Operation | None |  | None | None
5 | Handrail to be removable for actuator valve SDV-1233051 handling. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-06 |  | OFHR-M06-000289, OFHR-M06-000288 | 20404c | 02/03/2026 |  |  | PB - Operation | None |  | None | None
5 | Improvise the actuator valve SDV-1233051 handling rotation simulation study. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | SDV-1233051 | 20405c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Add break-up flanges in the following lines highlighted in S3D item tags at marked location for valve handling using pedestal crane. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 3"-P-E6N-0162-NI, 4"-P-E3N-0405-NI, 4"-P-E3N-0412-NI and 3"-P-E6N-0545-NI | 20406c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Pipe support SP-M06-12906 to be removable type for valve VALV-12380071 handling using pedestal crane. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | SP-M06-12906 | 20407c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Gas detector AST-CH4-M06-501-102R post SPI-M06-506 to be removable type for equipment P-1238001A handling using pedestal crane. | None | None | EIT | OPEN |  | None |  | None | None | EIT | None | None | M-06 |  | AST-CH4-M06-501-102R SPI-M06-506 | 20408c |  |  |  | PB - Operation | None |  | None | None
5 | Ensure Heater platform extension should be removable type. Duplicate beams of layout model to be deleted. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 20409c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
5 | 1. Handling volume for heater to be updated. 2. Cable tray to be relocated away from handling volume | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | P-1233005B, P-1233005D, EC-M06-L-E-TRAY-46528 | 20410c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
6 | Add A-Frame handling volume for valve. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | VALV-12330494, VALV-12330727 and VALV-12330728. | 20411c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
6 | Handrail to be removable type for actuator valve SDV-1233044-1 handling. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | OFHR-M06-000323 and OFHR-M06-000313 | 20412c | 02/03/2026 |  |  | PB - Operation | None |  | None | None
6 | Valve changed to conventional type as per latest vendor information. Update the 3D model. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | FV-1233047 | 20413c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
6 | Valve handling to includes study of removing the pipes, showing the pipe flange, penetration size and sleeve height. Telecom Item, Cable tray with penetration to be relocated away from handling route. Pipe support SP-M06-21155 to be consider as removable type. Pipe spool handling using mobile handling devices to be modelled. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | VALV-12330493 | 20414c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
7 | ELE Light fixture to be relocated away. Valve to be shifted towards west to avoid the clash with starboard side line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | LNO-213-25-M06-005 VALV-51350011 | 20415c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
7 | Model A-Frame handling volume for valve. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | VALV-51350011 and VALV-12330938. | 20416c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
6, 7 | Hatch cover to be splitted into multiple pieces for Level-6 and Level-7. Use A-Frame for the handling study to reduce the pedestal crane approach lifting through hatch. KBR need to provide the list of items that require direct crane handling through full hatch opening. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20417c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
None | Valve handling using stacker is not feasible. Mainly due to not enough space around the valve and coaming obstruction the stacker leg. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | LV-1238004-1 VALV-12380044 VALV-12330787 VALV-12330055 VALV-12330946 VALV-12330773 VALV-12330786 SDV-1233009B VALV-12330834 VALV-12330019 VALV-12330718 VALV-12330671 VALV-12330676 VALV-12330847 VALV-12330835 SDV-1233012B VALV-12330040 VALV-12330947 | 20418c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
None | Control valve (height >3m) proposed handling solution is not feasible due to vendor size change. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | XV-1233923A XV-1233923B XV-1233923D XV-1233924D XV-1233924A XV-1233924B XV-1233924C XV-1233923C XV-1233920A XV-1233920B XV-1233920C XV-1233920D XV-1233922A XV-1233922B XV-1233922C XV-1233922D | 20419c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Valve handling can use beam clamp instead of stack. Add a spool above for valve handling. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | VALV-12330325 | 20420c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Available headroom not sufficient for handling of control valve TV-5124003-1 and further transfer to loading area is not possible due to the valve height. Further discussion to be required for this valve handling. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | TV-5124003-1 | 20421c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
1-Mezz | Electrical tray EC-M15-L-E-TRAY-15526 and Pipe 3"-DA-B22-0352-NI to be modified away from valve handling volume. | None | None | ELE | OPEN |  | None |  | None | None | PIP | None | None | M-15 |  | EC-M15-L-E-TRAY-15526 3&quot;-DA-B22-0352-NI | 20422c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Reserve handling volume for valve. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | VALV-51240163 | 20423c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Check the filter vendor drawing and update the handling solution. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | PD-M15-L1-92724, PD-M15-L1-92935 and ESP-51250020 | 20424c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Filter equipment model to be update along with motor in 3D model. Update swinging volume for davit opening with motor. Electrical tray to be modified away from davit swinging volume. | None | None | PIP | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | FT-5111001A/B/C/D/E | 20425c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
1 | 1. Access volume at platform to be modelled for filter access. 2. Relocate the light LEM-352-01-M15-013 and LES-313-03-M15-006 to provide clear access for filter maintenance. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-15 |  | None | 20426c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Proposed handling solution of A-Frame is not feasible. Beam clamp to be consider for the valve handling. For transfer, check the valve height. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | TV-5124005-2 | 20427c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
1-Mezz | INST Tray to be modified away from handling volume. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | IT-M15-S-I-TRAY-01008 | 20428c |  |  |  | PB - Operation | None |  | None | None
2 | 1. Reserve handling volume for the plate maintenance heat exchanger. 2. Relocate the INST item SPI-M15-02503 and Safety extinguisher Z-5428398. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | SPI-M15-02503 Z-5428398 | 20429c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Drop zone volume to be enlarged to align with handling path. Telecom Item to be relcoated away from drop zone volume. | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M-15 |  | COR-5518424B | 20430c | 27/01/2026 |  |  | PB - Operation | None |  | None | None
4 | INST Tray and ELE Tray to be modified away from handling volume. | None | None | EIT | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | IT-M15-S-S-TRAY-04002-TRAY-0312 EC-M15-L-E-TRAY-40501-TRAY-0072 | 20431c |  |  |  | PB - Operation | None |  | None | None
5 | Removable handrail to be splitted as marked to ensure the maximum length of handrail removable should be 2100mm. | None | KBR | STR | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | PultrudedHandrail_E3-7-0994 and PultrudedHandrail_E3-7-0993 | 20432c | 04/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Route the sampling line without pocket. Sampling box distance from sampling point to be confirmed with Instruments | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 1/2&quot;-PC-E3N-2390-CC SC9-I2/ESP-12380107 | 1603c | 09/01/2026 |  |  | PB - Operation | None |  | None | None
7 | TIT tagging to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | TIT-1238019 | 1604c | 09/01/2026 |  |  | PB - Operation | None |  | None | None
1 | P&amp;ID note 51 states that valves are to be disimilar type. Valve commodity codes to be verified. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12380109 VALV-12380039 VALV-12380113 | 1605c | 09/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Mismatching TPs to be updated by vendor. Ref. P&amp;ID I-DE-3010.2S-1238-944-S2N-003 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | Z-UT-1238001-01/02 | 1606c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Handwheels to be extended for platform access | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12388048 VALV-12388128 | 1607c | 09/01/2026 |  |  | PB - Operation | None |  | None | None
1 | 1" vent valve to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12338670 | 1608c | 09/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Spectacle blind to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | ESP-12380111 VALV-12380381 | 1609c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Include slope on these lines as per Note 8 of P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 20&quot;-PC-E3N-0732-HC 20&quot;-PC-E3N-0032-H | 1610c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | High point vent to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | 4"-W-B10-0594-NI | 1611c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Rotate Safety Shower toward AFT so shower will be closer to drain pit | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | Z-5434342 | 1612c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
3 | High point vent to be provided | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | W-0594 | 1613c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Valves to updated from ball to globe valves | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12380380 VALV-12380382 | 1614c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Valve and FO deleted on P&ID, to be deleted in model | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | VALV-12380169 FO-1238011 | 1615c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
6 | PSV size to be updated as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | PSV-1238003A | 1616c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Line to be top tapping to avoid accumulation of condensate at XV-1233033. | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M-06 |  | 10"-PC-E19N-0549-HC | 1617c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Pipe support to be updated | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | SE-M06-10226 SE-M06-103413 SP-M06-10201 SP-M06-10204 | 1618c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Confirm with vendor that location of equipment, considering height from lowest point of ball extraction to extraction equipment nozzle, for extraction of filter balls meets requirement for efficient extraction | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-UT-1233001A/B/C/D | 1619c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Routing to be updated and accessway height reduced TO 1950. PB confirms that reduced head height is acceptable. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | W-0594 | 1620c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Ensure valve opening is not blocked by pipe support. Valve to be reoriented. | Awaiting KSB vendor response. | None | MECH | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | B-5115003A/B/C | 1621c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Verify with vendor that PB memo is met regarding orientation. 2m to be available for maintenance access. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | CIP-12510005 CIP-51220003 CIP-51150101 CIP-51150102 | 1622c | 16/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Penetration sleeve size to be updated | Pipe penetration sleeve size updated | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | mo piing dcn required | M15 |  | 1"-CNI-B3-3162-NI | 1623c |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
3 | Line to be modelled in Piperack area | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 2"-CI2-B27-0002-NI | 1624c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Model the high point vents | High point vent valves are added | KBR | PIP | Pending PB Reply |  | None |  | None | None | PIP | None | no piping dcn required | M15 |  | B-5122001A/B | 1625c |  |  | 0 | PB - Operation | None |  | None | None |  | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026
1 | Strainer to be updated in 3D model and check with vendor to include the drain for the strainers. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | B-5122001A/B | 1626c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Consider this ball valve as the vent and provide a tie-in connection for the AIT | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51220292 | 1627c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Bolt removal to be verified, update the arrangement if required | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | None | 1628c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | High point vent to be provided. Typical for all 3 skids. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | None | 1629c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Update the FO in 3D model, TIT tagging to be updated. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | FO-5122001 TIT-5122906 | 1630c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | FRP flange support to be shortened for bolt access | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | None | 1631c | 23/01/2026 |  |  | SEA/KBR | None |  | None | None
4 | Provide the connections on the side, due to any dirt on the system will go back to the UD-5122001A/B/C, to try to connect the pipes on the side of the header. So any solids will be captured on the filters of the pump | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 6&quot;-HWU-B4-0022-HC 6&quot;-HWU-B4-0021-HC 6&quot;-HWU-B4-0020-HC | 1632c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Low point drain to be provided after the check valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | None | 1633c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | 1&quot;-IA-B3-1105-NI - Tie-in point to be changed. 1&quot;-W-B3-3681-NI - To be finished and connected to the Z-5122001 1&quot;-DA-B22-1572-NI - is on the wrong tie-in - Should be on the analyser drain connection. Missing the ESP-51220107 (Tank drain) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 1&quot;-IA-B3-1105-NI 1&quot;-W-B3-3681-NI 1&quot;-DA-B22-1572-NI ESP-51220107 | 1634c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Ensure clearance for accessing valve lever. Clear interfernce between structure and issued line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51150244 | 1635c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | LG vents and drains to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | LG-5115009-1 LG-5115009-2 LG-5115009-3 | 1636c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Gas detector to be modelled for vent line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | TQ-5115003 | 1637c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Move the isolation valve closer to the tank as marked | Valve moved closer to the nozzle as per the markup. | KBR | PIP | Pending PB Reply | 04/01/2026 | None |  | None | None | PIP | None | no piing dcn required | M15 |  | None | 1638c |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | None |  | None | None | 07/01/2026 | 08/01/2026 | 10/01/2026 | 11/01/2026 | 08/01/2026 | 07/01/2026
None | The orientation of the strainer is different for the typical pumps. Maintain the same orientation for the strainers. Removable volume to be clear of obstruction | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | None | 1639c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
None | Drains to be inside the coaming | coaming updated | KBR | STR | RE-OPEN | 06/01/2026 | None |  | None | None | PIP | None | no piing dcn required | M15 |  | None | 1640c | 19/01/2026 | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
3 | Orient the drain to vertical and make pipe shorter | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-51150261 VALV-51150255 | 1641c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Valves and FITs to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | FIT-5115003-1 FIT-5115003-2 FIT-5115004-1 FIT-5115004-2 VALV-51150269 VALV-51150275 | 1642c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Valve to be modelled | High point vent (VALV-51150539 ) modelled | KBR | PIP | Pending PB Reply | 05/01/2026 | None |  | None | None | PIP | None | None | M15 |  | VALV-51150539 | 1643c |  | 2.00000000000000 |  | PB - Operation | True |  | None | None | 08/01/2026 |  |  |  |  | 08/01/2026
4 | Sampling connection to be at accessible level. No panel, only isolation valve and needle valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | ESP-51150109 | 1644c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Model the CIP | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | CIP-1251005 | 1645c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
2 | Piping to be connected | Piping connected between the pipe rack and Module. | KBR | PIP | Pending PB Reply | 05/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | 2"-SW-B23-0007-NI | 1646c |  | 1.00000000000000 | 1.00000000000000 | PB - Operation | None |  | None | None | 08/01/2026 | 09/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
3 | Tie in connection to the Sea Water Treatment Package chemical lines, these valves should be non slam type. Check valves in series to be different from each other. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-12510654 VALV-12510657 VALV-12510674 VALV-12510747 VALV-12510663 VALV-12510671 UT-1251001 | 1647c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Missing line from the piperack until the UT-1251001(2"-CNI-B3-2255-NI) and valves VALV-12510746/747/748 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 2"-CNI-B3-2255-NI | 1648c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Provide drain connection downstream of the check valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | 2&quot;-CNI-B3-2249-NI 2&quot;-CNI-B3-2242-NI | 1649c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Sampling point to be deleted as per P&ID | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-12510072 | 1650c | 30/01/2026 |  |  | SEA/KBR | None |  | None | None
3 | Move the drain to AFT side | drain valve moved to the AFT side of the pipe | None | PIP | Pending PB Reply | 08/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | 8"-SW-B23-0067-NI | 1651c | 30/01/2026 | 0 | -1.00000000000000 | PB - Operation | None |  | None | None | 11/01/2026 | 11/01/2026 | 13/01/2026 | 13/01/2026 | 11/01/2026 | 11/01/2026
3 | Gas detector to be modelled for vent line | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | TQ-5115001 | 1652c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Extend the coaming up to the level instrument | Coaming upated | KBR | STR | RE-OPEN | 06/01/2026 | None |  | None | None | PIP | None | no piping dcn required | M15 |  | None | 1653c | 20/01/2026 | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
3 | Evaluate with Process the correct position for SDV and TIT - one is located on pump suction and one is on discharge. Model to be updated accordingly. | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M15 |  | SDV-5115001 SDV-5115020 TIT-5115001 | 1654c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
3 | Model the pressure tappings for the FE | None | None | PIP | OPEN |  | None |  | None | None | MECH | None | None | M15 |  | FE-5115001A/B | 1655c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | SWT vendor package to update the tie-ins for the utility lines Missing tie-ins to UT-1251001: 1-1/2&quot;-PW-B3-0107-NI - Pipe tag should be 2&quot;-W-B3-3768-NI 1-1/2&quot;-SA-B10-0147-NI 1-1/2&quot;-BG-B10-0734-NI 2&quot;-W-B3-0520-NI / 2&quot;-W-B3-3768-NI / verify, seems duplicated 2&quot;-SW-B23-1271-NI | Awaiting a response from Vendor Veolia | None | MECH | OPEN |  | None |  | None | None | MECH | None | None | M15 |  | UT-1251001 | 1656c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Access to the package is obstructed by the cage ladder | Awaiting a response from vendor HITACHI | None | MECH | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | UD-5122002A/B | 1657c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Height of step over into package is more than max allowed (300mm). Check with vendor the possibility to adjust coaming and drain pit by 250mm to allow step into package. | Awaiting a response from vendor HITACHI | None | MECH | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | UD-5122002A/B | 1658c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Relocate the cable tray and extend the access way. This the main entry to the package. | None | None | ELE | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | UE-5121501 | 1659c |  |  |  | PB - Operation | None |  | None | None
1 | Model a portable steps into the package at the marked locations. | Awaiting a response from Vendor Denora | None | MECH | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | UE-5121501 | 1660c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
None | FO is deleted from P&ID (ref. PUN #1566). To be approved by PB Process. | None | None | PRO | OPEN |  | None |  | None | None | SAF | None | None | M15 |  | FO-5111008A/E | 1661c |  |  |  | PB - Operation | None |  | None | None
None | Block valves to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | VALV-12510705 - 1&quot;-IA-B3-1071-NI VALV-12510668 - 1&quot;-IA-B3-0046-NI VALV-12510669 - 1&quot;-SA-B10-0020-NI | 1662c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
5 | Check with Safety if guardrail is required | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M15 |  | PSV-5124005A/B | 1663c | 04/02/2026 |  |  | PB - Operation | None |  | None | None
None | Sampling point to be relocated upstream of the branch. Isolation valve to be placed at accessible level. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | (ESP-51220103)VALV-51220067 1/2&quot;-W-B3-0575-NI | 1664c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
None | Coaming to be extended to include drain valve | None | KBR | STR | OPEN |  | None |  | None | None | PIP | None | None | M15 |  | None | 1665c | 04/02/2026 |  |  | PB - Operation | None |  | None | None
None | Rotate the drain valve 90deg within the coaming | Drain valve rotated within the coaming | KBR | PIP | Pending PB Reply | 06/01/2026 | None |  | None | None | PIP | None | dcn required | M15 |  | VALV-51240088 | 1666c |  | 1.00000000000000 | 0 | PB - Operation | None |  | None | None | 09/01/2026 | 10/01/2026 | 12/01/2026 | 12/01/2026 | 11/01/2026 | 11/01/2026
None | The vendor interface and KBR interface are located at different positions and need to be discussed and aligned with the vendor. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | TS-M15-TRAY-01 | 10972c |  |  |  | SEA/KBR | None |  | None | None
None | The interface for the instrument cable tray from the vendor opening is missing on the skid. Additionally, the KBR opening at the bottom is blocked by the skid plate. This requires clarification and alignment with the vendor to finalize the interface. (Typical for 3 Pumps) | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | FRESH-WATER-SKID-EI-A | 10973c |  |  |  | SEA/KBR | None |  | None | None
None | Interfaces are not aligned; the KBR Instrument penetration shall be relocated to match the vendor interface (applicable to two skids). | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | IT-M15-S-I-TRAY-04009 | 10974c |  |  |  | SEA/KBR | None |  | None | None
Level 1 | Evaluate the possibility to mount the transmitters on the wall in order to eliminate the support. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | PDIT-5111005c | 10975c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Move the PG towards East side for better access. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | PG-5111004D | 10976c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Relocate the equipment to the north side, in front of the tee. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | SPI-M15-171 | 10977c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Change the transmitter from pole mount to wall mount. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | PDIT-5124011 | 10978c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
General | Ensure that all sub-cable trays are properly terminated and connected to the termination point of instrument and the valves. Sub cable tray using proper cable ladder accessories (such as bends, tees, reducers, and drop-out fittings) to maintain continuity. This requirement applies to all Instruments, JB and valves M15. Also the Tray which running close to the deck is should be checked and routed above the coaming height. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | General | 10979c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Move the instrument south side to avoid clashing with tapping. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | PIT-5125024 | 10980c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Penetrations shall be modeled in accordance with structural guidelines to ensure sufficient space for welding. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | PDA-M15-E-02 | 10981c | 13/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 3 | Positioner in the wrong side. Rotate the positioner to the opposite direction. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | SDV-5115002 | 10982c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Relocate the Instrument for better access. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | PIT-5115001A PIT-5115002A PIT-5115020A PIT-5115002B PIT-5115020B PIT-5115004A PIT-5115004B PIT-5115009 PIT-5125004 | 10983c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Rotate the Instrument facing the tapping point and also move closer the Pipe beside. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | LIT-5115010 LIT-5115011 | 10984c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate the instrument as marked | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | PIT-5115001B PIT-5115004B | 10985c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | Move the Instrument towards east side. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | PIT-5115003B | 10986c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Relocate the instrument to nearest column. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M15 |  | LIT-5125005 | 10987c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Vendor to provide an updated model for penetration and tray supports based on KBR input. Punch applicable to both MV & LV tie-ins/interfaces. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | ET-M15-M-TRAY-05002 B-5125001A/B/C B-5125002A/B B-5125003A/B | 10988c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Vendor to update the tie-ins model. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | 22-Dec-25: The 3D model for basket strainer is by KBR. Vendor already provided the 2D drawing with tie in location. KBR need to reflect this in the 3D model. Not vendor action. | M15 |  | EC-M15-L-N-TRAY-10003 FT-5111001A/B/C/D/E | 10989c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Vendor to model package internal trays based on agreed tie-ins. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | ET-M15-L-N-TRAY-10016 | 10990c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Resolve access/installation space issues to MCT. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | EC-M15-L-N-TRAY-20001 | 10991c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Vendor to update/show internal package trays connected to agreed tie-ins. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | ET-M15-L-N-TRAY-20022 Z-5122001 FRESH WATER CHLORINATION UNIT | 10992c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Vendor to model package internal trays based on agreed tie-ins and KBR input. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | ET-M15-M-TRAY-30004 ET-M15-M-TRAY-30005 UD-5122002A/B FRESH WATER MAKER FOR OIL DILUTION | 10993c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Vendor to provide the required deck penetrations model. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | EC-M15-L-N-TRAY-30017 | 10994c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Resolve access issues for lighting fixture. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LEM-353-01-M15-005 | 10995c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 1 | Provide/extend sub-tray to lighting fixture. Resolve spacing issues with nearby Instrument tray. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LES-313-01-M15-001 | 10996c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Check possibility of mounting light to pipe support, to avoid pole mounted lights installed outside guard rails. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LEM-353-01-M15-002 | 10997c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
None | Mount floodlight to nearby pipe support. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LNO-226-04-M15-001 | 10998c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Adjust location of light as marked in punch reference model snapshot. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LEM-353-02-M15-002 | 10999c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
None | Adjust location of floodlight as marked in punch reference model snapshot. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LNO-226-06-M15-003 | 11000c | 26/02/2026 |  |  | SEA/KBR | None |  | None | None
Level 2 | Adjust location of floodlight as marked in punch reference model snapshot. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LNO-226-10-M15-004 | 11001c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Lighting too close to cage ladder, to provide adequate clearance between 2 items. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LEM-353-05-M15-002 | 11002c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Resolve JB access issues by adjusting floodlight location as marked in punch reference model snap. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LNO-226-20-M15-001 | 11003c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Resolve JB access issues against guard rail. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | CXE-L-M15-228 | 11004c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Resolve JB access issues against guard rail. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M15 |  | LNO-226-17-M15-002 | 11005c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | 125A socket to be relocated from L1 to L4, based on PB operations recommendation, as indicated in punch reference model snap. | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-06 |  | SKN-M06-425 | 11006c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Specifically for only valve PV-1254050 which weight more than 5mT, handling is presented with direct lifting by crane is rejected. PB operation will use scaffold for handling and place on deck before using the crane for lifting. The floor SWL need to have sufficient SWL for valve to place on the floor. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | PV-1254050 | 20433c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
None | Transferred from Parking Lot #2002: PB has raised a concern that the possibility of someone missing the correct route for transporting the valve is high, as there are no floor indications. Operations highlighted that, in practice, we do not have a quick way to identify the SWL for each floor. For example, on M-02, the correct route is on the starboard side, but there is a possibility that the valve could be swung toward the port side, where the handling path SWL is much lower. Other example (M-05 and M-05B) is shown in Snapshot 3, where there is a possibility of operational handling moving toward the interconnection area. (Corrected comment: PB is only requesting to swap the handling route for specifically M-02 only. Preference is the valve swing to the port side which is facing the handrails side.) | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-02 |  | None | 20434c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
None | Transferred from Parking Lot #2003: Vendor 3D model (UC-1231001A/B/C) missing terminal box door opening swing volume. It will clashing with handrail. | None | None | ELE | OPEN |  | None |  | None | None | HAND | None | None | M-05 |  | UC-1231001A/B/C | 20435c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
None | Transferred from Parking Lot #2005: PB highlighted concerns regarding safety issues with the current plan to install the temporary monorail. Lifting it directly by crane at a high elevation poses a hazard due to potential swinging during installation. Further discussion is required, and the installation method must be reviewed and approved by PB Safety. | None | KBR | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-05/M-05B |  | None | 20436c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
None | Transferred from Parking Lot #2007: M-02: KBR to provide simulation step by step how to remove the valve using a manual stacker. M-04, M-10A: control valves handling with manual stacker (snapshot 2) Gen: Typical handling method to be provided. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | Gen<br>M-02<br>M-04<br>M-10A |  | None | 20437c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
None | Transferred from Parking Lot #2010: Valve Handling – VALV-12330085: Current plan: Access platform to be removed, lift with beam clamp, place at deck Level-2 Mezzanine, then move via main route. (refer snapshot 1) PB request: Evaluate converting platform to fixed type; valve to be handled over access platform and dropped at safety shower location. (refer snapshot 2) Impact: KBR noted space constraints for relocating safety shower and additional lifting beam for beam clamp is required. | None | None | HAND | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | VALV-12330085 | 20438c | 21/02/2026 |  |  | PB - Operation | None |  | None | None
None | Transferred from Parking Lot #2011: PB highlighted to show the saddle for the plate pack maintenance inside the vendor 3D model, currently missing inside the overall P84/85 3D model. Typical comment for all chiller and condenser plate pack. | Awaiting a response from Vendor MAYEKAWA | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | None | 20439c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
None | Transferred from Parking Lot #2013: PB highlighted to reroute a portion of vendor tubing (MB-19799-01-04-03-80-007:1) further inside the skid to prevent interference with the chiller plate pack during maintenance. | Awaiting a response from Vendor MAYEKAWA | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-06 |  | MB-19799-01-04-03-80-007:1 | 20440c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
None | Transferred from Parking Lot #2016: PB raised a concern that the davit swing volume from the vendor’s equipment skid is obstructing the permanent gateway of the access ladder. In addition, the 3.65 m handrail needs to be modified or segregated to provide clearance for handling, as shown in the markup snapshot, due to safety concerns about removing the total handrail. However, KBR’s PRE mentioned that the fabrication drawing has already been released, and any further changes will need to be further discuss with the vendor. Vendor Davit Tag number: /P84_STRU_M15_UFU/SECONDARY_DAVIT | Awaiting a response from Vendor Veolia | None | MECH | OPEN |  | None |  | None | None | HAND | None | None | M-15 |  | P84_STRU_M15_UFU/SECONDARY_DAVIT | 20441c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Add a note on M07B Safety Layout to indicate that escape route is shown in M07A | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-07B |  | NA | 40001c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Clear obstruction from escape route | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | NA | 40002c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Clear clash of telecom panel with primary escape path | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07b |  | NA | 40003c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Clear clash of pipe support with primary escape path | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | NA | 40004c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Clear clash of instrument cable tray with secondary escape path near stairs | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07b |  | NA | 40005c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Quarter pipe to be modelled in the escape path between M-04 and pipe rack (M-07B | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | NA | 40006c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Clear clash of instrument cable tray support with escape route | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07b |  | NA | 40007c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Push button stand clash with escape route to be cleared | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M07b |  | NA | 40008c |  |  |  | PB - Operation | None |  | None | None
Level 5 | Link between M-07A and M-07B at Level 5 (PS and SB) to be modelled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-07B |  | NA | 40009c | 21/01/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | Fire hose reel box clash with escape path to be cleared | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | NA | 40010c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Re-orient hydrant to correct orientation to clear operation volume | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | H-5423057 | 40011c | 15/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Move Z-5428155 (Fire Extinguisher) closer to the coaming and escape route | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | Z-5428155 | 40012c | 15/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Relocate fire extinguisher outside the structure | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | Z-5428156 | 40013c | 15/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Update 2D Safety Layout to match 3D model | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M07b |  | NA | 40014c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Tubing to be rerouted to clear obstruction to safety shower | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-07B |  | NA | 40015c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Fire extinguisher to be relocated away from dropzone | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | Z-5428437 | 40016c | 15/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Remove handling volume to clear clash with hydrant | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | H-5423059 | 40017c | 15/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Support to be re-oriented by 180deg (AFT direction) | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | H-5423060 | 40018c | 15/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Shift extinguisher towards aft to give clearance between support and the column | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | Z-5428158 | 40019c | 16/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Support for fire extinguisher cabinet to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | Z-5428159 | 40020c | 16/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Move the fire extinguisher to clear hatch volume | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07b |  | Z-5428161 | 40021c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Equipment support to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | Z-5434025 | 40022c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Support to be re-oriented behind the hydrant | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | H-5423062 | 40023c | 16/02/2026 |  |  | PB - Engineering | None |  | None | None
3 | Equipment supports to be aligned | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | Z-5428164 | 40024c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
3 | Equipment support to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | Z-5434026 | 40025c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
4 | Ensure hydrant is clear of handling route | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | H-5423064 | 40026c | 17/02/2026 |  |  | PB - Engineering | None |  | None | None
4 | Ensure equipment is clear of handling route | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | Z-H-5423064 | 40027c | 17/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | 1. Evaluate reorienting hydrant 45deg similarly to M07A to avoid interference with hydrant operating volume. 2. Operating volume to be at front of hydrant. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | H-5423065 | 40028c | 17/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Equipment support to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | Z-5428427 | 40029c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
5 | Ensure equipment is clear of handling route | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | Z-5428438 | 40030c | 17/02/2026 |  |  | PB - Engineering | None |  | None | None
5 | Ensure equipment is clear of handling route. Equipment support to be aligned. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | Z-5434028 | 40031c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
1 | Cable tray too close to ladder rungs | None | None | CSE | OPEN |  | None |  | None | None | CSE | None | None | M-07B |  | IC-M07A-S-I-TRAY-01015 | 40032c | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Support structure on access platform to be updated to clear obstruction in front of ladder | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 40033c | 18/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Electrical tray to relocated away from ladder | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-07B |  | EC-M07B-L-E-TRAY-10524 | 40034c | 19/02/2026 |  |  | PB - Engineering | None |  | None | None
1 | Telecom equipment to be moved away from ladder access area | None | KBR | TEL | OPEN |  | None |  | None | None | TEL | None | None | M07B |  | PA-5517017 LES-302-02-M07B-004 | 40035c | 30/01/2026 |  |  | PB - Operation | None |  | None | None
1 | Equipment to be moved away from ladder access area | 8/1/26 - UST-M07B-101-008 is a F&G item and to be resolve by Safety | None | PIP | OPEN |  | None |  | None | None | CSE | None | None | M07B |  | UST-M07B-101-008 | 40036c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
2 | Kickplate to be extended across the gap - typical punch for M07B | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-07B |  | None | 40037c | 19/01/2026 |  |  | PB - Engineering | None |  | None | None
3 | Handrail to be provided | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-07B |  | None | 40038c | 19/01/2026 |  |  | PB - Operation | None |  | None | None
4 | Handrail to be updated considering bracing is temporary | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-07B |  | None | 40039c | 19/01/2026 |  |  | PB - Engineering | None |  | None | None
PPRK | Handrails to be modelled on Ultrasonic Flowmeter access platform and cross over platform at end of Piperack | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-07B |  | None | 40040c | 19/01/2026 |  |  | PB - Engineering | None |  | None | None
Level 1 | Handrails to be modelled. Missing in Model. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-07B |  | None | 40041c | 19/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Handrail to be modelled missiong near the piperack - to be modelled | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-07B |  | None | 40042c | 19/01/2026 |  |  | PB - Operation | None |  | None | None
Multilevel | Valve catalogue to be updated and handwheels to be modelled correctly. For example: VALV-12312525 - Turn 180 ° - Equal to M07A | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | General | 40043c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
Multilevel | Piping to check with Structure to fill the gap between column and the platform and provide kick plate/handrail if required. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | General | 40044c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Rotate elbow to move the PSV downstream line closer to the column to provide more space between handrail and the pipes | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | PSV-1231102D | 40045c | 18/02/2026 |  |  | SEA/KBR | None |  | None | None
Multilevel | Review possibility of rotating the handwheel to the SB side for better access (M-07B). | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | VALV-12312525 | 40046c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | Update instrument valve with remote panel to have more gap between pipes (M-07B). | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | XV-1252004B | 40047c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | Review to relocate valve outside the gap between the coaming of piperack and M-04, since no drainage is available in the infil area. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | VALV-51350290 | 40048c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | Re-orient drain valve to have obstruction fee acess | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | VALV-51351602 | 40049c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Coaming across handling path to be removed and modified to stop at the gutter with a 29mm overlap on the gutter. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 40050c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | Model the coaming to extend upto the gutter with a 29mm overlap. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 40051c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate the air distribution manifold closer to the column and rotate by 90 deg. Add tubing support and inion evry 6m length of tubing run. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | PDA-M07B-E-07 | 40052c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
None | Penetration sleeve height and sealant type to be reviewed with Safety an dmodel to be fixed | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 40053c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
None | Relocate lighting junction box to have clear gap to view LG | None | None | ELE | OPEN |  | None |  | None | None | ELE | None | None | M-07B |  | CXN-L-M07B-006 | 40054c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Coaming to be removed along the secondray escape paths as marked | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 40055c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Coaming to be modified to stop at the column flange and rest of the coaming to be deleted. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | None | 40056c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | TP-1252-8230/8130 line connection to this TP point should not have any flanges along the line. This is for IGC conditioning skid A/B. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | TP-1252-8230 | 40057c | 22/02/2026 |  |  | PB - Engineering | None |  | None | None
Level 2 | Missing 3% slope - Check the slope for these lines. 3&quot;-DA-B9-0234-NI 3&quot;-DA-B9-3314-NI 3&quot;-DA-B9-0119-NI 3&quot;-DA-B9-1420-NI | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | 3&quot;-DA-B9-0234-NI 3&quot;-DA-B9-3314-NI 3&quot;-DA-B9-0119-NI 3&quot;-DA-B9-1420-NI | 40058c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Review the tapping orientation of branch pipe to the header. Preferred is vertical / 45 deg orientation instead of side connection. Check to modify the header to remove short spool between elbow and tee. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | 12"-DA-B9-1455-NI | 40059c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
None | 1. To be tapped off near the discharge cooler as per the Note 8. Review with process and model to be updated. PIT-1252044B TIT-1252014B Note 8 2. Review with instrument to confirm on the orientation. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A/B |  | PIT-1252044B TIT-1252014B Note 8 | 40060c | 23/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Relocate instrument panel to give access to the valve operation | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | PIT-1231010C? | 40061c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Valve handwheel to be updated to the correct orientation | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | VALV-12311226 | 40062c | 23/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Move instrument stand and the trays towards forward to provide clear access and avoid tripping. | None | None | CSE | OPEN |  | None |  | None | None | INST | None | None | M-07B |  | None | 40063c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Check bolt retrieval clearance for check valve and the type of check valve | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | VALV-12311276 | 40064c | 23/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Valve lever orientation to be ratated 180 deg to provide access from accss path | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | VALV-12311552 | 40065c | 23/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Sample connection line to be modelled | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | VALV-53360116 | 40066c | 23/02/2026 |  |  | PB - Operation | None |  | None | None
Multilevel | PSV Downstream lines to have line stop | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | General | 40067c | 23/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Extinguisher volume to be modeled with 2.1m height - typical for M02 Extinguishers | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-02 |  | Z-5428017 Z-5428018 Z-5428019 Z-5428020 Z-5428021 Z-5428022 Z-5428023 Z-5428024 Z-5428025 Z-5428026 Z-5428027 Z-5428028 Z-5428029 Z-5428030 Z-5428031 Z-5428032 Z-5428033 Z-5428034 Z-5428035 Z-5428036 Z-5428439 | 40068c | 20/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Extinguisher volume to be modeled with 2.1m height - typical for M04 Extinguishers | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | Z-5428037 Z-5428038 Z-5428039 Z-5428040 Z-5428041 Z-5428042 Z-5428043 Z-5428044 Z-5428045 Z-5428046 Z-5428047 Z-5428048 Z-5428049 Z-5428050 Z-5428051 Z-5428052 Z-5428433 | 40069c | 06/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Extinguisher volume to be modeled with 2.1m height - typical for M11 Extinguishers | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M11 |  | Z-5428296 Z-5428297 Z-5428298 Z-5428299 Z-5428300 Z-5428301 Z-5428302 Z-5428303 Z-5428304 Z-5428305 Z-5428306 Z-5428307 Z-5428308 Z-5428309 Z-5428310 Z-5428311 Z-5428312 Z-5428313 Z-5428314 Z-5428315 Z-5428480 | 40070c | 13/02/2026 |  |  | PB - Engineering | None |  | None | None
None | Flare line from sample station to be connected. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | F-0051 | 40071c |  |  |  | PB - Operation | None |  | None | None
Level 1 | To connect piping 2027 and 2031. Check pipe support. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 30001c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 5 | To ensure consistency between P&amp;ID and 3D model for FT-1233002A. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FT-1233002A | 30002c |  |  |  | PB - Operation | None |  | None | None
Level 5 | Connection mismatch line 2048. Check pipe support Nozzle is missing 2048. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. Check pipe support. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 30003c |  |  |  | PB - Operation | None |  | None | None
Level 5 | To resolve dry spot for FT-1233002A and to add PFP for this vessel. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FT-1233002A | 30004c |  |  |  | PB - Operation | None |  | None | None
Level 5 | To solve dry spot for P-1235001A To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation Check pipe support. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1235001A | 30005c |  |  |  | PB - Operation | None |  | None | None
Level 5 | Obstruction of valve VALV-12330619 and bottom of vessel to be deluged for P-1235001A To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1235001A | 30007c |  |  |  | PB - Operation | None |  | None | None
Level 5 | Obstruction of valve, dry spot and bottom of vessel to be deluged for P-1235001B To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1235001B | 30008c |  |  |  | PB - Operation | None |  | None | None
Level 5 | Obstruction of valve, dry spot and bottom of vessel to be deluged for P-1235001C To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1235001C | 30009c |  |  |  | PB - Operation | None |  | None | None
Level 5 | Obstruction of valve, dry spot and bottom of vessel to be deluged for P-1235001D To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1235001D | 30010c |  |  |  | PB - Operation | None |  | None | None
Level 5 | To cover the shell of the equipment P-1238001A and the saddle. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. To update the line number of this pipe for this equipment. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1238001A | 30011c |  |  |  | PB - Operation | None |  | None | None
Level 5 | Spray obstructed by F&G. To clear | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 30012c |  |  |  | PB - Operation | None |  | None | None
Level 5 | To cover the shell of the equipment P-1238001B and the saddle. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. To update the line number of this pipe for this equipment. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1238001B | 30013c |  |  |  | PB - Operation | None |  | None | None
Level 5 | To cover the shell of the equipment P-5135001 and the saddle. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. To update the line number of this pipe for this equipment. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-5135001 | 30014c |  |  |  | PB - Operation | None |  | None | None
Level 4 | To cover dryspot of the equipment P-1233001A and the saddle. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. To update the line number of this pipe for this equipment. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233001A | 30015c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Support header of piping SP-M06-119323 is obstructing spray to P-1233001A. Please check header is also missing support. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | P-1233001A | 30016c |  |  |  | PB - Operation | None |  | None | None
Level 4 | To cover dryspot of the equipment P-1233001B and the saddle. Tp update line number. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. To update the line number of this pipe for this equipment. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233001B | 30017c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Please check header is missing support for P-1233001B. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | P-1233001B | 30018c |  |  |  | PB - Operation | None |  | None | None
Level 3 | To improve coverage for FT-123303A and model PFP for skirt. Missing piping support. Clear piping obstruction. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FT-123303A | 30019c |  |  |  | PB - Operation | None |  | None | None
Level 3 | To improve coverage for FT-123303B and model PFP for skirt. Missing piping support. Update line number. Clear piping obstruction. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FT-123303B | 30020c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Update P&ID tag for equipment repeated FT-1233003A to B. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 30021c |  |  |  | PB - Operation | None |  | None | None
Level 3 | P-1233002A - check structural obstruction on top. Cover dry spot. Missing support. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233002A | 30022c |  |  |  | PB - Operation | None |  | None | None
Level 3 | P-1233002B - check structural obstruction on top. Cover dry spot. Missing support. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. Update line number based on P&amp;ID. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233002B | 30023c |  |  |  | None | None |  | None | None
Level 3 | P-1233004 - dry spot to be covered. Saddle to be covered. Nozzle projection obstructed by Sructure. Missing deluge pipe support. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233004 | 30024c |  |  |  | PB - Operation | None |  | None | None
Level 3 | P-1233006A -dry spot to be covered. Saddle to be covered by spray/PFP. Valve obstruction to be checked. Clashing to be checked near PIT. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. Update line number based on P&amp;ID. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233006A | 30025c |  |  |  | PB - Operation | None |  | None | None
Level 3 | P-1233006A - FW-2064 line needs to be connected. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | P-1233006A | 30026c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | P-1233006A - Piping cannot be over the handrail and causing obstruction to access route, to shorten deluge pipe. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233006A | 30027c |  |  |  | PB - Operation | None |  | None | None
Level 3 | P-1233006B- -Dry spot near shell needs to be covered. Saddle to be covered by spray/PFP. Piping support to be shifted to prevent obstruction. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. Update line number based on P&amp;ID. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233006B | 30028c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Deluge nozzle clashing to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 30029c |  |  |  | None | None |  | None | None
Level 3 | P-1233006B - FW-2238 line needs to be connected. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233006B | 30030c |  |  |  | PB - Operation | None |  | None | None
Level 3 | P-5135002 - Obstruction of deluge piping header. Saddle to be covered. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-5135002 | 30031c |  |  |  | PB - Operation | None |  | None | None
Level 3 | P-5135002 - Obstruction of deluge spray on the top of equipment. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-5135002 | 30032c |  |  |  | PB - Operation | None |  | None | None
Level 2 | P-Z-UT-1238001-02A/B - Deluge system is not modelled for this equipment. Vendor to complete deluge modelling and to include correct tag for chillers in mode To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-Z-UT-1238001-02A/B | 30033c |  |  |  | PB - Operation | None |  | None | None
Level 2 Mezz | To add a note for P-1233003B in P&ID that it is located on Level 2 Mezz and to adjust position. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | P-1233003B | 30034c |  |  |  | PB - Operation | None |  | None | None
Level 2 Mezz | P-1233003A - Saddle to be provided with deluge. Equipment surface towards access platform needs to covered by deluge. Missing deluge pipe support. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233003A | 30035c |  |  |  | PB - Operation | None |  | None | None
- | The following deluge pipes are missing supports: P-5135002 P-1233004 P-1233006A P-1233006B P-1233002A P-1233002B | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 30036c |  |  |  | PB - Operation | None |  | None | None
Level 2 Mezz | P-1233003B - Saddle to be provided with deluge. Equipment surface towards access platform needs to covered by deluge. Missing deluge pipe support. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | P-1233003B | 30037c |  |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1233001A - Dry spot at the surface of equipment bottom near ladder. PFP to be modelled. P&ID and hydraulic report shall match. Missing deluge pipe support. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FT-1233001A | 30038c |  |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1233001A - Dry spot at the surface of equipment near manhole. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FT-1233001A | 30039c |  |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1233001A/B - No of nozzles in P&ID and hydraulic report shall match. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FT-1233001A/B | 30040c |  |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1233001A - Obstruction of beam | None | KBR | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FT-1233001A | 30041c |  |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1233001B - Dry spot at the surface of equipment bottom near ladder. PFP to be modelled. P&ID and hydraulic report shall match. Missing deluge pipe support. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FT-1233001B | 30042c |  |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1233001B - Dry spot at the surface of equipment near manhole. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | None | 30043c |  |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1233001B - Obstruction of beam | None | KBR | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | None | 30044c |  |  |  | None | None |  | None | None
Level 1 | FT-1238001A - Dry spot on equipment surface. PFP to be modelled. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FT-1238001A | 30045c |  |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1238001A - Structure obstructing manhole. | Awaiting a response from Vendor MAYEKAWA | KBR | MECH | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FT-1238001A | 30046c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1238001B - Dry spot on equipment surface. PFP to be modelled. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | FT-1238001B | 30047c |  |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1238001B - Missing one nozzle on top ring as per P&ID. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FT-1238001B | 30048c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | FT-1238001B - To evaluate the coverage of the manhole. | Manhole for FT-1238001B is provided with a dedicated spray nozzle with adequate coverage as per TQF-P84P85-S2N-DD-TOP-SAF-0041. Please see attached snapshot. | None | PIP/SAF | Pending Seatrium Reply | 30/12/2025 | None |  | None | None | SAF | None | None | M-06 |  | FT-1238001B | 30049c |  | 8.00000000000000 |  | PB - Operation | None |  | None | None | 02/01/2026 |  |  |  |  | 04/01/2026
Level 1 | FT-1238001A/B - Header of the deluge piping not connected. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | FT-1238001A/B | 30050c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | V-1233001 - Line number for rings to be updated as per P&ID. Model hierarchy to be updated. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. PFP to be modelled. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-1233001 | 30051c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-1233001 - To evaluate position of nozzle. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-1233001 | 30052c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-1233001 - To evaluate all welding points of connections to the surface of the vessel. | Awaiting a response from Vendor NOV. | None | PIP/SAF | OPEN |  | None |  | None | None | MECH | None | None | M-06 |  | V-1233001 | 30053c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | V-1233001 - Obstruction by piping supports on both sides. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-1233001 | 30054c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-1233002 - To model the PFP on the skirt and dry spot at the bottom of the vessel. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-1233002 | 30055c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-1233002 - Missing deluge piping support (typical) and missing connection to header. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-1233002 | 30056c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | V-1233002 - Missing connection to header. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-1233002 | 30057c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-1233002 - Obstruction by vessel cleat. | Awaiting a response from Vendor NOV. | None | PIP/SAF | OPEN |  | None |  | None | None | MECH | None | None | M-06 |  | V-1233002 | 30058c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | V-1238001 - To cover bottom of vessel with deluge. To model PFP on saddle. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-1238001 | 30059c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-1238001 - Manhole coverage to be evaluated. | Manhole for V-1238001 is provided with a dedicated spray nozzle with adequate coverage as per TQF-P84P85-S2N-DD-TOP-SAF-0041. Please see attached snapshot. | None | PIP/SAF | Pending Seatrium Reply | 30/12/2025 | None |  | None | None | SAF | None | None | M-06 |  | V-1238001 | 30060c |  | 8.00000000000000 |  | PB - Operation | None |  | None | None | 02/01/2026 |  |  |  |  | 04/01/2026
Level 1 | V-1238001 - Missing deluge piping support (typical for this vessel). Missing connection to header. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-1238001 | 30061c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-1238001 - Deluge projection obstructed by vessel connection projection. Unable to reach the other side of the welding. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-1238001 | 30062c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-1238001 - To clear clash and and evaluate coverage for the vessel. | Awaiting a response from Vendor MAYEKAWA | None | PIP/SAF | OPEN |  | None |  | None | None | MECH | None | None | M-06 |  | V-1238001 | 30063c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | V-5135001 - PFP to be modelled for vessel skirt. | Modelling of PFP for equipment support is not part of DR90 Review. It was agreed via 90% DESIGN REVIEW - TERMS OF REFERENCE (I-LI-3010.2S-1200-940-S2N-013) that PFP on equipment supports will only be modelled post DR-90. Please see attached snapshot. | None | SAF | Pending PB Reply | 06/01/2026 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | None | M-06 |  | V-5135001 | 30064c | 06/01/2026 | 2.00000000000000 |  | PB - Operation | True | 09/01/2026 | True | None | 09/01/2026 |  | 11/01/2026 | 11/01/2026 |  | 11/01/2026
Level 1 | V-5135001 - Line number in model to be updated as per P&ID and to match quantity of nozzles. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-5135001 | 30065c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | V-5135001 - Dry spot on vessel surface. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-5135001 | 30066c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-5135001 - Missing support for deluge piping. Missing connection to header. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-5135001 | 30067c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-5135001 - Obstruction of deluge spray by cable tray and piping. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-5135001 | 30068c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-5135001 - Dry spot on vessel shell. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-5135001 | 30069c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001A - PFP to be modelled for vessel skirt. | Modelling of PFP for equipment support is not part of DR90 Review. It was agreed via 90% DESIGN REVIEW - TERMS OF REFERENCE (I-LI-3010.2S-1200-940-S2N-013) that PFP on equipment supports will only be modelled post DR-90. Please see attached snapshot. | None | SAF | Pending PB Reply | 06/01/2026 | None |  | None | 09-01-26_KUB7_CLOSE | PIP | None | None | M-06 |  | V-UT-1233001A | 30070c | 06/01/2026 | 2.00000000000000 |  | PB - Operation | True | 09/01/2026 | True | None | 09/01/2026 |  | 11/01/2026 | 11/01/2026 |  | 11/01/2026
Level 1 | V-UT-1233001A - Line number in model to be updated as per P&ID and to match quantity of nozzles. Hierarchy in model to be updated. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-UT-1233001A | 30071c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001A - Dry spot on the vessel surface. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-UT-1233001A | 30072c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001A - Missing support for deluge piping. Missing connection to header and the rings. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-UT-1233001A | 30073c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001A - To clear obstruction to deluge spray. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-UT-1233001A | 30074c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001A - To ensure coverage to both sides of the welded connection. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-UT-1233001A | 30075c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001A - To resolve clash and ensure coverage for top of vessel. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-UT-1233001A | 30076c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001A - To provide adequate coverage for this manhole. | Manhole for V-UT-1233001A is provided with a dedicated spray nozzle with adequate coverage as per TQF-P84P85-S2N-DD-TOP-SAF-0041. Please see attached snapshot. Additional nozzle cannot be spared to cover the manhole as the flowrate for this vessel is already exceeding the min. firewater demand by 60%. | None | PIP/SAF | Pending Seatrium Reply | 30/12/2025 | None |  | None | None | SAF | None | None | M-06 |  | V-UT-1233001A | 30077c |  | 8.00000000000000 |  | PB - Operation | None |  | None | None | 02/01/2026 |  |  |  |  | 04/01/2026
Level 1 | V-UT-1233001B/C/D - PFP to be modelled for vessel skirt. | Modelling of PFP for equipment support is not part of DR90 Review. It was agreed via 90% DESIGN REVIEW - TERMS OF REFERENCE (I-LI-3010.2S-1200-940-S2N-013) that PFP on equipment supports will only be modelled post DR-90. Please see attached snapshot. | None | SAF | Pending PB Reply | 06/01/2026 | None |  | None | None | SAF | None | None | M-06 |  | V-UT-1233001B/C/D | 30078c |  | 1.00000000000000 |  | PB - Operation | None |  | None | None | 09/01/2026 |  |  |  |  | 11/01/2026
Level 1 | V-UT-1233001B/C/D - Line number in model to be updated as per P&ID and to match quantity of nozzles. Hierarchy in model to be updated. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-UT-1233001B/C/D | 30079c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001B/C/D - Dry spot on the vessel surface. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-UT-1233001B/C/D | 30080c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001B/C/D - Missing support for deluge piping. Missing connection to header and the rings. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-06 |  | V-UT-1233001B/C/D | 30081c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001B/C/D - To ensure coverage to both sides of the welded connection. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-UT-1233001B/C/D | 30082c |  |  |  | PB - Operation | None |  | None | None
Level 1 | V-UT-1233001B/C/D - To provide adequate coverage for this manhole. | Manholes for V-UT-1233001B/C/D is provided with a dedicated spray nozzle with adequate coverage as per TQF-P84P85-S2N-DD-TOP-SAF-0041. Please see attached snapshot. Additional nozzle cannot be spared to cover the manhole as the flowrate for these vessels are already exceeding the min. firewater demand by 60%. | None | PIP/SAF | Pending Seatrium Reply | 30/12/2025 | None |  | None | None | SAF | None | None | M-06 |  | V-UT-1233001B/C/D | 30083c |  | 8.00000000000000 |  | PB - Operation | None |  | None | None | 02/01/2026 |  |  |  |  | 04/01/2026
Level 1 | V-UT-1233001B/C/D - Nozzle spray obstructed. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-06 |  | V-UT-1233001B/C/D | 30084c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Clear clash with structural elements, include reducers and piping supports. | Clash resolved, reducing coupling & supports modeled. | KBR | PIP | CLOSE | 06/01/2026 | Julius Orzales | 08/01/2026 | None | 08-01-26; KUB7; CLOSE | PIP | None | no piping dcn required | M-05B | 08/01/2026 | C-UC-1225001B-01/02 | 30085c |  | 0 | 2.00000000000000 | PB - Operation | True | 08/01/2026 | True | None | 09/01/2026 | 09/01/2026 | 10/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
Level 1 | Reducers and piping supports missing. | Reducing coupling and supports modeled. | KBR | PIP | CLOSE | 06/01/2026 | Julius Orzales | 08/01/2026 | None | 08-01-26; KUB7; CLOSE | PIP | None | no piing dcn required | M-05B | 08/01/2026 | C-UC-1225001A-01/02 | 30086c |  | 0 | 2.00000000000000 | PB - Operation | True | 08/01/2026 | True | None | 09/01/2026 | 09/01/2026 | 10/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
Level 1 | Missing PFP for equipment skirts/ saddles to be modelled. | 30-Dec-25: As per Rev. A of DR90 ToR (I-LI-3010.2S-1200-940-S2N-013), PFP for structure and equipment support (intumescent type) will be modelled post DR90 upon safety studies result. Hence, this punch is not valid at the point of DR90 review. | SE | SAF | Pending PB Reply | 29/12/2025 | None |  | None | None | SAF | None | None | M-05B |  | V-1225001 V-UC-1225001A/B-01 | 30087c |  | 9.00000000000000 |  | PB - Operation | None |  | None | None | 01/01/2026 |  |  |  |  | 01/01/2026
Level 1 | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | 30-Dec-25: Nozzle discharge angle (deg) and K-factor has been aligned with P&ID and PIPENET hydraulic calculation. Whereas the nozzle maximum axial distance has been aligned with TYCO datasheet based on the corresponding installation and spray angle. Refer to nozzle properties in 3D model. | SE | SAF | RE-OPEN | 29/12/2025 | None |  | None | None | SAF | None | None | M-05B |  | V-1225001 V-UC-1225001A/B-01/02 P-UC-1225001A/B-01/02 C-UC-1225001A/B-01/02 V-UC-1225001A/B-03 | 30088c |  | 9.00000000000000 |  | PB - Operation | None |  | None | None | 01/01/2026 |  |  |  |  | 01/01/2026
Level 1 | Change orientation of piping supports or nozzle piping to avoid spray obstruction. | Model updated. | KBR | PIP | CLOSE | 05/01/2026 | Julius Orzales | 08/01/2026 | None | 08-01-26; KUB7; CLOSE | PIP | None | no piping dcn required | M-05B | 08/01/2026 | V-1225001 | 30089c |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | True | 08/01/2026 | True | None | 08/01/2026 | 09/01/2026 | 10/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
Level 1 | Re-orientate nozzles on 3rd ring to avoid spray obstructions. | None | KBR | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05B |  | V-UC-1225001A/B-02 | 30090c | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Piping supports missing. | Supports modeled. | KBR | PIP | CLOSE | 05/01/2026 | Julius Orzales | 08/01/2026 | None | 08-01-26; KUB7; CLOSE | PIP | None | no piping dcn required | M-05B | 08/01/2026 | 3/4"-FW-B7-2180-NI | 30091c |  | 1.00000000000000 | 2.00000000000000 | PB - Operation | True | 08/01/2026 | True | None | 08/01/2026 | 09/01/2026 | 10/01/2026 | 11/01/2026 | 11/01/2026 | 08/01/2026
Level 3 | Reposition nozzles to avoid spray obstructions caused by adjacent piping. | Nozzles re-positioned. | KBR | PIP | CLOSE | 06/01/2026 | Julius Orzales | 08/01/2026 | None | 08-01-26; KUB7; CLOSE | PIP | None | no piping dcn required | M-05B | 08/01/2026 | P-UC-1225001B-02 | 30092c |  | 0 | 2.00000000000000 | PB - Operation | True | 08/01/2026 | True | None | 09/01/2026 | 09/01/2026 | 10/01/2026 | 11/01/2026 | 11/01/2026 | 11/01/2026
Level 3 | Change orientation of piping supports or reposition nozzle to avoid spray obstruction. | None | KBR | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05B |  | P-UC-1225001B-02 | 30093c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Update the line tag numbering for FW-1750 and FW-2232 to align with P&amp;ID | 10Jan26: Model updated as per Comment. | KBR | PIP | Pending Seatrium Reply | 09/01/2026 | None |  | None | None | PIP | None | None | M-05 |  | V-UC-1231001A-01 | 30094c | 02/02/2026 | 0 |  | PB - Operation | None |  | None | None | 12/01/2026 |  |  |  |  | 12/01/2026
Level 1 | Dry spots are not permitted. Ensure there are no Dry spots. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001A-01 | 30095c | 03/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing PFP for equipment skirts/ saddles to be modelled. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001A-01 V-UC-1231001B-01 V-UC-1231001C-01 | 30096c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle projection is obstructed by Vessel trim valves. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001A-01 | 30097c | 03/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Piping interference with the cable tray support. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | V-UC-1231001A-01 | 30098c | 04/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Update the line tag numbering for FW-2234 to align with P&amp;ID | 10Jan2026 - Line no. FW-224 has been already updated in the Model | KBR | PIP | Pending Seatrium Reply | 09/01/2026 | None |  | None | None | PIP | None | None | M-05 |  | V-UC-1231001B-01 | 30099c | 04/02/2026 | 0 |  | PB - Operation | None |  | None | None | 12/01/2026 |  |  |  |  | 12/01/2026
Level 1 | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001A-01 /02 V-UC-1231001B-01/02 V-UC-1231001C-01/02 VV-UC-1231001B V-1231001 Z-UC-123001A-01/B-01/C-01 V-1231001 P-UC-1231001A-02/B-02/C-02 P-UC-1231001A-01/B-01/C-01 | 30100c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spots are not permitted. Ensure there are no Dry spots. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001B-01 | 30101c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle projection is obstructed by Vessel trim valves. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | V-UC-1231001B-01 V-UC-1231001C-01 | 30102c | 05/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing pipe supports for FW-1739 | 10Jan26: Support for FW-1739 has been already updated in the Model. | KBR | PIP | Pending Seatrium Reply | 09/01/2026 | None |  | None | None | PIP | None | None | M-05 |  | V-UC-1231001B-01 | 30103c | 08/02/2026 | 0 |  | PB - Operation | None |  | None | None | 12/01/2026 |  |  |  |  | 12/01/2026
Level 1 | Update the line tag numbering for FW-2236 to align with P&amp;ID | 10Jan26 : FW-2236 Line number updated. | KBR | PIP | Pending Seatrium Reply | 09/01/2026 | None |  | None | None | PIP | None | None | M-05 |  | V-UC-1231001C-01 | 30104c | 08/02/2026 | 0 |  | PB - Operation | None |  | None | None | 12/01/2026 |  |  |  |  | 12/01/2026
Level 1 | Dry spots are not permitted. Ensure there are no Dry spots. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001C-01 | 30105c | 09/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle projection is obstructed by Cable trays & structure | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001C-01 | 30106c | 08/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Update the line tag numbering for FW-2236 to align with P&amp;ID | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001A-02 | 30107c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle projection shall be re-oriented towards the equipment surface to avoid dry spots. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001A-02 V-UC-1231001B-02 V-UC-1231001C-02 | 30108c | 09/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle projection is obstructed by Vessel trim valves. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001A-02 V-UC-1231001B-02 V-UC-1231001C-02 | 30109c | 10/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing PFP for equipment skirts/ saddles to be modelled. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001A-02 V-UC-1231001B-02 V-UC-1231001C-02 | 30110c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Update the line tag numbering for FW-2235 to align with P&amp;ID | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001B-02 | 30111c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Disconnected deluge piping is observed in the model. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | V-UC-1231001B-02 | 30112c | 10/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Update the line tag numbering for FW-2237 to align with P&amp;ID | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-UC-1231001B-02 | 30113c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Include the equipment tag for both the compressor and Gas seal panel which is being protected by deluge system in the model & PIDs. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | C-UC-1231001A C-UC-1231001B C-UC-1231001C VV-UC-1231001A VV-UC-1231001B VV-UC-1231001C | 30114c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Missing support for deluge piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | C-UC-1231001A C-UC-1231001B C-UC-1231001C VV-UC-1231001A VV-UC-1231001B VV-UC-1231001C | 30115c | 11/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Obstruction of deluge piping with other process piping within Compressor module | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | C-UC-1231001A C-UC-1231001B C-UC-1231001C VV-UC-1231001A VV-UC-1231001B VV-UC-1231001C | 30116c | 11/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing PFP for equipment skirts/ saddles to be modelled. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-1231001 | 30117c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Delete the duplicate nozzle in 3D model | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | V-1231001 | 30118c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | The projection of the nozzle at level 3 needs to be revisited and ensure there is no dry spot. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-1231001 | 30119c | 12/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Nozzle projection is obstructed by Vessel trim valves. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-1231001 | 30120c | 15/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Missing piping connection | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | V-1231001 | 30121c | 15/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Cable Tray blocking the deluge cone projection. | None | None | CSE | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | V-1231001 | 30122c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Provide breakflanges on Deluge lines | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | C-UC-1231001A C-UC-1231001B C-UC-1231001C VV-UC-1231001A VV-UC-1231001B VV-UC-1231001C | 30123c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Include the equipment tag for both the compressor and Gas seal panel which is being protected by deluge system in the model & PIDs. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | Z-UC-123001A-01 Z-UC-123001B-01 Z-UC-123001C-01 | 30124c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Missing support for deluge piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | Z-UC-123001A-01 Z-UC-123001B-01 Z-UC-123001C-01 | 30125c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Obstruction of the deluge cone spray with pipiing support | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | Z-UC-123001B-01 Z-UC-123001C-01 | 30126c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spots are not permitted. Ensure there are no dry spots on welding part of the interconnection on the bottom portion of the vessel. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | P-UC-1231001A-02 P-UC-1231001B-02 P-UC-1231001C-02 | 30127c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spots are not permitted. Ensure there are no dry spots on the saddles. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | P-UC-1231001A-02 P-UC-1231001B-02 P-UC-1231001C-02 | 30128c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Overlapping of the nozzles shall be maintained on the upper deluge ring to avoid dry spots. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | P-UC-1231001A-02 P-UC-1231001B-02 P-UC-1231001C-02 | 30129c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Missing piping fasteners connection. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | P-UC-1231001A-02 P-UC-1231001B-02 P-UC-1231001C-02 | 30130c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Missing supports for the Top & bottom deluge rings. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | P-UC-1231001B-02 | 30131c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle projection clash with the platform handrail & structure. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | P-UC-1231001A-02 P-UC-1231001B-02 P-UC-1231001C-02 | 30132c | 22/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Welded portion of the interconection is not covered by the nozzle. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | P-UC-1231001A-02 P-UC-1231001B-02 P-UC-1231001C-02 | 30133c | 23/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Nozzle quantity heirarchy to be updated in the 3D model. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | P-UC-1231001A-01 | 30134c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Overlapping of the nozzles shall be maintained on the upper deluge ring to avoid dry spots. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | P-UC-1231001A-01 P-UC-1231001B-01 P-UC-1231001C-01 | 30135c | 23/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spots are not permitted. Ensure there are no dry spots on the saddles. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | P-UC-1231001A-01 P-UC-1231001B-01 P-UC-1231001C-01 | 30136c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing supports for the bottom deluge ring on P-UC-1231001A-01 Missing supports for both top &amp; bottom deluge rings applicable only for P-UC-1231001B-01 &amp; P-UC-1231001C-01 | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-05 |  | P-UC-1231001A-01 P-UC-1231001B-01 P-UC-1231001C-01 | 30137c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spots are not permitted. Ensure there are no dry spots on welding part of the interconnection | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-05 |  | P-UC-1231001A-01 P-UC-1231001B-01 P-UC-1231001C-01 | 30138c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spots are not acceptable. Dumper, flange and pump are required to be covered by water deluge. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | B-5133001A B-5133001B B-5133001C | 30139c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Deluge pipping shall be installed as removable piping (provide flange). | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | B-5133001A B-5133001B B-5133001C | 30140c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing support (U shape fasterner/ clamp) for deluge piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | B-5133001A B-5133001B B-5133001C | 30141c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing connection to pipe and header. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | B-5133001A B-5133001B B-5133001C | 30142c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing support for deluge piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | B-5133002A | 30143c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spots on the pump. Deluge should be targetted at pump only, deluge shall be excluded for the motor. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | B-5133002A/B | 30144c |  |  |  | PB - Operation | None |  | None | None
Level 1 |  | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | B-5133002B | 30145c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Breaking flange to be added for both pumps. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | B-5133002A/B | 30146c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle from both sides are obstructed. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | B-1233003A/B | 30147c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spot on pump. The coverage of the nozzle does cover the top of the pump. One nozzle to be shifted to cover the top of the pump (misalligned arrangement). | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | B-1233003A/B | 30148c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Missing pump support. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | B-1233003A/B | 30149c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Blinding flange required for material handling. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/C |  | B-1233003A/B (M10A) B-1233003C/D (M10C) | 30150c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Overlapping of the nozzles shall be maintained on the upper deluge ring to avoid dry spots | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A/C |  | SG-1223001A (M10A) SG-1223001B (M10C) | 30151c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Improve the coverage of the deluge, further minimising the dry spots. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A/C |  | SG-1223001A (M10A) SG-1223001B (M10C) | 30152c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Missing pipping supports on the top, mid and bottom rings. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | SG-1223001A | 30153c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Obstruction of deluge coverage due to the piping. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | SG-1223001A | 30154c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Improve the coverage of the deluge, further minimising the dry spots of bottom of vessel. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | TO-1223001A/ TO-1223002A | 30155c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Missing pipping supports on the top, mid and bottom rings. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | TO-1223001A / TO-1223002A | 30156c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | 6" pipeline is missing tag in the model. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | TO-1223002A / SG-1223001A | 30157c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Clash of deluge line with piping. Check the condition of this pipe and its support, due to clash with the nozzle projection. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | TO-1223002A | 30158c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Obstruction of deluge nozzle. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | TO-1223002A | 30159c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Nozzle is in the operational volume of manhole. Clash to be cleared. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | TO-1223002A | 30160c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Ensure there are no dry spots on welding part of the interconnection. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | TO-1223002A | 30161c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spot at manhole, ensure manhole coverage. Nozzle clash with operational volume of manhole, to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | V-TO-1223001A / V-TO-1223002A | 30162c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Improve the coverage of the deluge, further minimising the dry spots of bottom of vessel. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | V-TO-1223001A / V-TO-1223002A | 30163c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Nozzle spray blocked by cable tray, this volume obstruction to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | V-TO-1223001A | 30164c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing pipping supports on the top and bottom rings. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | V-TO-1223001A / V-TO-1223002A | 30165c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Welding point to be covered on the interconnection at the bottom of the vessel. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | V-TO-1223002A | 30166c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Deluge P&ID to be updated with the correct nozzle qty at the bottom ring. P&ID - 40 no. of nozzles vs model - 42 no. of nozzles | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | P-1223001A P-1223001B P-1223001C | 30167c | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Welding points to be covered on the interconnection at both the bottom & top of the vessel. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | P-1223001A P-1223001B P-1223001C | 30168c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spot to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | P-1223001A P-1223001B P-1223001C | 30169c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Flange to be added to the deluge pipe so that it should be removable, for maintenance activity | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | P-1223001A P-1223001B P-1223001C | 30170c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing pipping supports on the top and bottom rings. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A |  | P-1223001A P-1223001B P-1223001C | 30171c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | To be assessed whether the skirt and saddle of equipment to be covered with PFP or deluge to be provided. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | P-1223001A P-1223001B P-1223001C | 30172c | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Obstruction of nozzle to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | P-1223001A | 30173c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
All | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A |  | B-1223003A / B B-5133001A / B / C B-5133002A / B SG-1223001A TO-1223001A TO-1223002A V-TO-1223001A V-TO-1223002A P-1223001A / B / C | 30174c |  |  |  | PB - Operation | None |  | None | None
FGRU Package | Deluge piping line no. to be updated in the model as per the P&ID | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | General | 30175c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
FGRU Package | Interconnection between FGRU package battery limit to the M01 deluge system to be shown. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | General | 30176c |  |  |  | PB - Operation | None |  | None | None
FGRU Package | All deluge cone volumes to be shown in red colour. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | General | 30177c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
FGRU Package | Flange connection to be added in the deluge piping to facilitate compressor maintenance activity. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | C-UC-5412001-01A / B / C P-UC-5412001-01A / B / C | 30178c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
FGRU Package | To reduce water wastage as most water is currently spraying outside the equipment. Eg. lower nozzle elevation / change nozzle spray angle. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | FT-UC-5412001-01A / B | 30179c |  |  |  | PB - Operation | None |  | None | None
FGRU Package | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | FT-UC-5412001-01A / B C-UC-5412001-01A / B / C P-UC-5412001-01A / B / C V-UC-5412001-01 | 30180c |  |  |  | PB - Operation | None |  | None | None
FGRU Package | Dry spot at vessel manholes, ensure manhole coverage for all manholes on the equipment. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-UC-5412001-01 | 30181c |  |  |  | PB - Operation | None |  | None | None
FGRU Package | Improve the coverage of the deluge, further minimising the dry spots of bottom curveture of vessel. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-UC-5412001-01 | 30182c |  |  |  | PB - Operation | None |  | None | None
FGRU Package | Dry spots on the vessel surface to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-UC-5412001-01 | 30183c |  |  |  | PB - Operation | None |  | None | None
FGRU Package | Welding points (both sides) to be covered by deluge at the interconnection of the vessel. (direct coverage is required, not considering rundown) | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-UC-5412001-01 | 30184c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
FGRU Package | Nozzle spray profile should not be obstructed by the pink structural beams. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-UC-5412001-01 | 30185c |  |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | Deluge piping line no. to be updated in the model as per the P&ID | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | General | 30186c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | Interconnection between STGRU package battery limit to the M01 deluge system to be shown. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | General | 30187c |  |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | All deluge cone volumes to be shown in red colour. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | General | 30188c |  |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | To reduce water wastage on equipment. Eg. lower nozzle elevation / change nozzle spray angle. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | FT-UC-1350001-01A/B | 30189c |  |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | Dry spots on the vessel surface to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-UC-1350001-01 | 30190c |  |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | Dry spots on the vessel manhole to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-UC-1350001-01 | 30191c |  |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | Welding points to be covered by deluge at the interconnection of the vessel. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-UC-1350001-01 | 30192c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | To reduce water wastage as most water is currently spraying outside the equipment. Eg. check if correct cone representation / lower nozzle elevation / change nozzle spray angle. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-UC-1350001-01 | 30193c |  |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | To reduce water wastage as most water is currently spraying outside the equipment. Eg. check if correct cone representation / lower nozzle elevation / change nozzle spray angle. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | P-UC-1350001-01A / B | 30194c |  |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | To evaluate coverage of equipment skirt / saddle (with PFP / deluge) | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | P-UC-1350001-01A / B | 30195c |  |  |  | PB - Operation | None |  | None | None
STGRU<br>Package | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | FT-UC-1350001-01A/B P-UC-1350001-01A /B V-UC-1350001-01 C-UC-1350001-01A / B | 30196c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Please check number of nozzles is the mid ring 1, 2 and bottom ring are consistent with p&id. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30197c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spots on the boot and area near the boot to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30198c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spots in between the mid ring 1 and bottom ring to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30199c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spots to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30200c |  |  |  | PB - Operation | None |  | None | None
Level 1 | To check for the missing support. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | V-5412001/ V-5412002 | 30201c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle obstruction and clash with cable tray. Typical comments, to check for the rest of the nozzles. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30202c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Missing connnection of nozzle. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | V-5412001 | 30203c |  |  |  | PB - Operation | None |  | None | None
Level 1 | For these nozzles, KBR to check if the nozzles are able to cover the vessel with neighbouring nozzles if there are any obstruction. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30204c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle clash with structure to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30205c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle clash with structure to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30206c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzles clash on mid rings with structure to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30207c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spot on welding points to be checked. Typical comments for all welding points on V-5412001. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412001 | 30208c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Please check number of nozzles are consistent with p&id. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412002 | 30209c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spots on vessel to be addressed. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412002 | 30210c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spot on welding points to be checked. Typical comments for all welding points on V-5412002. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412002 | 30211c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle to be lowered down, closer to vessel. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412002 | 30212c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Space for steps on the ladder to be ensured. (move ladder/ readjust deluge line position) | None | KBR | PIP/SAF | OPEN |  | None |  | None | None | STR | None | None | M-01 |  | V-5412002 | 30213c | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Disconnected deluge piping is observed in the model. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | V-5412002 | 30214c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle clash with cable tray to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-5412002 | 30215c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Missing support clamping for deluge lines. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | B-5412001A/B B-5412002A/B | 30216c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing header support for deluge lines. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-01 |  | B-5412001A/B B-5412002A/B | 30217c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Incorrect tag line for equipment. To check and correct. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | B-5412001A/B B-5412002A/B | 30218c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spot to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-1350001 | 30219c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Manhole and flange welding shall be provided with deluge. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-1350001 | 30220c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle coverage obstruction due to platform. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | V-1350001 | 30221c |  |  |  | PB - Operation | None |  | None | None
Level 3 | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | Nozzle discharge angle (deg) and K-factor has been aligned with P&ID and PIPENET hydraulic calculation. Whereas the nozzle maximum axial distance has been aligned with TYCO datasheet based on the corresponding installation and spray angle. Refer to nozzle properties in 3D model. | None | SAF | RE-OPEN | 04/01/2026 | None |  | None | None | SAF | None | None | M-01 |  | V-5412001/2 B-5412001A/B B-5412002A/B V-1350001 P-1350001A/B | 30222c |  | 3.00000000000000 |  | PB - Operation | None |  | None | None | 07/01/2026 |  |  |  |  | 07/01/2026
Level 3 | Missing Deluge system for the Flare Pilot system | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-01 |  | CN-5412001 | 30223c |  |  |  | PB - Operation | None |  | None | None
Level 1 | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M12/M13/M13B |  | UB-TG-5147001E/F-03 UB-TG-5147001C/D-03 UB-TG-5147001A/B-03 FT-5133002E/F FT-5135001E/F FT-5133002A/B FT-5135001A/B FT-5133002C/D FT-5135001C/D | 30224c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Deluge to cover flange. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M12/M13/M13B |  | FT-5133002E/F FT-5133002A/B FT-5133002C/D | 30225c | 15/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Adjust tag numbers of deluge lines. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M12/M13B |  | FT-5135001E/F FT-5135001C/D | 30226c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Obstruction of deluge coverage. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M12/M13B |  | FT-5135001E/F FT-5135001C/D | 30227c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Dry surface to be fixed. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M12/M13B |  | FT-5135001E/F FT-5135001C/D | 30228c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Resolve clash and reevalute delgue coverage if required. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M12 |  | FT-5135001E/F | 30229c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing pipe support. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M12/M13B |  | FT-5135001E/F FT-5135001C/D | 30230c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle clash with operation volume. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M12/M13B |  | FT-5135001E/F FT-5135001D | 30231c | 26/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle coverage obstructed by access way. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M12 |  | FT-5135001F | 30232c | 16/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Flange and PSV to be covered by deluge. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M12/M13/M13B |  | UB-TG-5147001E/F-03 UB-TG-5147001A/B-03 UB-TG-5147001C/D-03 | 30233c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Flange to be added. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M12/M13/M13B |  | UB-TG-5147001E/F-03 UB-TG-5147001A/B-03 UB-TG-5147001C/D-03 | 30234c | 17/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing support and header on deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | B-1223004A/B | 30235c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Add break flange on the foam line (FL-1855). | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B Foam |  | SDV-5331032B | 30236c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Update number of nozzles in P&ID as per 3D model. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | V - 5331001 | 30237c | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Reroute deluge line/ add break flange (maintain nozzle position) near at both man holes of vessel to move away from the ring to allow for vessel maintenance. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | V - 5331001 | 30238c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing supports and header on deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | V - 5331001 | 30239c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spot to be covered on vessel on bottom and sides. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | V - 5331001 | 30240c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Deluge piping is clashing with structure. Projection is blocked by structure, leading to dry spot. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | V - 5331001 | 30241c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spots at the piping welding area. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | V - 5331001 | 30242c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Line 1-1/2"-FW-B7-2081-NI is missing from P&ID. To maintain consistency in P&ID and 3D model. Update number of nozzles in P&ID as per 3D model. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | Z-1212001 | 30243c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Valves to be covered with deluge. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | Z-1212001 | 30244c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Missing support and header on deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | Z-1212001 | 30245c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Line number mismatch of P&ID and 3D model. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | Z-5133002 | 30246c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Missing support on deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | Z-5133002 | 30247c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Verify and evaluate if the equipment at the lower level of the skid requires deluge. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | Z-5133002 | 30248c | 28/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spots on the vessel to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | SG-1223002 | 30249c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Deluge line is clashing with structure to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | SG-1223002 | 30250c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Missing support on deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | SG-1223002 | 30251c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Missing support on deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | SG-1223002 | 30252c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Incomplete modelling of foam nozzle, line is not connected. Ensure line size is consistent with p&id. Height of nozzle to comply with the regulatory standards. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B Foam |  | None | 30253c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle clash and obstruction with structure to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | SG-1223002 | 30254c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Reroute deluge line/ add break flange (maintain nozzle position) near at all man holes of vessel to move away from the ring to allow for vessel maintenance. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | SG-1223002 | 30255c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spots on the welding and vessel surface to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223004 | 30256c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Deluge coverage of saddle is not complete. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223004 | 30257c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Missing support on deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | P-1223004 | 30258c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Obstruction of nozzle coverage by structure to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223004 | 30259c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Addition of flange is required to enable removal for maintenance. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | P-1223004 | 30260c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Resolve clash and reevalute coverage. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223004 | 30261c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Line number mismatch of P&ID and 3D model. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223005A/B/C/D | 30262c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | The cooler shall be provided with deluge coverage. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223005A/B/C/D | 30263c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Missing support on deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | P-1223005A/B/C/D | 30264c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spot to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223005C | 30265c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spot on welding to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223005A/B/C/D | 30266c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Coverage obstruction with beam to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223005B | 30267c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Dry surface to be fixed. Both cones to cover the filter. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | FT-5133001 | 30268c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Missing support to be provided. Clash of deluge piping to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | FT-5133001 | 30269c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Minor dry spots on the manhole to be fixed. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | V-5133001 | 30270c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spots on vessel due to obstruction of nozzle due to platform | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | V-5133001 | 30271c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Nozzle coverage is obstructed by the flange. Dryspot on the welding to be fixed. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | V-5133001 | 30272c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing suport on deluge piping on all rings. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | V-5133001 | 30273c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Clash of deluge line/ nozzle to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | V-5133001 | 30274c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Line number mismatch of P&ID and 3D model. The number of nozzle is also mismatched, to be resolved of P&ID and 3D model. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223002A/B/C/D/E/F | 30275c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spots on the bottom, sides and top of the heater to be fixed. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223002A/B/C/D/E/F | 30276c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spots on vessel to be addressed. PFP/ deluge to be provided for vessel saddles. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223002A/B/C/D/E/F | 30277c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Support/ clamp of deluge is missing. Connection to header is missing. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10B |  | P-1223002A/B/C/D/E/F | 30278c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Primary structures clashing with deluge line to be resolved. | None | KBR | STR | OPEN |  | None |  | None | None | STR | None | None | M-10B |  | P-1223002B | 30279c | 29/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spot of vessel welding to be fixed. Typical comment. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223002A/B/C/D/E/F | 30280c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Clash of deluge line FW-1201 with piping to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | P-1223002C | 30281c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B |  | All | 30282c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | The flange connecting to the pump is the main source of leakage of pump. Deluge to be provided for the pump. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | B-1223003C/D | 30283c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Missing pump support. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C |  | B-1223003C/D | 30284c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Mismatch of line number on P&ID and 3D model. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10C |  | B-1223003C/D | 30285c | 10/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spot on flange to be covered by deluge. The projection of the nozzle is not protecting the door of the PIG launcher/ receiver. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09A/B |  | M09A LP-1244002A/B LP-1244003A RP-1210001A RP-1210002 M09B LP-1244001A | 30286c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Saddle is not protected by deluge, to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09A/B |  | M09A LP-1244002A/B LP-1244003A RP-1210001A RP-1210002 M09B LP-1244001A | 30287c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Axial distance of the nozzle is not covering to the deck. To be resolved. (This punch is deleted with agreement from PB Tulio &amp; Pamela) | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09A |  | M09A LP-1244002A/B LP-1244003A RP-1210001A RP-1210002 M09B LP-1244001A | 30288c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing pipe support for PIG launcher pipe penetrations. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A |  | LP-1244002A/B | 30289c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Mismatch of line number and nozzle quantity on P&ID and 3D model. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09A/B |  | M09A LP-1244003A RP-1210001A RP-1210002 M09B LP-1244001A/B/C LP-1244002C LP-1244003C/D | 30290c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Nozzle spray projection obstructed by piping to be resolved. Take note of shadow effect due to the pipe nearby. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09A |  | LP-1244003A | 30291c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Wrong nozzle spray angle was used. To be updated in 3D model. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09A |  | RP-1210001A | 30292c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Nozzle spray projection obstructed by piping to be resolved. Take note of shadow effect due to the pipe nearby. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09A/B |  | M09A RP-1210002 M09B LP-1244003C/D | 30293c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M09A |  | M09A LP-1244002A/B LP-1244003A RP-1210001A RP-1210002 M09B LP-1244001A/B/C LP-1244002C LP-1244003C/D | 30294c | 15/01/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Insufficient coverage of the pipeline. To readjust nozzle location. To check if the nozzle to be provided on the other sides as well for this line. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09A/B/C/D/E/F |  | Level 3 Injection Manifold M09A/B/C/D/E/F | 30295c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Piping support missing for deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A/B/C/D/E/F |  | Level 3 Injection Manifold M09A/B/C/D/E/F | 30296c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing support for deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09B |  | LP-1244003C/D | 30297c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Add removable flanges to be able to remove pipes during material handling. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09A/B |  | M09A LP-1244002A/B LP-1244003A RP-1210001A RP-1210002 M09B LP-1244001A/B/C LP-1244002C LP-1244003C/D | 30298c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Hinges to be protected. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M09B |  | LP-1244001A/B/C LP-1244002C LP-1244003C/D | 30299c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spot to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M09B |  | LP-1244003D | 30300c | 15/01/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spot on flange to be covered by deluge. The projection of the nozzle is not protecting the door of the PIG launcher/ receiver. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09C |  | M09C LP-1244001D/E/F LP-1244002D | 30301c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Saddle is not protected by deluge, to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09C/D |  | M09C LP-1244001D/E/F LP-1244002D M09D LP-1244003F/G RP-1210003A LR-1231001 | 30302c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Mismatch of line number and nozzle quantity on P&ID and 3D model. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09C/D |  | M09C LP-1244001D/E/F LP-1244002D M09D LP-1244003F/G RP-1210003A LR-1231001 | 30303c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Add removable flanges to be able to remove pipes during material handling. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09C/D |  | M09C LP-1244001D/E/F LP-1244002D M09D LP-1244003F/G RP-1210003A LR-1231001 | 30304c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Hinges to be protected. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M09C/D |  | M09C LP-1244001D/E/F LP-1244002D M09D LP-1244003F/G RP-1210003A LR-1231001 | 30305c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Nozzle spray projection obstructed by piping to be resolved. Take note of shadow effect due to the pipe nearby. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09D |  | LP-1244003F/G RP-1210003A | 30306c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing support for deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09D |  | M09C LP-1244001D/E/F LP-1244002D M09D LP-1244003F/G RP-1210003A LR-1231001 | 30307c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spot on flange to be covered by deluge. The projection of the nozzle is not protecting the door of the PIG launcher/ receiver. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09E/F |  | M09E LP-1244001G/H/J M09F LP-1244002E | 30308c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Saddle is not protected by deluge, to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M09E/F |  | M09E LP-1244001G/H/J LP-1244003E M09F LP-1244002E LP-1244003B RP-1210001B RP-1231003B | 30309c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Mismatch of line number and nozzle quantity on P&ID and 3D model. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09E/F |  | M09E LP-1244001G/H/J LP-1244003E M09F LP-1244002E LP-1244003B RP-1210001B RP-1231003B | 30310c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Add removable flanges to be able to remove pipes during material handling. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M09E/F |  | M09E LP-1244001G/H/J LP-1244003E M09F LP-1244002E LP-1244003B RP-1210001B RP-1231003B | 30311c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Hinges to be protected. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09E/F |  | M09E LP-1244001G/H/J LP-1244003E M09F LP-1244002E RP-1231003B | 30312c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Nozzle spray projection obstructed by piping to be resolved. Take note of shadow effect due to the pipe nearby. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09E/F |  | M09E LP-1244003E M09F LP-1244003B RP-1210001B RP-1231003B | 30313c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing support for deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M09E/F |  | M09E LP-1244001G/H/J LP-1244003E M09F LP-1244002E LP-1244003B RP-1210001B RP-1231003B | 30314c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spot to be covered. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M09E |  | M09E LP-1244001G LP-1244003E | 30315c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
All | DR60 Punch 30330B (REOPENED) Ensure no cable tray/structure obstruction/any other obstruction to achieve uniform discharge of foam solution from the foam nozzles. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A/B/C Foam |  | None | 30316c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30317c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30318c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
All | Ensure that the maximum height of each nozzle from the deck is 5m. Nozzles which do not meet this requirement will be discussed on a case by case basis. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A/B/C Foam |  | None | 30319c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30320c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30321c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30322c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30323c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30324c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30325c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30326c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30327c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30328c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30329c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30330c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Ensure the coverage does not spray outside of the coaming area, through the vertical ladder. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10A Foam |  | None | 30331c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spot to be covered. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10C Foam |  | None | 30332c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10C Foam |  | None | 30333c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10C Foam |  | None | 30334c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10C Foam |  | None | 30335c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Coaming is disconnected. To be resolved. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10C Foam |  | None | 30336c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10C Foam |  | None | 30337c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Ensure the coverage does not spray outside of the coaming area. Typical comment for the M10B level 1. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B Foam |  | None | 30338c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Relocate the nozzles to ensure that there is no foam projection on the platform (which is on a different elevation). This is to prevent loss of foam coverage on level 3 platform. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B Foam |  | None | 30339c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B Foam |  | None | 30340c |  |  |  | PB - Operation | None |  | None | None
Level 4 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B Foam |  | None | 30341c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Ensure the coverage does not spray outside of the coaming area. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M10B Foam |  | None | 30342c |  |  |  | PB - Operation | None |  | None | None
Level 3 | To check if piping support has been provided for the foam line. Typical comment for all foam modules. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M10A/B/C Foam |  | None | 30343c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Line number and diameters in P&ID for all the rings need to be updated in 3D Model. Nozzle quantity to be aligned. Equipment tag in P&ID and 3D model to be aligned. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-07B |  | V-UC-1252001B V-UC-1231002C-01/D-01 V-UC-1231002C-02/D-02 C-UC-1231002C-01/02 VV-UC-1252001B | 31001c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Welded connection of vessel projection to be covered with deluge | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M07B/M07A |  | V-UC-1252001B V-UC-1252001A | 31002c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Dry spot at top of vessel. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M07B/M07A |  | V-UC-1252001B V-UC-1252001A | 31003c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Spray nozzle cannot be obstructed | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M07B/M07A |  | V-UC-1252001B V-UC-1252001A | 31004c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Bottom ring for this vessel to be provided with removable flange to be removed during handling of compressor. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B/M07A |  | V-UC-1252001B V-UC-1252001A | 31005c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Spectacle blind and nozzle to be re-orientated to ensure no obstruction to spray coverage. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07B/M07A |  | V-UC-1252001B V-UC-1252001A | 31006c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Welded connection of vessel projection to be covered with deluge | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M07B/M07A |  | V-UC-1231002C-01/D-01 V-UC-1231002A-01/B-01 | 31007c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Re-orientate nozzle away from support cleat. Typical for these vessels. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M07B/M07A |  | V-UC-1231002C-02/D-02 V-UC-1231002A-02/B-02 | 31008c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Welded connection of vessel projection to be covered with deluge. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M07B/M07A |  | V-UC-1231002C-02/D-02 V-UC-1231002A-02/B-02 | 31009c |  |  |  | PB - Operation | None |  | None | None
Level 1 | To cover the compressor seal with deluge. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M07B/M07A |  | C-UC-1252001B C-UC-1231002C-01/02 C-UC-1231002D-01/02 C-UC-1252001A C-UC-1231002A-01/02 C-UC-1231002B-01/02 | 31010c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Missing pipe supports for compressor. To add removable flanges and use removable support type. Add support for gas seal panel for deluge piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | C-UC-1252001B C-UC-1252001B_GSP C-UC-1231002C-01/02 C-UC-1231002C-01/02_GSP C-UC-1231002D-01/02 C-UC-1231002D-01/02_GSP UC-1252001B_SGTS UC-1231002C_SGTS UC-1231002D_SGTS | 31011c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Adjust nozzles to cover the dry spots. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M07B/M07A |  | UC-1252001B_SGTS UC-1231002C/D_SGTS UC-1252001A_SGTS UC-1231002A/B_SGTS | 31012c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Add removable flanges | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B/M07A |  | UC-1252001B_SGTS UC-1231002C/D_SGTS UC-1252001A_SGTS UC-1231002A/B_SGTS | 31013c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Add removable flanges and support (removable type) for top and bottom rings. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07B |  | P-UC-1252001B P-UC-1231002C-01/D-01 P-UC-1231002C-02/D-02 | 31014c | 24/02/2026 |  |  | None | None |  | None | None
Level 4 | Add deluge spray to connections of heat exchanger. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07B/M07A |  | P-UC-1231002B P-UC-1231002C-01/D-01 P-UC-1231002C-02/D-02 P-UC-1231002A P-UC-1231002A-01/B-01 P-UC-1231002A-02/B-02 | 31015c | 24/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Cover Dry Spot. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M07B |  | P-UC-1231002D-01 P-UC-1231002C-02/D-02 | 31016c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Reposition nozzles to cover dry spot on compressor surface. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | C-UC-1254001A/B/C-01 C-UC-1254001A/B/C-02 | 31017c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Resolve clash with process piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | C-UC-1254001A/B/C-01 C-UC-1254001A/B/C-02 | 31018c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Deluge pipe supports missing. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | C-UC-1254001A/B/C-01 C-UC-1254001A/B/C-02 C-UC-1254001A/B/C-01_GSP C-UC-1254001A/B/C-02_GSP | 31019c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Include flange for purpose of removing deluge piping during maintenance of compressors | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | C-UC-1254001A/B/C-01 C-UC-1254001A/B/C-02 | 31020c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Bottom ring nozzles located in wrong hierarchy. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | V-UC-1254001A/B/C-02 | 31021c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Add additional nozzle to cover manhole for each suction scrubber. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | V-UC-1254001A/B/C-01 V-UC-1254001A/B/C-02 | 31022c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Minimize dry spots on the surface and vessel's welded connections | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | V-UC-1254001A/B/C-01 V-UC-1254001A/B/C-02 | 31023c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Piping supports missing for top ring for V-UC-1254001A/B/C-01. Provide missing clamp for all deluge piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | V-UC-1254001A/B/C-01 V-UC-1254001A/B/C-02 | 31024c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Resolve clash with process piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | VV-UC-1254001A/B/C | 31025c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Deluge pipe supports missing. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | VV-UC-1254001A/B/C | 31026c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Equipment tag no. to be updated in P&ID from UC-1254001A/B/C_SGTS to VV-UC-1254001A/B/C | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-02 |  | VV-UC-1254001A/B/C | 31027c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Deluge pipe supports missing. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | Z-5135001 | 31028c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Deluge pipe supports missing. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | P-UC-1254001A/B/C-01 P-UC-1254001A/B/C-02 | 31029c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Nozzle coverage may be obstructed by process piping. Extend nozzle closer to equipment to minimize spray obstruction and include removable flange. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M-02 |  | P-UC-1254001A/B/C-01 P-UC-1254001A/B/C-02 | 31030c |  |  |  | PB - Operation | None |  | None | None
- | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-02 |  | ALL | 31031c |  |  |  | PB - Operation | None |  | None | None
None | Obstruction of deluge coverage. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M13 |  | FT -5135005A FT -5135005B | 31032c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
None | Dry surface to be fixed. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M13 |  | FT -5135001A FT -5135001B | 31033c | 18/02/2026 |  |  | PB - Operation | None |  | None | None
None | Deluge piping is crossing the handrail. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M13 |  | FT -5135001A FT -5135001B | 31034c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
None | Branch line size in the PID shall be indicated and aligned with the 3D model | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M13 |  | FT -5135001A FT -5135001B | 31035c | 19/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Missing support for deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | Z-1359501 | 31036c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Gap between nozzle and equipment to be reduced. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | Z-1359501 | 31037c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | Nozzle hierarchy needs to be updated as per P&amp;ID in the 3D model. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | V-UT-1235001 | 31038c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Missing support for deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | V-UT-1235001 | 31039c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle hierarchy needs to be updated as per P&ID in the 3D model. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | P-UT-1235001-01 | 31040c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Welding connection for projection need to be covered with deluge. To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | P-UT-1235001-01 | 31041c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Missing support for deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | P-UT-1235001-01 | 31042c | 06/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing connection to nozzle. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | Z-UT-1235001-A/B/C | 31043c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Dry spot at both ends to be covered with deluge. To close this punch, it shall be checked the discharge angle (deg), the &quot;k factor&quot; and the nozzle&#39;s instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | Z-UT-1235001-A/B/C | 31044c |  |  |  | PB - Operation | None |  | None | None
Level 4 | To clear obstruction/clash. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-04 |  | Z-UT-1235001-A/B/C | 31045c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Missing support for deluge line. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-04 |  | Z-UT-1235001-A/B/C | 31046c | 13/02/2026 |  |  | PB - Operation | None |  | None | None
Level 1 | It shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | SAF | OPEN |  | None |  | None | None | SAF | None | None | M13 |  | FT -5135001A FT -5135001B | 31047c |  |  |  | PB - Operation | None |  | None | None
Level 1 | Line number and diameters in P&ID for all the rings need to be updated in 3D Model. Nozzle quantity to be aligned. Equipment tag in P&ID and 3D model to be aligned. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M07A |  | V-UC-1252001A V-UC-1231002A-01/B-01 V-UC-1231002A-02/B-02 C-UC-1231002A-01/02 VV-UC-1252001A | 31048c | 23/01/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Missing pipe supports for compressor. To add removable flanges and use removable support type. Add support for gas seal panel for deluge piping. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | C-UC-1252001A C-UC-1252001A_GSP C-UC-1231002A-01/02 C-UC-1231002A-01/02_GSP C-UC-1231002B-01/02 C-UC-1231002B-01/02_GSP UC-1252001A_SGTS UC-1231002A_SGTS UC-1231002B_SGTS | 31049c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Add removable flanges and support (removable type). | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-UC-1252001A P-UC-1231002A-01/B-01 P-UC-1231002A-02/B-02 | 31050c | 25/02/2026 |  |  | PB - Operation | None |  | None | None
Level 4 | Add bottom ring as per M07B to cover support. | None | None | PIP/SAF | OPEN |  | None |  | None | None | PIP | None | None | M07A |  | P-UC-1252001A P-UC-1231002A-01/B-01 P-UC-1231002A-02/B-02 | 31051c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Support for deluge piping to be provided. | None | None | PIP | OPEN |  | None |  | None | None | PIP | None | None | M-14 |  | PS-01 (B-UQ-1261001-09A/E) PS-02 (B-UQ-1261001-08A/E) PS-03 (B-UQ-1261001-10A/E) PS-04 (B-UQ-1261001-07A/E) PS-05 (B-UQ-1261001-11A/B) PS-06 (B-UQ-1261001-12A/B) PS-09 (B-UQ-1261001-15A/B) PS-12 (B-UQ-1261001-04A/C) | 32001c | 20/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Axial distance of the nozzle cone is not covering up till the deck. To be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | PS-01 (B-UQ-1261001-09A/E) PS-02 (B-UQ-1261001-08A/E) PS-03 (B-UQ-1261001-10A/E) PS-04 (B-UQ-1261001-07A/E) PS-05 (B-UQ-1261001-11A/B) PS-06 (B-UQ-1261001-03A/C) PS-06 (B-UQ-1261001-02A/C) PS-06 (B-UQ-1261001-12A/B) PS-08 (B-UQ-1261001-13A/B) PS-09 (B-UQ-1261001-15A/B) PS-10 (B-UQ-1261001-06A/C) PS-12 (B-UQ-1261001-04A/C) | 32002c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Pump discharge is not covered by nozzle cone. To adjust nozzle position to ensure coverage. (nozzle to focus on coverage of pump discharge flange) | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | PS-01 (B-UQ-1261001-09A/E) PS-02 (B-UQ-1261001-08A/E) PS-03 (B-UQ-1261001-10A/E) PS-04 (B-UQ-1261001-07A/E) PS-05 (B-UQ-1261001-11A/B) PS-06 (B-UQ-1261001-03A/C) PS-06 (B-UQ-1261001-02A/C) PS-08 (B-UQ-1261001-13A/B) PS-09 (B-UQ-1261001-15A/B) | 32003c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Nozzle cone to avoid coverage of the pumps' electric motor and electrical panels. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | PS-01 (B-UQ-1261001-09A/E) PS-02 (B-UQ-1261001-08A/E) PS-03 (B-UQ-1261001-10A/E) PS-04 (B-UQ-1261001-07A/E) PS-06 (B-UQ-1261001-12A/B) PS-08 (B-UQ-1261001-13A/B) | 32004c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Deluge pipe line no. and line size to be updated in model as per latest P&amp;ID / Hyraulics in Level 2 M14. Equipment tag to be corrected in P&amp;ID. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | General | 32005c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Pump deluge piping header to be shifted some distance away from the cable tray so that cable tray is not directly below (incase of leak from deluge piping) | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | PS-01 (B-UQ-1261001-09A/E) PS-02 (B-UQ-1261001-08A/E) PS-03 (B-UQ-1261001-10A/E) PS-04 (B-UQ-1261001-07A/E) | 32006c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Nozzle spray obstructed by the vertical structure and the cable tray (green circled). To be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | PS-06 (B-UQ-1261001-03A/C) PS-06 (B-UQ-1261001-02A/C) PS-06 (B-UQ-1261001-12A/B) PS-10 (B-UQ-1261001-06A/C) PS-12 (B-UQ-1261001-04A/C) | 32007c |  |  |  | PB - Operation | None |  | None | None
Level 2 | Missing deluge pipe connection. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | PS-06 (B-UQ-1261001-02A/C) | 32008c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 2 | Deluge piping clash with cable tray to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | PS-12 (B-UQ-1261001-04A/C) | 32009c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Piping support missing for deluge line on TG01. Piping support missing on nozzles and distribution pipe for the top header of TG01. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | TG-01 (TQ-UQ-1261001-02A/B , TQ-UQ-1261001-07A/B , TQ-UQ-1261001-08 , TQ-UQ-1261001-09, TQ-UQ-1261001-10A/B) | 32010c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle cone obstructed by structural bracing. To be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-01 (TQ-UQ-1261001-02A/B , TQ-UQ-1261001-07A/B , TQ-UQ-1261001-08 , TQ-UQ-1261001-09, TQ-UQ-1261001-10A/B) | 32011c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle cone obstructed by tubing tray on TG01. To be resolved. Also, evaluate type of tray for these tubings so that deluge spray is maximised. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-01 (TQ-UQ-1261001-02A/B , TQ-UQ-1261001-07A/B , TQ-UQ-1261001-08 , TQ-UQ-1261001-09, TQ-UQ-1261001-10A/B) | 32012c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Tank interconnection to be covered by nozzle cone. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-01 (TQ-UQ-1261001-02A/B , TQ-UQ-1261001-07A/B , TQ-UQ-1261001-08 , TQ-UQ-1261001-09, TQ-UQ-1261001-10A/B) | 32013c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Pipe support clash with TG03 guardrail to be resolved. Evaulate feasibility to move deluge piping outside TG03. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | TG-01 (TQ-UQ-1261001-02A/B , TQ-UQ-1261001-07A/B , TQ-UQ-1261001-08 , TQ-UQ-1261001-09, TQ-UQ-1261001-10A/B) | 32014c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Angle the nozzle slightly upwards to achieve better coverage below the platform. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-01 (TQ-UQ-1261001-02A/B , TQ-UQ-1261001-07A/B , TQ-UQ-1261001-08 , TQ-UQ-1261001-09, TQ-UQ-1261001-10A/B) | 32015c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spots. Evalute resolution. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-01 (TQ-UQ-1261001-02A/B , TQ-UQ-1261001-07A/B , TQ-UQ-1261001-08 , TQ-UQ-1261001-09, TQ-UQ-1261001-10A/B) | 32016c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle obstructed by structure. Dry spot to be resolved behind this structure. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-01 (TQ-UQ-1261001-02A/B , TQ-UQ-1261001-07A/B , TQ-UQ-1261001-08 , TQ-UQ-1261001-09, TQ-UQ-1261001-10A/B) | 32017c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Piping support missing for deluge line on TG08. Piping support missing on nozzles and distribution pipe for the top header of TG08. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | TG-08 (TQ-UQ-1261001-06A/B) | 32018c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Angle the nozzle slightly upwards to achieve better coverage below the platform. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-08 (TQ-UQ-1261001-06A/B) | 32019c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spot to be resolved. Shift nozzle towards tank edge. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-08 (TQ-UQ-1261001-06A/B) | 32020c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle cone obstructed by tubing tray on TG08. To be resolved. Also, evaluate type of tray for these tubings so that deluge spray is maximised. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-08 (TQ-UQ-1261001-06A/B) | 32021c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle spray obstructed by structural | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-08 (TQ-UQ-1261001-06A/B) | 32022c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spots on tank surface to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-08 (TQ-UQ-1261001-06A/B) | 32023c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spots on tank surface to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-08 (TQ-UQ-1261001-06A/B) | 32024c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle spray obstructed by structral bracing. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-08 (TQ-UQ-1261001-06A/B) | 32025c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Deluge pipe line no. and line size to be updated in model as per latest P&amp;ID / Hyraulics in Level 3 M14. Equipment tag to be corrected in P&amp;ID. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | General | 32026c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Deluge piping clash with tubing to be resolved. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | TG-08 (TQ-UQ-1261001-06A/B) | 32027c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle spray obstructed by ladder. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-07 (TQ-UQ-1261001-04) | 32028c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Angle the nozzle slightly upwards / directly 90 deg on tank surface to achieve better coverage below the platform. Applies to other areas under platform of tank. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-07 (TQ-UQ-1261001-04) | 32029c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle clash with guardrail | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | TG-07 (TQ-UQ-1261001-04) | 32030c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Position nozzle little further / change nozzle angle to ensure good coverage behind structural beam | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-07 (TQ-UQ-1261001-04) | 32031c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Piping support missing for deluge line on TG07. Piping support missing on nozzles and distribution pipe for the top header of TG07. | None | None | PIP | OPEN |  | None |  | None | None | SAF | None | None | M-14 |  | TG-07 (TQ-UQ-1261001-04) | 32032c | 27/02/2026 |  |  | PB - Operation | None |  | None | None
Level 3 | Evaluate better position of nozzle to ensure some distance from lighting. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-07 (TQ-UQ-1261001-04) | 32033c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Shift nozzle towards tank corner for better coverage behind tubing and tank corner. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-04 (TQ-UQ-1261001-03 , TQ-UQ-1261001-11 , TQ-UQ-1261001-13) | 32034c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle angle to be changed (evaulate 90 deg position of nozzle) so that better coverage achieved under tank platform and infront of vertical ladder. Applies to left side of tank platform also. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-04 (TQ-UQ-1261001-03 , TQ-UQ-1261001-11 , TQ-UQ-1261001-13) | 32035c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle cone obstructed by tubing tray on TG04. To be resolved. Also, evaluate type of tray for these tubings so that deluge spray is maximised. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-04 (TQ-UQ-1261001-03 , TQ-UQ-1261001-11 , TQ-UQ-1261001-13) | 32036c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Both nozzle sprays are obstructed, to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-04 (TQ-UQ-1261001-03 , TQ-UQ-1261001-11 , TQ-UQ-1261001-13) | 32037c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle obstructed by structure. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-04 (TQ-UQ-1261001-03 , TQ-UQ-1261001-11 , TQ-UQ-1261001-13) | 32038c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Adjust angle of nozzle to ensure coverage behind tubing tray. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-04 (TQ-UQ-1261001-03 , TQ-UQ-1261001-11 , TQ-UQ-1261001-13) | 32039c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Nozzle obstructed by guardrail, to be resolved. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-03 (TQ-UQ-1261001-12) | 32040c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spot, check feasibility to adjust nozzle to tank corner to cover dry spot. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-03 (TQ-UQ-1261001-12) | 32041c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Shift nozzle tapping point closer to tank corner. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-03 (TQ-UQ-1261001-12) | 32042c |  |  |  | PB - Operation | None |  | None | None
Level 3 | Dry spot at the top of the tank to be resolved, between the tank bracings. Credit to be taken from nozzle at the top of tank. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | TG-03 (TQ-UQ-1261001-12) | 32043c |  |  |  | PB - Operation | None |  | None | None
Level 2/3 | To close this punch, it shall be checked the discharge angle (deg), the "k factor" and the nozzle's instalation angle in the memorial calculation. | None | None | PIP/SAF | OPEN |  | None |  | None | None | SAF | None | None | M14 |  | General | 32044c |  |  |  | PB - Operation | None |  | None | None
MAIN DECK ACCOMMODATION | Update reopen remarks and reset cleared dates. | TESTING | None | ELE | OPEN | 31/12/2025 | TESTING | 16/12/2025 | TESTING | TESTING | ELE | None | TESTING | FWD | 19/01/2026 | TESTING | TESTING_1 | 31/12/2025 | 11.0000000000000 | 8.00000000000000 | PB - Operation | True | 14/01/2026 | False | True | 03/01/2026 | 14/01/2026 | 16/01/2026 | 18/01/2026 | 14/01/2026 | 04/01/2026