## Sheet1
Punch No | Zone | DECK No. | Zone-Punch Number | Action Description | Punched by | Punch SnapShot1 | Punch SnapShot2 | Closing SnapShot1 | Hotwork | ABB/CIMC Discipline | Company | Close Out Plan Date | Action by | Status | Action Comment | Date Cleared by ABB | Days Since Date Cleared by ABB | KBR Response | KBR Response Date | KBR Response by | KBR Remarks | KBR Category | KBR Discipline | KBR Screenshot | Date Cleared by KBR | Days Since Date Cleared By KBR | Seatrium Discipline | Seatrium Remarks | Checked By (Seatrium) | Seatrium Comments | Date Cleared By Seatrium | Days Since Date Cleared by Seatrium | Petrobras Response | Petrobras Response By | Petrobras Screenshot | Petrobras Response Date | Petrobras Remarks | Petrobras Discipline | Petrobras Category | Date Cleared by Petrobras | Days Since Date Cleared By Petrobras | Additional Remarks | ARC Reference No(HFE Only) | Modified | Modified By | Item Type | Path
E001C | M17 |  | M17-E001C | The escape route Connection between M17 and M13-B is Missing. | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[23b3f06775724a6b80ec6072d7d7edf2][1]_[2].png","originalImageName":"E001C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1c864cfafa064d70aae795aa7001acfb][2]_[20].png","originalImageName":"E001C-20251208"} | NO | SAFETY | ABB/CIMC | 09/12/2025 | CIMC | Close | 2025/12/05: The escape route has been updated 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 07/12/2025 | 9.00000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E002C | M17 |  | M17-E002C | The escape route Connection between M17 and M13-B to be Aligned | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1b72a351a6324a4092dd9d4112af3ed8][1]_[2].png","originalImageName":"E002C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6fab64e293354008b18234e00e554db8][2]_[16].png","originalImageName":"E002C-20251208"} | NO | SAFETY | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/08,the escape route had been updated to align with M13B module . 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 07/12/2025 | 9.00000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E003C | M17 |  | M17-E003C | Connection for the Escape route is missing in LEVEL-3 of M17 | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[5ae1839107bf43358149c6e5862dc96c][1]_[2].png","originalImageName":"E003C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[fb36b81c33d84a0583de6e46fa33951d][1]_[8].png","originalImageName":"M17 EC003C"} | NO | SAFETY | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05: The escape route has been updated 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 04/12/2025 | 12.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E004C | M17 |  | M17-E004C | Coaming is missing at level-1 aftside | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[55b756ca3aa849bd80a50945d5ac9a0f][1]_[2].png","originalImageName":"E004C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[be77126aba6d4cc1aac3c9ed7546feb1][2]_[10].png","originalImageName":"E004C"} | NO | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:Coaming has been updated 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 04/12/2025 | 12.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E005C | M17 |  | M17-E005C | SCBA to be moved outside | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[2276cd9dee7a4130bf4d7c203db83b60][1]_[2].png","originalImageName":"E005C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6205aa94e4d84ffa9d38f86c9baf2951][2]_[20].png","originalImageName":"E005C-20251209"} | YES | SAFETY | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05: The SCBA's position has been updated as comment. 2025/12/09, the SCBA had been shifted to outside column and the height is above monorail ,refer to snapshot. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 04/12/2025 | 21.0000000000000 | [5 empty] | Structure |  |  |  | Safety | [5 empty] | 26dec25: This punch can be closed. | Danilo |  | 25/12/2025 |  | Safety | [5 empty] | 26/12/2025 | ID: 372
E006C | M17 |  | M17-E006C | Additional New EEBD to be added outside near to the door as per PB Spec I-ET-3010.00-5400-947-P4X-004 in every Access of Protected Equipment. | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[28b53cc5f712480aab4a9a4ab581798a][1]_[2].png","originalImageName":"E006C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[94fb76dee50047678abfe43c9d2c320f][2]_[11].png","originalImageName":"M17 E006C +2 eebd"} | YES | SAFETY | Seatrium | 18/12/2025 | Seatrium | Pending Petrobras | 2025/12/08： The EEBD has been added as per comment 2025/12/08, as per close out meeting discussion , Seatrium need to double confirm with teams. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 07/12/2025 | 34.0000000000000 | [5 empty] | Safety |  |  |  | Safety |  | Tsen Tze Jia | 12 Jan: As per the latest model (20260109), EEBD Z-5434057 and Z-5434056 have been modelled in. PB to review and close this punch | 12/01/2026 | -1.58333333333576 | [5 empty] | Safety | [5 empty] | 12/01/2026 | ID: 96
E007C | M17 |  | M17-E007C | Fire Extingusher clashes with Handling Volume | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[9b5aa1d7b3c64af983a11192f3dd55a1][1]_[2].png","originalImageName":"E007C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9e6e15a81c384b0aa8f8279a757626f1][1]_[5].png","originalImageName":"M17 E007C"} | YES | SAFETY | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: The location of extinguisher has been updated 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 04/12/2025 | 12.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E008C | M17 |  | M17-E008C | IG541 Push button Door Volume to be Modelled | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[32e499b584f549af8c2d5b1c19dd63ff][1]_[2].png","originalImageName":"E008C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[38737668ecfb47e5bc384c7e60ca7ee7][2]_[10].png","originalImageName":"E008C-20251208"} | NO | SAFETY | ABB/CIMC | 06/12/2025 | CIMC | Pending Petrobras | 2025/12/08, the required door volume had been added. | 07/12/2025 | 34.0000000000000 | 19 Dec 2025: IG-541 Push Button door volume has been modelled. | 18/12/2025 | Indra/ Hong | Completed |  | Safety |  |  |  | Safety |  | Tsen Tze Jia | 12 Jan: As per the latest model (20260109), the push button door volume has been modelled. | 12/01/2026 | -1.61666666666861 | [5 empty] | Safety | [5 empty] | 12/01/2026 | ID: 96
E009C | M17 |  | M17-E009C | Fire Extingusher Support not aligned | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e0132e2c1a9744c78b082651ad60c287][1]_[2].png","originalImageName":"E009C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[79018ee2edcf4927b055173e512fe53b][1]_[7].png","originalImageName":"E009C-20251206"} | YES | SAFETY | ABB/CIMC | 05/12/2025 | CIMC | Close | 2025/12/06,the equipment support had been adjusted. 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 05/12/2025 | 11.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E010C | M17 |  | M17-E010C | Clashes with Matering Handling Route | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[09d4a86c72434877a502454784e19b22][1]_[2].png","originalImageName":"E010C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[221340162d6c422f93cfd3c424f27a85][1]_[4].png","originalImageName":"M17 E010C"} | YES | SAFETY | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: The Matering Handling Route has been updated 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 04/12/2025 | 12.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E011C | M17 |  | M17-E011C | Piping Support Missing | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e862b871bae54cb3ba1a1012f86dfc90][1]_[2].png","originalImageName":"E011C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2295f70e330a48c8840b28c0c6d2f941][2]_[16].png","originalImageName":"E011C-20251206"} | YES | SAFETY | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/06,the missing piping support had been added. 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 05/12/2025 | 11.0000000000000 | [5 empty] | Safety |  |  |  | Piping | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E012C | M17 |  | M17-E012C | Eye washer shall be moved to other side of the Battery room located near to the door | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[fa144ecdc7cc46f195fed5d645381156][1]_[2].png","originalImageName":"E012C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[fb664a70618f42339c6c788ffff24138][1]_[4].png","originalImageName":"M17 E012C"} | NO | SAFETY | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: The eyewash's position has been updated 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 04/12/2025 | 9.00000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 15/12/2025 | ID: 19
E013C | M17 |  | M17-E013C | Fire Extinguisher shall be moved to other side of the Battery room located near to the door | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7e34bf30f47e47a2b2557e461618e7d2][1]_[2].png","originalImageName":"E013C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b5052ec23cdb4a268da5b4b695f6e3ca][1]_[4].png","originalImageName":"M17 E013C"} | YES | SAFETY | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: The fire extinguisher's position has been updated 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 04/12/2025 | 12.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E014C | M17 |  | M17-E014C | Location of Safety shower Valve to be Evaluated to move to Level-4 | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e618e7443bb84b948d25ed065451ba29][1]_[2].png","originalImageName":"E014C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1ee6daf835c54c848dba8aeedce07205][2]_[13].png","originalImageName":"E014C-20251206"} | NO | SAFETY | ABB/CIMC | 05/12/2025 | CIMC | Close | 2025/12/06, this safety shower valve had been moved to level 4. 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 07/12/2025 | 9.00000000000000 | [5 empty] | Safety |  |  |  | Piping | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E015C | M17 |  | M17-E015C | FIRE Hydrant equiment Location is incorrect and to be aligned with equipment Support Location. | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0794c3449599486698d3665e0935741e][1]_[2].png","originalImageName":"E015C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c391a858fb1b40739b61212caf5940ee][1]_[4].png","originalImageName":"M17 E015C"} | YES | SAFETY | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: The fire locker's position has been updated. 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 04/12/2025 | 12.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E016C | M17 |  | M17-E016C | Valve postion to be rotated 90deg to behind side | Tsen Tze Jia | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0b2d1ecfcab74efa9032f62cd749f81e][1]_[2].png","originalImageName":"E016C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[89c3f1d56f5e4153b72671b51866dc86][2]_[11].png","originalImageName":"E016C-20251206"} | NO | SAFETY | ABB/CIMC | 05/12/2025 | CIMC | Close | 2022/12/06,the hydrant valve position had been rotate 90 degree to behind side. 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 07/12/2025 | 6.00000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 15/12/2025 | ID: 19
E017C | M17 |  | M17-E017C | Ladder Model is incorrect | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0e34c74c41c24579a87e507cd4cf81d3][1]_[2].png","originalImageName":"E017C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a76749be041e4b56bea4fa327ea21713][1]_[8].png","originalImageName":"E017C"} | NO | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:Ladder has been updated 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 04/12/2025 | 12.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E018C | M17 |  | M17-E018C | Handrail is missing | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8e149ec1c3224a81aef308cfa7293f67][1]_[2].png","originalImageName":"E018C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c46f7088d7364a3b9ba439d989f371e9][1]_[8].png","originalImageName":"E018C"} | NO | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:Handrail has been updated 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 04/12/2025 | 12.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E019C | M17 |  | M17-E019C | General comment for all Level :Handrail clearance Gap shall be 75mm | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d1b19c2c53354027b119e31379e062bc][1]_[2].png","originalImageName":"E019C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[dbd2e137850d4b4c842c1446a900c0ac][2]_[42].png","originalImageName":"E019C2"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/11:With reference to the typical drawing of KBR handrail standard, I-DE-3010.2S-1400-140-S2N-004_C, the center-to-center distance of the handrail is 125mm, the minimum clearness between handrail boundary is 76.7mm | 10/12/2025 | 28.0000000000000 | KBR STR (22 Dec 2025): Agreed to ABB comment that center to center as per standard drawing is 125 mm | 22/12/2025 | Bobby Pramayudha |  |  | Structure |  |  |  | Structure |  | Caryn Tan | 24-Dec-25: Model updated. | 23/12/2025 | 15.0000000000000 | Noted | Maxwell |  | 08/01/2026 |  | Structure | [5 empty] | 09/01/2026 | ID: 476
E020C | M13R |  | M13R-E020C | Vertical Ladder Safety Gate Clash with Escape route | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[ce7a976851154f71baee7236ca16a91e][1]_[2].png","originalImageName":"E020C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[583aca6facac40c4aaa3cce616e1b3ce][1]_[4].png","originalImageName":"M13R E020C"} | NO | SAFETY | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: The escape route has been updated. 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 04/12/2025 | 9.00000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 15/12/2025 | ID: 19
E021C | M13R |  | M13R-E021C | Cable Tray Clash with Escape route volume | Tsen Tze Jia | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[01a9a44c50df4b25ad6d159357570fc9][1]_[2].png","originalImageName":"E021C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[5434e6397f104f80ad7747eb69c1458c][2]_[11].png","originalImageName":"E021C-20251209"} | NO | SAFETY | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/09, the clash between escape route and cable tray had been cleared. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 08/12/2025 | 30.0000000000000 | [5 empty] | Safety |  |  |  | Instrumentation | [5 empty] | Closed | Julius Orzales |  | 08/01/2026 | closed | Instrumentation |  | 08/01/2026 | -1.00000000000000 |  |  | 09/01/2026 | ID: 484
E022C | M13R |  | M13R-E022C | Coaming to be modelled | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4d0e0c5c788e454bab97c12b05c3343b][1]_[2].png","originalImageName":"E022C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[e79be05831c44ed486613d040763a27f][1]_[9].png","originalImageName":"E022C"} | NO | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:Coaming has been updated 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 04/12/2025 | 9.00000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 15/12/2025 | ID: 19
E023C | M13R |  | M13R-E023C | General comment for all Level :Handrail clearance Gap shall be 75mm | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[cac53941f81d470796428492f0fd5d9c][1]_[2].png","originalImageName":"E023C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[5de550837fd04179bccc96e063215e71][2]_[14].png","originalImageName":"E023C-20251205"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:With reference to the typical drawing of KBR handrail standard, I-DE-3010.2S-1400-140-S2N-004_C, the center-to-center distance of the handrail is 125mm.the minimum clearness between handrail boundary is 76.7mm 2025/12/09, the clearance gap for all handrail had been double check and confirm the cleanrance is 76mm. | 04/12/2025 | 34.0000000000000 | KBR STR (22 Dec 2025): Agreed to ABB comment that center to center as per standard drawing is 125 mm | 22/12/2025 | Bobby Pramayudha |  |  | Structure |  |  |  | Structure |  | Caryn Tan | 24-Dec-25: Model updated. | 23/12/2025 | 15.0000000000000 | Noted | Maxwell |  | 08/01/2026 |  | Structure | [5 empty] | 09/01/2026 | ID: 476
E024C | M13R |  | M13R-E024C | General Comment :Fire locker Support to be align with fire locker Equipment | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4c1c6cfadf0c4926912141e1bd115e58][1]_[2].png","originalImageName":"E024C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7d162acc9c38451f9c958e550533c863][2]_[22].png","originalImageName":"E024C1"} | YES | SAFETY | ABB/CIMC | 07/12/2025 | CIMC | Pending Petrobras | 2025/12/05:Fire Locker Supports and Fire Locker Equipment have been aligned. 2025/12/11：All fire locker supports have been aligned with the fire locker equipment. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 10/12/2025 | 28.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [10 empty] | Safety | [5 empty] | 09/01/2026 | ID: 476
E025C | M13R |  | M13R-E025C | Support for Fire extinguisher and Fire Locker is Missing and to be Modelled | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c4db9eaf9f4f4768bcffe5fdc1230d52][1]_[4].png","originalImageName":"E025C-M13R"} | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot2][32]_[b55ba78ca95b4e18813f0dcedaa35483][1]_[6].png","originalImageName":"E025C-M13R_2"} | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[5190091eabd840d2b06423d17ab7d5c6][2]_[37].png","originalImageName":"EC025C1"} | YES | SAFETY | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/05:the Support has been updated and align with equipment 2025/12/11：All supports for fire extinguishers and lockers have been updated. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 10/12/2025 | 28.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [5 empty] | Noted. | Maxwell |  |  |  | Structure | [5 empty] | 09/01/2026 | ID: 476
E026C | M13R |  | M13R-E026C | General Comment :Support location for fire extingusher to be aligned with fire extinguisher Z-54281001 Z-54281002 Z-54281003 Z-54281013 Z-54281012 Z-54281018 Z-54281016 Z-54281017 | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0e56af0283574417a7d0ea2ea9acc668][1]_[4].png","originalImageName":"E026C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[52a24d0da3d440c4b67bae453d0283cb][2]_[20].png","originalImageName":"E026C1"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:The support position has been aligned with the fire extinguisher. 2025/12/08, as per meeting discussion ,the 1014 equipment shall be shift a little to match 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 04/12/2025 | 12.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E027C | M13R |  | M13R-E027C | CPE /PPE CABINET support Structure bottom opening to be covered | Tsen Tze Jia | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[01ecdfd39e73487b8a3ca07d49404b93][1]_[4].png","originalImageName":"E027C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[51855d577a1d4c609ef22c165eb07186][2]_[10].png","originalImageName":"E027"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:The openings in the CPE/PPE support structure have been closed with plates. 2025/12/09,the opening below CPE /PPE support had been closed with plate for both level 1 and 2 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 04/12/2025 | 34.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [5 empty] | Noted | Maxwell |  | 08/01/2026 |  | Structure | [5 empty] | 09/01/2026 | ID: 476
E028C | M17 |  | M17-E028C | CPE /PPE CABINET support Structure bottom opening to be covered for LEVEL-1 and Level-2 | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[fa0a08ba4e6c4500950045ef691c21af][1]_[4].png","originalImageName":"E028C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[d86c2ea4c04442c096b8056208d4e9cb][2]_[12].png","originalImageName":"E028"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/06：The openings in the support structures for CPE/PPE Level 1 and Level 2 have been closed with steel plates. 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 05/12/2025 | 11.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E029C | M13R |  | M13R-E029C | SCBA Support is missing and to be Modelled, Support Location for EBD Z-5434054 & Z-5434452 to be aligned with Equipment | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[30f3df8a411e48eba80d901f501d9e9a][2]_[21].png","originalImageName":"E029C-20251208"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[f657dca4429a477099377ba4080501e6][2]_[35].png","originalImageName":"M13R E029"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:the Support has been updated and align with equipment 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 04/12/2025 | 35.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [5 empty] | Closed | Julius Orzales |  | 08/01/2026 | Closed | Safety |  | 08/01/2026 | 0 |  |  | 09/01/2026 | ID: 484
E030C | M13R |  | M13R-E030C | Powder Fire Extinguisher Handle clashes with Material Handling Volume. | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4d66a35aad1748719e7b545c1152d9d0][1]_[4].png","originalImageName":"E030C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[cad8f363d5b243be8e9416fa664919b1][2]_[10].png","originalImageName":"E030C-20251207"} | YES | STRUCTURAL | ABB/CIMC | 08/12/2025 | CIMC | Close | 2025/12/07, the powder fire extinguisher already rotate and shifted to another position to avoid clash with handling route 2025/12/08, the support for fix to be added 2025/12/09, two support had been added to fix this portable fire extinguisher 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 07/12/2025 | 18.0000000000000 | [5 empty] | Structure |  |  |  | Safety | [5 empty] | 26dec25: This punch can be closed. | Danilo |  | 25/12/2025 |  | Safety | [5 empty] | 26/12/2025 | ID: 372
E031C | M13R |  | M13R-E031C | Vaccum Breaker to be separated from Fire Hydrant Location and to make elbow Branch for safe operation of personel | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[81266055e261467fbd45408266a25c2e][1]_[4].png","originalImageName":"E031C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[53d811a87ad24d6eb6addae41bd497aa][1]_[8].png","originalImageName":"E031C"} | NO | SAFETY | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05： Vaccum breaker has been rearranged. 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 04/12/2025 | 9.00000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 15/12/2025 | ID: 19
E032C | M13R |  | M13R-E032C | Safety cage Height shall not be more than 2m | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[084b6ca0ac474de4ad887ce0ea0fa7ca][1]_[4].png","originalImageName":"E032C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[11e962c4b498449ca81def242dd6476d][2]_[13].png","originalImageName":"E032"} | NO | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/06：The height of the safety cage has been adjusted to 2 meters. 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 05/12/2025 | 11.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E033C | M13R |  | M13R-E033C | Safety Cage Support to be extended to cover the Gap | Danilo Alexandre Lima Cardosoo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[67f6d260131344c3b3d9d5b66ffc87d0][1]_[5].png","originalImageName":"E033C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[74ffb560a5514a78b04a62792a779998][2]_[31].png","originalImageName":"E033C1"} | NO | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/06：The safety cage support model has been updated. 2025/12/08, as per meeting discussion ,the top of cage shall be curve . 2025/12/09, the curve plate of safety cage had been updated. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 05/12/2025 | 36.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [6 empty] | Julius Orzales |  | 11/01/2026 |  | Safety |  | 11/01/2026 | -1.00000000000000 |  |  | 12/01/2026 | ID: 484
E034C | M17 |  | M17-E034C | Smoke Detector YST-M17-101-A008 Volume clashes with Tubing Cable tray | Julimar | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[39d5129c43894f69afc0d10409609e23][1]_[4].png","originalImageName":"E034C-M17"} | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot2][32]_[c1a326d735f6486c9872fafd907b478d][2]_[12].png","originalImageName":"E034C-20251204"} | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6b86f04ed7d64486aa3bd1f3d64be33d][2]_[34].png","originalImageName":"034"} | NO | INSTRUMENTATION | ABB/CIMC | 08/12/2025 | CIMC | Close | 2025/12/09, the clash had been cleared. | 08/12/2025 | 31.0000000000000 | KBR has no comments. |  | Roberto |  |  | Instrument |  |  |  | Instrumentation |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 15.3750000000000 | [U5D6 - 09/JAN/2026] Clash has been solved. | U5D6 |  | 08/01/2026 |  | Instrumentation |  | 08/01/2026 | 0 |  |  | 09/01/2026 | ID: 399
E035C | M17 | Level1&2 | M17-E035C | General Comments for Level-1 & Level-2 Transformer Room- Smoke Detector Location and Volume to be modified to avoid clash with other structure and cable trays | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6333e48538d34cde85b758f771f802ee][1]_[5].png","originalImageName":"E035C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[54044f40889c47d9a92d70a2fb424049][2]_[24].png","originalImageName":"E035C-20251226"} | NO | INSTRUMENTATION | ABB/CIMC | 25/12/2025 | CIMC | Pending Petrobras | 2025/12/26, The detector maintenance volume clash had been cleared , refer to attachement and viewpoint for all transformer detector.ABB propose to use lifting table (max 6m ) and handling tools to replace detector. | 25/12/2025 | 15.0000000000000 | There are related punch list items that were similar to this and have been cleared. SEA to advise on the acceptance of ABB's proposal regarding access. | 04/01/2026 | Roberto |  |  | Instrument |  |  |  | Instrumentation |  | Guanyu Zhu | 05/01/2026: Seatrium no comment. ABB proposal subject to PB operation team final approval | 05/01/2026 | 4.30972222222044 |  |  |  |  | [U5D6 - 11/JAN/2026] This punch requires operation team agreement. I am consulting them, discussion is still ongoing. | Instrumentation | [5 empty] | 11/01/2026 | ID: 399
E036C | M17 |  | M17-E036C | To update the model of PFP with cutout | Camila | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d506e33c3be94a77afcca8020683c5d7][1]_[5].png","originalImageName":"E036C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[3755e0b0e83845049df63eaffc66c76c][2]_[18].png","originalImageName":"M17-E036"} | NO | ARCHITECTURAL | ABB/CIMC | 07/12/2025 | CIMC | Pending Petrobras | 20225/12/05，the PFP already updated based on comments . | 04/12/2025 | 37.0000000000000 | PFP is already updated at the door location. | 19/12/2025 | Suresh |  |  | Architecture |  |  |  | Architecture |  | Tsen Tze Jia | 12 Jan: As per the latest model (20260109), PFP model has been updated as per comment. | 12/01/2026 | -1.61388888888905 | [5 empty] | Architecture | [5 empty] | 12/01/2026 | ID: 96
E037C | M17 |  | M17-E037C | One No Peforated floor tile is missing in Level-2 | Camila | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8082297b716d4ff6b22c8d8fbf46b140][1]_[5].png","originalImageName":"E037C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[eec944cd92e14ecc87e22d90b5bac919][1]_[7].png","originalImageName":"M17-E037"} | NO | ARCHITECTURAL | ABB/CIMC | 04/12/2025 | CIMC | Pending Petrobras | 12/5/2025： Added the missing Peforated floor tile. | 04/12/2025 | 37.0000000000000 | The missing perforated tile is already added. | 19/12/2025 | Suresh |  |  | Architecture |  |  |  | Architecture |  | Tsen Tze Jia | 12 Jan: As per the latest model (20260109), the perforated tiles floor has been modelled. | 12/01/2026 | -1.61597222222190 | [5 empty] | Architecture | [5 empty] | 12/01/2026 | ID: 96
E038C | M13R |  | M13R-E038C | Door Position to be Modelled correctly (clashing with wall Panel) | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a897e1a2d1cf409782ce4fed4e405326][1]_[6].png","originalImageName":"E038C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[81b2d07636ae4b9daa112f66768e68b4][1]_[8].png","originalImageName":"M17-E038"} | NO | ARCHITECTURAL | ABB/CIMC | 04/12/2025 | CIMC | Pending Petrobras | 12/5/2025: Door Position be updated. | 04/12/2025 | 37.0000000000000 | Door is already shifted to avoid clash with wall panel. | 19/12/2025 | Suresh |  |  | Architecture |  |  |  | Architecture |  | Tsen Tze Jia | 12 Jan: As per the latest model (20260109), the position of the door has been updated correctly. | 12/01/2026 | -1.62013888888760 | [5 empty] | Architecture | [5 empty] | 12/01/2026 | ID: 96
E039C | M17 |  | M17-E039C | Handrail Kickplate is missing and to be Modelled (Kick Plate shall be Ship Loose).ABB to add a note in Design Dwg for items to be installed on board. | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[014235f52d05494aaa7628719585dd4f][1]_[6].png","originalImageName":"E039C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[f823da3a168b4870b8a97519f9ef1518][2]_[11].png","originalImageName":"E039"} | NO | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:The Ship Loose Coaming has been updated and added. 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 04/12/2025 | 12.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E040C | M17 |  | M17-E040C | Tubing Cable Tray to be clear from the Hand rail | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6c2171ffa5764396937d69e6d7b02957][1]_[6].png","originalImageName":"E040C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[cb27393d85a44c9ba86ff970f7c00425][2]_[33].png","originalImageName":"E40"} | YES | SAFETY | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, The damper control panel had been shifted to clear the interface hndrail and stair space. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 09/12/2025 | 30.0000000000000 | [5 empty] | Safety |  |  |  | Instrumentation | [9 empty] | [U5D6 - 09/JAN/2026] Sending to PB Safety (danilo). I cannot see where the handrail is / was. Besides, KBR/SEA fields are empty | Safety | [5 empty] | 09/01/2026 | ID: 399
E041C | M17 |  | M17-E041C | Calculation for Secondary structure where Monorail support is taken support from Primary beam | Maxwell | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[eaadf9902a404cf9bd931f283d71de65][1]_[5].png","originalImageName":"E041C-M17"} |  |  | NO | STRUCTURAL | ABB/CIMC | 18/12/2025 | CIMC | Pending KBR | 2025/12/08：For Secondary Beam which support the monorail, it will not be reduce the elastic modules and will be check in SOC condition(Sec.6.9.1 UC Result of Static Operational Condition) of inplace report. 2025/12/23:The monorail beam and its support structure global check (include secondary beam) has been check in SOC of inplace report. the local datail UC plots has email to Rommel by attachment. this part will be also added in Local calculation report in next revision. 2026/01/04,please find attached advance coply for monorail calculation. | 22/12/2025 | 11.0000000000000 | KBR STR (22 Dec 2025): The model analysis at supporting structure for the monorail shall be expanded to include secondary and primary in the analysis. The load on primary and secondary either dead load and live load (if applicable as per design premise) shall also be included beside the load on monorail during operation. Furthermore, the Stress Ratio check to be presented for monorail, its supports plus secondary and primary that are affected KBR STR (29 Dec 2025): Noted for the update by ABB/CIMC. Await the updated calculation in the inplace next revision. ABB/CIMC to attach the result for advanced review | 22/12/2025 | Bobby Pramayudha |  |  | Structure |  |  |  | Structure | [10 empty] | Structure | [5 empty] | 04/01/2026 | ID: 539
E042C | M17 |  | M17-E042C | To verify newly updated interface staircase with KBR | Caryn Tan Siu Sze | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6fcb5544fbae4af9b0e98249831cb69d][1]_[5].png","originalImageName":"E042C-M17"} |  |  | YES | STRUCTURAL | ABB/CIMC | 11/12/2025 | ABB | Pending Seatrium | 2025/12/11：ABB /CIMC have updated these stair as per standard stairs typical details / I-DE-3010.2S-1400-140-S2N-002_Rev.D and SEATRIUM's instruction, KBR will update the sliding pad, grating and hanrail accordingly. | 10/12/2025 | 17.0000000000000 | KBR STR (29 Dec 2025): Sliding pad, grating and handrail have been updated as per 3D dated 23 Dec 2025, see M17-E042C KBR STR 20251229 attachment | 29/12/2025 | Bobby Pramayudha |  |  | Structure | M17-E042C KBR STR 20251229 attachment |  |  | Structure | [10 empty] | Structure | [5 empty] | 29/12/2025 | ID: 596
E043C | M13R |  | M13R-E043C | Handrail model to be rectified | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[697d18412d7c47fc85650033130dcc58][1]_[5].png","originalImageName":"E043C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7ed2a916c6084a21a070af3931c248a1][1]_[9].png","originalImageName":"E043C-20251205"} | NO | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05，the handrail model had been updated ,refer to snapshot. 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 04/12/2025 | 9.00000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 15/12/2025 | ID: 19
E044C | M13R |  | M13R-E044C | Handrail model to be rectified | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[45faf82844ef46d1b4df679d1765bfc5][2]_[12].png","originalImageName":"E044C-20251202"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[5463d776e5974d1b85397b8d9a0c0749][2]_[14].png","originalImageName":"E044C-20251205"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:With reference to the typical drawing of KBR handrail standard, I-DE-3010.2S-1400-140-S2N-004_C, the center-to-center distance of the handrail is 125mm, the minimum clearness between handrail boundary is 76.7mm 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 04/12/2025 | 12.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E045C | M13R |  | M13R-E045C | Coaming need to be modified infront of the Ladder for the Escape route from Level-3 to Level-2 ,Dimension to be verified. | Tulio/Maxwell | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[22baad6bfa664a20a0fb424cce71471d][1]_[6].png","originalImageName":"E045C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[317f7cbbf9cb4fc0b855a5dad9c8a5f4][2]_[13].png","originalImageName":"E045"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05:With reference to the screenshot, the model has been updated. 2025/12/08, as per close out meeting discussion ,customer agree to close this punch . | 04/12/2025 | 12.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E046C | M17 |  | M17-E046C | Lifting lugs for the Removable wall Panel to be Modelled | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e9d3fa3a048c45218aeb238ae6e4bc14][1]_[5].png","originalImageName":"E046C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1df24e8f94f140a29893da6bf58d30fc][2]_[16].png","originalImageName":"E046C-20251206"} | NO | MATERIAL HANDLING | ABB/CIMC | 07/12/2025 | CIMC | Pending Petrobras | 2025/12/06,the lifting lug for the removal wall panel already added. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 05/12/2025 | 8.00000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [9 empty] | 10Dec25_B0RG_Ok | Mechanical Handling | [5 empty] | 15/12/2025 | ID: 19
E047C | M17 |  | M17-E047C | Fire Hydrant,SCBA and EEBD clashing with Material Handling volume | Tulio/Danilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c8b0f29ec101453d8cbb4f909023a1a6][1]_[5].png","originalImageName":"E47"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[ba3fa6c80af842cab16bcdc68245c308][2]_[18].png","originalImageName":"E047C-20251211"} | YES | SAFETY | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the clash between safety equipment and material handling operation volume had been cleared. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 10/12/2025 | 15.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [5 empty] | 26dec25: This punch can be closed. | Danilo |  | 25/12/2025 |  | Safety | [5 empty] | 26/12/2025 | ID: 372
E048C | M17 |  | M17-E048C | Pulling Post Bolt Modelling is incorrect, the Length of bolt shall be shorter. | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[3db86556c5b647a3a3166f1677690df8][1]_[5].png","originalImageName":"E48"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[41c9157acbd744cf9edf61f28ac7ffbc][2]_[25].png","originalImageName":"E048C-20251209"} | NO | MATERIAL HANDLING | ABB/CIMC | 08/12/2025 | CIMC | Pending Petrobras | 2025/12/09, the screw had been updated in 3D model 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 5.00000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [9 empty] | 10Dec25_B0RG_Ok | Mechanical Handling | [5 empty] | 15/12/2025 | ID: 19
E049C | M17 |  | M17-E049C | Cable tray to be removed to clear the space for padeye | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[df965d914e7b4e0e8b693f7add488a11][1]_[5].png","originalImageName":"E49"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[99b41bb58952430191ab14aa212ce4ca][2]_[32].png","originalImageName":"049"} | NO | MATERIAL HANDLING | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/08, the cable tray already shift to another place and the space below padeye had been cleared 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 07/12/2025 | 31.0000000000000 | [5 empty] | Mechanical Handling |  |  |  | Electrical | [5 empty] | 09/01/25-UR7U- Noted. Cable tray shifted | Welton |  | 08/01/2026 | 10Dec25_B0RG_Ok | Electrical |  | 08/01/2026 | -1.00000000000000 |  |  | 09/01/2026 | ID: 398
E050C | M17 |  | M17-E050C | Lighting Fixture clashes with Material handling Volume, material handling Volume to be verified | Tuilio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[fd4c308e69264513a4ed6d71ddb41534][1]_[5].png","originalImageName":"E50"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[e3c831d4f2e644f18d1a408bf3badcab][2]_[13].png","originalImageName":"E050C-20251208"} | Re-work | MATERIAL HANDLING | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/808, the lighting had been adjusted to avoid obstruct the monorail operation space and handling route. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | [7 empty] | Mechanical Handling |  |  |  | Electrical | [5 empty] | 09/01/26-UR7U-Noted. Lighting had been adjusted. | Welton |  | 08/01/2026 | 10Dec25_B0RG_Ok | Electrical |  | 08/01/2026 | -1.00000000000000 |  |  | 09/01/2026 | ID: 398
E051C | M17 |  | M17-E051C | Handling Volume to be Modeled Considering 910mm height. | Tulio/Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[744b5266850a413395d8a8afc89e0d67][1]_[6].png","originalImageName":"E51"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7fb4c668a83d48e19b188f9e018973cd][2]_[10].png","originalImageName":"E051"} | NO | MATERIAL HANDLING | ABB/CIMC | 04/12/2025 | CIMC | Pending Petrobras | 5/Dec/2025: The LV coil size of the transformer TF-5143001A/B is OD865mm×H890mm, and the HV coil size is OD560mm×H910mm. In the 3D model, we simulate the coils according to OD865mm×H910mm. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 04/12/2025 | 12.0000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [9 empty] | 10Dec25_B0RG_Ok | Mechanical Handling | [5 empty] | 17/12/2025 | ID: 537
E052C | M13R |  | M13R-E052C | General comment: PFP Coating is missing for the structure | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[64cee57ba2004448b940b94c779e23d1][1]_[5].jpg","originalImageName":"E052C-M13R_1"} | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot2][32]_[bb763c8d025f4cd996f54601e20a5135][1]_[7].png","originalImageName":"E052C-M13R_2"} | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9b57895d0d52480dad3ee53609c3bcfa][2]_[15].png","originalImageName":"E052"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E053C | M13R |  | M13R-E053C | General comment: PFP Coating is missing for the structure | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[34683f33adb641b4b2d44c90bf4f57e5][1]_[5].png","originalImageName":"E53"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c951ee9fc0d04c53a69cf86ee17a05da][2]_[11].png","originalImageName":"E053"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E054C | M13R |  | M13R-E054C | PFP coating shall be match with drawing | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[16728f071dd94e798be68d28d67fc8c1][1]_[5].png","originalImageName":"E054C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[ec9c8c8eeba546fcad870dd67531fc60][2]_[15].png","originalImageName":"E054"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E055C | M17 |  | M17-E055C | General comment: PFP Coating is missing for the structure of Level-1 Deck | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7096bdd1c358471bb90fe017ad8eadf1][1]_[5].png","originalImageName":"E055C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9cbc7643404f480c83fac3a27dd4c2f9][2]_[11].png","originalImageName":"E055"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E056C | M17 |  | M17-E056C | 1 meter Extension PFP coating shall be followed as per drawing in 3D Model | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[29b276d26c4d4e8db05a61c4dcfda50c][1]_[5].png","originalImageName":"E056C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a70a77ed8b5c44c29e9f6179a438d79c][2]_[10].png","originalImageName":"E056"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E057C | M17 |  | M17-E057C | To update the PFP location based in basic design at air lock | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[bf9825e755c9439d9b6e9a55a7af496f][1]_[5].png","originalImageName":"E057C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[028fb1c1829f4a73b6574e140b963104][2]_[11].png","originalImageName":"E057"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E058C | M17 |  | M17-E058C | PFP Coating shall be align with the Drawing , 3D Model to be updated | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[add7af4d0d9c4e259be1f8c00ee0f6bd][1]_[5].png","originalImageName":"E058C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[5df4d0d521b345efadd8d859d6eca552][2]_[10].png","originalImageName":"E058"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E059C | M17 |  | M17-E059C | PFP Coating is missing ,shall be align with Drawing in Level-3 | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[fbf40f482f6249cebe2d76ccf0f28dc8][1]_[5].png","originalImageName":"E059C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[930f114be6624456bdca560e56fb27b5][2]_[10].png","originalImageName":"E059"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E060C | M17 |  | M17-E060C | PFP Coating is missing ,shall be align with Drawing in Level-4 | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[420d13d7debe4f8b9c65fa79f25fa3c5][1]_[5].png","originalImageName":"E060C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[47e2d07474ac4752974a1188bd0973af][2]_[10].png","originalImageName":"E060"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E061C | M17 |  | M17-E061C | PFP Coating is missing ,shall be align with Drawing for all Levels | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8c7f8cbe886f40c1b3289a0f34795ba7][1]_[5].png","originalImageName":"E061C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1b7ac748e77245f0904e63de23dc5389][2]_[10].png","originalImageName":"E061"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E062C | M17 |  | M17-E062C | PFP Coating is missing for column ,shall be align with Drawing | Danilo Alexandre Lima Cardosoo/Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[515c334727734eb185110a8dabcc6b33][1]_[6].png","originalImageName":"E062C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bdf26dcbc38b425ca461d2c4609118de][2]_[11].png","originalImageName":"E062"} | NO | PAINTING | ABB/CIMC | 06/12/2025 | CIMC | Close | 7/Dec/2025：The 3D model has been updated.refer to snapshot. 2025/12/08, as per close out meeting , customer agree to close this punch | 06/12/2025 | 10.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 17/12/2025 | ID: 537
E063C | M17 |  | M17-E063C | Additional Padeye to be provided for material handling the equipments | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[62c7477e92ce49209b62994cdf2c354b][1]_[5].png","originalImageName":"E063C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[4da303c2797f42859aaf5d2774e3e525][2]_[12].png","originalImageName":"E063C-20251206"} | Re-work | MATERIAL HANDLING | ABB/CIMC | 05/12/2025 | CIMC | Pending Petrobras | 2025/12/06, the required pad eye had been added , two pad eye can be used for hatch lifting 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 05/12/2025 | 11.0000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [9 empty] | 10Dec25_B0RG_Ok | Mechanical Handling | [5 empty] | 17/12/2025 | ID: 537
E064C | M17 |  | M17-E064C | Provide the details for the fixing the frame and show the connection details | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e8363d74d0e44ca988ac4bb45d814b4d][1]_[5].png","originalImageName":"E064C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c2fdff54f8784470b420654d65ee986f][2]_[38].png","originalImageName":"E064-2"} | NO | MATERIAL HANDLING | ABB/CIMC | 04/12/2025 | CIMC | Pending KBR | 5/Dec/2025: The 3D model has been updated. The attached snap includes the specific dimensions of the Hatch bracket. Lifting lug are set on both sides of each bracket for fixing the bracket to the trolley and fixing the Hatch. This bracket has been confirmed by Hatch's supplier. 2025/12/10, as per close out meeting discussion ,the new added payeye location is acceptable . But to provide the below information : 1-the actual weight of hatch ; 2-the lifting and transfer procedure to trolley 3- the fixed method and connetion detail in the trolly ; 07/Jan/2026: Above issues has already complete as below: 1. The actual weight of hatch is about 1.21T 2.3. lifting procedue and fixed method had been included in "Closing Snapshot" | 06/01/2026 | -1.00000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [10 empty] | Mechanical Handling | [5 empty] | 07/01/2026 | ID: 844
E065C | M17 |  | M17-E065C | Seatrium/KBR to provide the manual/Procedure for removal of 6T transformer for the well service VFD | Juliana/Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4fd0695eeb04466e8c466492ad5ba769][1]_[5].png","originalImageName":"E065C-M17"} |  |  | NO | MATERIAL HANDLING | Seatrium | 09/12/2025 | Seatrium | Pending Petrobras | 2025/12/10, for the VFD which transformer weight is more than 5t, CIMC propose to use monorial to lift the entire transformer and transfer to outsider by skiding rail .Because the transformer part don't have lifting lug , the proposal is to use belt cross the bottom hole to fix with monorail trolley. 2025/12/10, as per close out meeting ,this punch can be transfer to PB close. | 09/12/2025 | 4.00000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [9 empty] | 10Dec25_B0RG_Ok | Mechanical Handling | [5 empty] | 15/12/2025 | ID: 19
E066C | M17 |  | M17-E066C | Check the Feasibility of moving the deck trolley through Equipment door sill of 26mm | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[ecc39f56bfb84b5d91917da199b7a052][1]_[5].png","originalImageName":"E066C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[8d7b9c36d520404aa7d7035bb4700410][2]_[13].png","originalImageName":"E066"} | NO | MATERIAL HANDLING | ABB/CIMC | 30/12/2025 | ABB | Pending Petrobras | 8/Dec/2025: Deck trolley suppliers believe that there is a certain risk in forcibly crossing the 26mm threshold when the load is relatively heavy. Therefore, it is recommended to apply the portable ramp here. There are four in total, two each inside and outside the door (Each ramp capacity, L:450mm*W:800mm*H:32mm, Slope: Less than 4°) 2025/12/10, as per close out meeting discussion ,the provided proposal is acceptabel ,this punch can be transfer to PB close. | 07/12/2025 | 36.0000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [9 empty] | 10Dec25_B0RG_Ok | Mechanical Handling | [5 empty] | 13/01/2026 | ID: 537
E067C | M17 |  | M17-E067C | Provide the Simulation model for removing the internal components of VFD, Seatrium /KBR to provide the material handling procedure for the removal of the internal components,currently cable tray clash with A frame | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[85439e1596f946e6abf3a3aa93d3d711][1]_[5].png","originalImageName":"E067C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[893d569ed6f74ea3b75590c970026465][2]_[19].png","originalImageName":"E067"} | NO | MATERIAL HANDLING | Seatrium | 30/12/2025 | Seatrium | Pending KBR | 8/Dec/2025: Handling simulation of VFD has been added in 3D model 2025/12/10, as per close out meeting discussion , KBR to check with equipment vendor to confirm below issue for all VFD: 1- if the entire transformer need to be removed , or we can just replace the partly componenets.; 2- if the top beam of transformer enclosure can be removed , for partly components removed from inside to outside . | 07/12/2025 | 29.0000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [10 empty] | Mechanical Handling | [5 empty] | 07/01/2026 | ID: 844
E068C | M17 |  | M17-E068C | Provide the Model simulation for removing the motor,cooling coil and the fan from AHU unit. | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1a32e71949294f13b1eef64e0c9d4ced][1]_[5].png","originalImageName":"E068C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[4a38662fa5d94217991044c0819a5b80][2]_[21].png","originalImageName":"E068C"} | NO | MATERIAL HANDLING | ABB/CIMC | 30/12/2025 | ABB | Pending KBR | 7/Jan/2026: The components that require maintenance inside the AHU have been created in the 3D model. | 06/01/2026 | 6.00000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [10 empty] | Mechanical Handling | [5 empty] | 13/01/2026 | ID: 537
E069C | M17 |  | M17-E069C | Provision to place the belt on the battery cell to lift to be clarified , belt for battery to be supplied | Juliana/Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[734f9800bf024e2fae5ed340ee21d59a][1]_[5].png","originalImageName":"E069C-M17"} |  |  | NO | MATERIAL HANDLING | ABB | 30/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [10 empty] | Mechanical Handling | [5 empty] | 17/12/2025 | ID: 537
E070C | M17 |  | M17-E070C | Two sets of ramp (4nos) to be provided and to be modelled | Juliana/Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[240d59b56dcd4ae5b5b2aa5901dd48ea][1]_[5].png","originalImageName":"E070C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[d047a6e208284939afe7c8f9ced888d2][2]_[10].png","originalImageName":"E070"} | YES | MATERIAL HANDLING | ABB/CIMC | 04/12/2025 | CIMC | Pending Petrobras | 5/Dec/2025: The battery room and air lock room are plastered with ceramic tile, so the indoor threshold height is only 6mm, and there is no need to set up a portable ramp. Therefore, in this scenario, we only set up portable ramps outdoors. However, CIMC will still provide two pairs of ramps (L:450mm*W:800mm*H:32mm, Slope: Less than 4°) to facilitate use in other scenarios. 2025/12/10, as per close out meeting discussion , this punch can be transfer to PB close. | 04/12/2025 | 12.0000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [9 empty] | 10Dec25_B0RG_Ok | Mechanical Handling | [5 empty] | 18/12/2025 | ID: 537
E071C | M17 |  | M17-E071C | Lightng fixture postion to be shifted far way or Removable type from Material Handling Volume | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a51648fa890e43cd9bb92e518c049e11][1]_[5].png","originalImageName":"E071C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9e4d952b7b5a431194d6f3be65694fa5][2]_[17].png","originalImageName":"E071"} | NO | MATERIAL HANDLING | ABB/CIMC | 07/12/2025 | CIMC | Pending KBR | 9/Dec/2025: The length of Davit's boom is set at 2600mm, even when transporting the largest component, the distance from this Light to the component is approximately 500mm. Therefore, this lamp has no impact on material handling. It is recommended to keep it in its original position. 2025/12/10, as per close out meeting discussion , PB accept the lighting fixture position ,but the davit beam shall update to corret value with 2.6m 2025/12/11, The Length of davit beam has already updated to 2600mm. Please check attachment snap E071-1.png | 08/12/2025 | 33.0000000000000 | [5 empty] | Mechanical Handling |  |  |  | Electrical | [10 empty] | Electrical | [5 empty] | 12/01/2026 | ID: 739
E072C | M17 |  | M17-E072C | Check the possibity to clear the area for material handling | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[af8c1a4376924721acf319fd197be1be][1]_[5].png","originalImageName":"E072C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[976ce955cb684f7192c81af78aa844e9][2]_[35].png","originalImageName":"E072C"} | Re-work | MATERIAL HANDLING | ABB/CIMC | 09/12/2025 | CIMC | Pending KBR | 2025/12/08, the purple cable tray already reduced to lower than coaming ,the green cable tray had been shifted to close the wall .which have no obstruction for lifting and drop down activities. 2025/12/10, as per close out meeting discussion , PB accept current cable tray and cable tray support arrangment ,but need to add some protection structure for this area. 2025/12/15, Protection structure for this area has already added in 3D model. | 14/12/2025 | 3.00000000000000 | [5 empty] | Mechanical Handling |  |  |  | Electrical | [10 empty] | Electrical | [5 empty] | 19/12/2025 | ID: 537
E073C | M17 |  | M17-E073C | Cable tray to be rerouted or clear for material handling | Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6c973777a9154b81ad353dc8782bccd4][1]_[5].png","originalImageName":"E073C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c5993be5843f4e4f8c834b230692f304][2]_[13].png","originalImageName":"E073C-20251208"} | YES | MATERIAL HANDLING | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/08, this cable tray already raise to above monorail to avoid obstruction monorail operation space. 2025/12/10, as per close out meeting discussion , this punch can be transfer to PB close. | 07/12/2025 | 31.0000000000000 | [5 empty] | Mechanical Handling |  |  |  | Electrical | [5 empty] | 09/01/26-UR7U-Noted. Cable tray moved. | Welton |  | 08/01/2026 | 10Dec25_B0RG_Ok | Electrical |  | 08/01/2026 | -1.00000000000000 |  |  | 09/01/2026 | ID: 398
E074C | M13R |  | M13R-E074C | Provide Table or additional LV handling trolley for placing faulty components for Level-2 | Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[88945db4abdf4c298b0d619c0f020dd2][1]_[5].png","originalImageName":"E074C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2a24b2e0963b4420ae29023a1350db74][2]_[16].png","originalImageName":"E074C-20251207"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/07, the required table had been added ,the dimension of table plate is 650mm in width and 1300mm in length. the height of table is 1.2m 2025/12/08, as per close out meeting discussion , need Mr Tuilo to check and close | 06/12/2025 | 10.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Structure | [5 empty] | 18/12/2025 | ID: 537
E075C | M17 |  | M17-E075C | Provide Table or additional LV handling trolley for placing faulty components for Level-2 | Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[757d5c0f35094281bda852b4547e226f][1]_[5].png","originalImageName":"E075C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[477037f64bb84b6ab3af873fe4ee1a62][2]_[14].png","originalImageName":"E075C-20251207"} | YES | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/07, the required table had been added ,the dimension of table plate is 650mm in width and 1500mm in length. the height of table is 1.2m 2025/12/08, as per close out meeting discussion , need Mr Tuilo to check and close | 06/12/2025 | 10.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Structure | [5 empty] | 18/12/2025 | ID: 537
E076C | M13R |  | M13R-E076C | SEA/KBR to check Provision to place the belt on the battery cell to lift to be clarified and Belt to be supplied along with Battery. | Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[def484da9deb466e816293f03db8647c][1]_[6].png","originalImageName":"E076C-M17"} |  |  | NO | MATERIAL HANDLING | Seatrium | 30/12/2025 | Seatrium | Pending Seatrium | 2025/12/17, please seatrium to coodinate with vendor to solve issue. | 16/12/2025 | -1.00000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [10 empty] | Mechanical Handling | [5 empty] | 17/12/2025 | ID: 539
E077C | M17 |  | M17-E077C | Coaming to be modified as per the markup | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6fb3ef5b5e7348c592119123def095c7][1]_[6].png","originalImageName":"E077C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[ad320ebb0b794a5c84d0401dab356d69][2]_[22].png","originalImageName":"E077C-20251209"} | Re-work | STRUCTURAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/1205,the coaming already updated as per markup snapshot. 2025/12/08, as per close out meeting discussion , the column position plate shall be removed. 2025/12/09, the column plate had been removed. 2025/12/12, as per close out meeting , this punch can be transfer to PB close | 04/12/2025 | 34.0000000000000 | [5 empty] | Structure |  |  |  | Structure | [5 empty] | Noted | Maxwell |  | 08/01/2026 |  | Structure | [5 empty] | 09/01/2026 | ID: 476
E078C | M17 |  | M17-E078C | Instrument air tubing specification T60 A to be verified | Luis | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[5faf02706faf415294e40412671b096a][1]_[5].png","originalImageName":"E078C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[cc94a51f5816440c98d6c35d12c8ebe0][1]_[7].png","originalImageName":"E078C"} | NO | PIPING | ABB/CIMC | 04/12/2025 | CIMC | Pending Seatrium | 2025/12/05: This tubing is for air horn of IG541 system, and the T60A is confirmed according to the P&ID I-DE-3010.2S-5425-944-YCT-002_PIPING AND INSTRUMENT DIAGRAM IG-541 DISTRIBUTION SYSTEM (CN-5425501A/B). 2025/12/10, as per close out meeting discussion , T60A is applicable for IG541 DO system ,other instrument air will follow instrument discipline requirement .This punch can be transfer to PB close. KBR to add DO service of T60A for IG541 system in Topside piping spec as agreed by PB | 04/12/2025 | 39.0000000000000 | T60A DO Service has been included in the Piping Class T60A in PMS Re.C. See attachment. | 12/01/2026 | Ma YuanYuan |  |  | Piping |  |  |  | Piping | [10 empty] | Piping | [5 empty] | 13/01/2026 | ID: 595
E079C | M17 |  | M17-E079C | Piping spool block the material handling Monorail | Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6f070a2428a34eac86dbe0aaa0328089][1]_[5].png","originalImageName":"E079C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[427bbeb0f14d4680aad558051e2ea902][2]_[32].png","originalImageName":"E079C-20260109"} | Re-work | MATERIAL HANDLING | Seatrium | 30/12/2025 | Seatrium | Pending KBR | 2025/12/17, please seatrium to coodinate with CIMC hull to solve issue. 2026/01/09, as per discussion, CIMC removed one gutter flange and raise piping elevation and chagne routing to avoid obstruction for monorial ,refer to snapshot. | 16/12/2025 | 26.0000000000000 | [5 empty] | Piping |  |  |  | Piping |  | Eric | 13/1/26: ABB has re-routed the gutter drain line to clear the filter maintenance area. KBR to acknowledge the new routing. | 13/01/2026 | -1.37500000000000 | [5 empty] | Piping | [5 empty] | 13/01/2026 | ID: 539
E080C | M17 |  | M17-E080C | ESP-54230144 Vaccum Breaker with Piping to be moved outside the Platform | Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b71997b29df84092bff430f303da7fe4][1]_[6].png","originalImageName":"E080C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[8d9b9089adce4fd0bed2da311500fa48][2]_[12].png","originalImageName":"E080C-20251206"} | YES | SAFETY | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/06, The vacuum breaker had been moved to outside of platform 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 05/12/2025 | 11.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E081C | M17 |  | M17-E081C | Vaccum Breaker to be separated from Fire Hydrant Location and to make elbow Branch for safe operation of personel | Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[66443cac04ab4bdb93f884e32ab95a64][1]_[6].png","originalImageName":"E081C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b068eb9bc2b34c8aafe8aa4cf642f3b6][1]_[9].png","originalImageName":"E081"} | YES | SAFETY | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: Vaccum breaker has been rearranged. 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | 04/12/2025 | 12.0000000000000 | [5 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 18/12/2025 | ID: 537
E082C | M17 |  | M17-E082C | Support for fire hydrant piping to be align with Topside Typical details | Tuilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[046fcc621f774c96a03bc8c9514b79b9][1]_[3].png","originalImageName":"E082C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[069e2e17362a4a449cd87b25961560e7][2]_[34].png","originalImageName":"E082C-20260114"} | Re-work | PIPING | ABB/CIMC | 04/12/2025 | CIMC | Pending KBR | 2025/12/05: We suggest to adopt attached support for fire hydrant which used in P80/P83 FPSO project. 2025/12/10, PB request to follow KBR typical details for hydrant piping support , KBR /Seatrium to provide the database . 2026/01/14, the fire hydrant support had been added based on KBR typical details . | 04/12/2025 | 39.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [10 empty] | Piping | [5 empty] | 14/01/2026 | ID: 539
E083C | M17 |  | M17-E083C | Chilled Water Valve and drain Line located at Level-4 to be Moved to Level-1 at a Height of 2.3 m from Level-1 Platform. Access for Valve is acceptable by PB as it is category -3.Drain line shall be located at above the valve. | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[37b90d5a14f44d898d416654f92c9a7f][1]_[1].png","originalImageName":"E083C-M17"} | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot2][32]_[24d01977f5794537b3c75c88fec62118][2]_[17].png","originalImageName":"E083C-20251210"} | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6162be2abe81411f83881f751d1d9947][2]_[25].png","originalImageName":"E083C-20251211"} | NO | PIPING | ABB/CIMC | 04/12/2025 | CIMC | Pending Petrobras | 2025/12/05: Valves and drain line has been rearranged on the 1st floor at a height no more than 1.8m so it is also easy for operation and maintenance. 2025/12/11, the drain line had been updated with shorten vertical pipe as per customer comments . 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 04/12/2025 | 12.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [10 empty] | Piping | [5 empty] | 17/12/2025 | ID: 537
E084C | M17 |  | M17-E084C | Strainer Maintenance volume to be Modelled | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[78cc05cdd568481f97c0cadd244ebd11][1]_[2].png","originalImageName":"E084C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6194f4a5d6b64a4caa5611e06e5e5451][2]_[11].png","originalImageName":"E084"} | NO | PIPING | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/09： Strainer Maintenance volume has been added. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Model has been updated with the retrieval volume. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E085C | M17 |  | M17-E085C | ABB to provide the revised P&ID for the change in Pipe Size | Eric | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[70c52db7ddef4569bc1ace64a4e95c08][1]_[2].png","originalImageName":"E085C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[77394010f146448ab056abb74ea17ac5][2]_[13].png","originalImageName":"E085C-20251206"} | NO | PIPING | ABB/CIMC | 18/12/2025 | CIMC | Close | 2025/12/05: please find the latest P&ID_REV.C 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close. The Rev C chilller water PID submitted to customer review ,include this changes . | 04/12/2025 | 29.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Diameter in the model is according to the latest P&ID. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 23.0000000000000 |  |  | 04/01/2026 | ID: 539
E086C | M17 |  | M17-E086C | "Pressure gauge tapping shall be changed to vertical Pipe | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d9cc53ccf2cb432f9960639cd041285a][1]_[4].png","originalImageName":"E086C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[88606f590f8d48119068a87055da3b9b][2]_[13].png","originalImageName":"E086"} | NO | PIPING | ABB/CIMC | 08/12/2025 | CIMC | Close | 2025/12/09： Pressure gauge tapping has been changed to vertical Pipe. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Pressure gauge tapping has been changed to vertical Pipe accordingly. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E087C | M17 |  | M17-E087C | 1 vent Valve to be added for each sub header and 6 nos of vent Valve to be added in total at Level-4 and level -5 and P&ID to be updated | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c2049a05c6bd4f309af5cd0b17bfebe7][1]_[2].png","originalImageName":"E087C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[33a0d9d285544c5cae082e7d8f03a840][2]_[11].png","originalImageName":"E087C-20251209"} | NO | PIPING | ABB/CIMC | 18/12/2025 | CIMC | Close | 2025/12/09,the required vent valve had been added 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 25.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Vent valves have been included at all subheaders fwd portion. Model already updated. Punch considered cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 23.0000000000000 |  |  | 04/01/2026 | ID: 539
E088C | M17 |  | M17-E088C | Base Plate clash with flange to be rectified | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a760735790ab4062977a8ee3fc30b72f][1]_[2].png","originalImageName":"E088C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[ee3e58340d524be98ab861092a1d8b17][1]_[4].png","originalImageName":"E088"} | YES | PIPING | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: Base plate clash with flange has been eliminated. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 04/12/2025 | 12.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Support clearance with the thermal insulation surface secured. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 18/12/2025 | ID: 537
E089C | M17 |  | M17-E089C | Insulation below deck to be removed for open drain | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[789535bd40e445e4a11f44083875e97b][1]_[2].png","originalImageName":"E089C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[e3c13d74892e416fa6c62e6e74406fd9][1]_[9].png","originalImageName":"E089C-20251206"} | NO | PIPING | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/06,the insulation below the deck had been removed ,which already confirmed by vendor. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 05/12/2025 | 11.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025(Alvim) - Thermal insulation for the small stretchs of pipe under the deck have been removed as per the current model. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E090C | M17 |  | M17-E090C | Operation of the valve clash with Structure and to be rectiifed | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[cb59b7dd07c04711b6bd16d3180a246b][2]_[12].png","originalImageName":"~"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[02af37992f5c40899d5f96b087cf1e83][2]_[16].png","originalImageName":"E090C-20251209"} | NO | PIPING | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/09,the valve had been shifted to horizontial pipe ,refer to snapshot 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) -Valve operation volume has been updated. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E091C | M17 |  | M17-E091C | PG is missing & to be Modelled as per the GAD | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[abe2dd0d3aad4074b1e074a460633a83][1]_[2].png","originalImageName":"E091C-M17"} |  |  | NO | PIPING | ABB | 11/12/2025 | ABB | Pending ABB/CIMC | lack of GA for Automatic Air Trap | [7 empty] | Piping |  |  |  | Piping | [10 empty] | Piping | [5 empty] | 22/12/2025 | ID: 842
E092C | M17 |  | M17-E092C | Hose Reel Station to be deleted as per confirmation with PB | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[182458820393451f8fa134f517483710][1]_[2].png","originalImageName":"E092C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1f3dba9ccb2446d98d22a6100c807d21][1]_[4].png","originalImageName":"E092"} | NO | PIPING | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: Hose Reel Station has been deleted. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 04/12/2025 | 12.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Hose reel station is removed. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E093C | M17 |  | M17-E093C | Quick release coupling to be provided at the end of the Pipe | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[5259a2a261b24b7a8b697932dc060761][1]_[4].png","originalImageName":"E093C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[84ac4692d3ad49a7a4bdb5749d5fddd8][2]_[12].png","originalImageName":"E093"} | NO | PIPING | ABB/CIMC | 13/12/2025 | CIMC | Close | 2025/12/09: Quick release coupling has been added at the end of the pipe. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Quick coupling has been updated accordingly. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E094C | M17 |  | M17-E094C | Instrument air for material handling tools to be Modelled as per P&id and Isolation Valve at each Line end to be evaluated. | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4d18f50775864dc1b6ceb9dd06187021][1]_[2].png","originalImageName":"E094C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c31ec1062df8469e8ba07a30c531bd6a][2]_[17].png","originalImageName":"E094"} | YES | PIPING | ABB/CIMC | 30/12/2025 | CIMC | Pending KBR | 2025/12/22： Instrument air for material handling tools has been modelled as per P&id and Isolation valve at each line has been added also. | [7 empty] | Piping |  |  |  | Piping | [10 empty] | Piping | [5 empty] | 22/12/2025 | ID: 842
E095C | M17 |  | M17-E095C | General Comment : Support for all the manifold is missing and to be Modelled | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[62cca940f99c417b875c4df99a1ee874][1]_[2].png","originalImageName":"E095-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[301c83ac27f44bf191959535d6377558][2]_[13].png","originalImageName":"E095C-20251209"} | YES | PIPING | ABB/CIMC | 13/12/2025 | CIMC | Close | 2025/12/809, the support for all manifold had been added. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Supports have been added for all air manifolds. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 18/12/2025 | ID: 537
E096C | M17 |  | M17-E096C | Support or tubing tray requirement for the Single tubing to be aligned with instrumentation | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[73e28aefb16640a0bb4129d326214d5b][1]_[2].png","originalImageName":"E096C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[26647f7498934956b953b67e5daa80ea][2]_[15].png","originalImageName":"096"} | YES | INSTRUMENTATION | ABB/CIMC | 18/12/2025 | CIMC | Close | 2025/12/17, the model has been updated | 16/12/2025 | 23.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | Instrumentation |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 15.3750000000000 | [U5D6 - 09/JAN/2026] No comments. | U5D6 |  | 08/01/2026 |  | Instrumentation |  | 08/01/2026 | 0 |  |  | 09/01/2026 | ID: 399
E097C | M17 |  | M17-E097C | Sleeve for instrument pipe penetration is missing and to be Modelled | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[97725e2117b34c9e898640d8dd8eb64c][1]_[2].png","originalImageName":"E097C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9fb194ed3fd04d67ba8d795a2b3dea8a][1]_[9].png","originalImageName":"E097C-20251206"} | YES | PIPING | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/06, the missing penetration had been added 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 05/12/2025 | 11.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Penetration has been included in the model. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 18/12/2025 | ID: 537
E098C | M17 |  | M17-E098C | Reduce the Height of Vaccum Breaker pipe to 1.2m from 1.6m | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0b631c4880514f378752c1b70a1d9f3d][1]_[2].png","originalImageName":"E098C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[67eb4fab9a8e41b4ba363a59e8ef4c22][1]_[6].png","originalImageName":"E098"} | NO | PIPING | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05: The height of Vaccum breaker has been changed to 1.2m 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 04/12/2025 | 9.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Vacuum breaker valve elevation has been reduced. Model updated accordingly and punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 3.00000000000000 |  |  | 15/12/2025 | ID: 19
E099C | M13R |  | M13R-E099C | Insulation Gasket to be Modelled | Eric | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e5fefca5c9524e5cbb344d4b0217b591][1]_[6].png","originalImageName":"E099C-M17"} |  |  | NO | PIPING | ABB | 11/12/2025 | ABB | Pending ABB/CIMC | 2025/12/08: The medium is condensate water for AHU, so there is no need to use the insulation gasket according to the I-ET-3010.2S-1400-200-S2N-001_PIPING SPECIFICATION FOR TOPSIDES. And gasket has been added in S3D, attached please find the snapshot for gasket properties. 2025/12/10, as per close out meeting discussion , the insulation gasket shall be added . | 07/12/2025 | 17.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [10 empty] | Piping | [5 empty] | 26/12/2025 | ID: 539
E100C | M13R |  | M13R-E100C | Pipe Support is not aligned with Chilled water Piping | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[838c4d4177ce4e619b76166572f428fa][1]_[9].png","originalImageName":"~"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[f800da04d152441c8db8b2330253c3fe][2]_[11].png","originalImageName":"E100"} | NO | PIPING | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/08: Pipe supports have been updated. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 07/12/2025 | 9.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Supports updated. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E101C | M13R |  | M13R-E101C | Isolation Valve and Drain Line to be shifted to Level-1 | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c079d7bedd18487881ce91377a5ee93d][1]_[2].png","originalImageName":"E101C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[dff671d17d7549f183c12f91797da407][2]_[19].png","originalImageName":"E101C-20251211"} | NO | PIPING | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/05: Valves and drain line has been rearranged on the 1st floor at a height no more than 1.8m so it is also easy for operation and maintenance. 2025/12/11, the drain line had been updated with shorten vertical pipe as per customer comments . 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 04/12/2025 | 38.0000000000000 |  | 12/01/2026 |  |  |  | Piping |  |  |  | Piping |  |  |  | 02/01/2026 | 11.2500000000000 | Mover to 1st LeveL | Julius Orzales |  | 13/01/2026 |  | Piping |  | 13/01/2026 | -1.62500000000000 |  |  | 13/01/2026 | ID: 484
E102C | M13R |  | M13R-E102C | Strainer Maintenance volume to be Modelled | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b4faad281b0a425895d3f2510e2a9a68][1]_[2].png","originalImageName":"E102C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bed99b29348942179dd5e1eb148fb1dc][2]_[10].png","originalImageName":"E103"} | NO | PIPING | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/09： Strainer Maintenance volume has been added. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Filter internal element retrieval volume has been updated in the model. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E103C | M13R |  | M13R-E103C | Pressure gauge tapping shall be changed to vertical Pipe PG-5252814 PG-5252815 PG-5252817 PG-5252816 | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[334bc46f50b14b3db831f7129f2ebb68][1]_[2].png","originalImageName":"E103C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[5cba3f674e4b42f29c5194724a8000b1][2]_[12].png","originalImageName":"E103C-20251209"} | NO | PIPING | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/09: these PG had been shifted to vertical pipe. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - PGs have been shifted to vertical pipe in the model. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E104C | M13R |  | M13R-E104C | 1 vent Valve to be added for each sub header and 2nos of vent Valve to be added in total | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[2693e7e3c28a4c2a9d3e785bda45573f][1]_[2].jpg","originalImageName":"E104C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[61a1de6cc0e14bf6ae02a8400a1513cd][2]_[11].png","originalImageName":"E104C-20251209"} | NO | PIPING | ABB/CIMC | 18/12/2025 | CIMC | Close | 2025/12/09: the required vent valve had been added 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 25.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Vent valves have been added at the FWD end of each subheader. Model updated accordingly. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 23.0000000000000 |  |  | 04/01/2026 | ID: 539
E105C | M13R |  | M13R-E105C | PG is missing & to be Modelled as per the GAD | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0ae731a709674e96b6538111b66aa3af][1]_[2].png","originalImageName":"E105C-M13R"} |  |  | NO | PIPING | ABB | 18/12/2025 | ABB | Pending ABB/CIMC | lack of GA for Automatic Air Trap | [7 empty] | Piping |  |  |  | Piping | [10 empty] | Piping | [5 empty] | 22/12/2025 | ID: 842
E106C | M13R |  | M13R-E106C | Hose Reel Station to be deleted as per confirmation with PB | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1584de6e2e014c2688520c0d2101a14a][1]_[2].png","originalImageName":"E106C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[ca77d6bb1ac14f0698a1b556b2d28fff][1]_[4].png","originalImageName":"E106"} | NO | PIPING | ABB/CIMC | 04/12/2025 | CIMC | Close | 2025/12/05: Hose Reel Station has been deleted. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 04/12/2025 | 12.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Hose Reel Station has been removed from model. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E107C | M13R |  | M13R-E107C | Quick release coupling to be provided at the end of the Pipe | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[969a7bcf6b3f41f884b571474362bd6c][1]_[2].png","originalImageName":"E107C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[53af8cf1fc4944a6893b8a7333633bbe][2]_[22].png","originalImageName":"E107"} | NO | PIPING | ABB/CIMC | 13/12/2025 | CIMC | Close | 2025/12/09: Quick release coupling has been added at the end of the pipe. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Quick release coupling has been added at the end of the pipe. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 17/12/2025 | ID: 537
E108C | M13R |  | M13R-E108C | Instrument air for material handling tools to be Modelled as per P&id and Isolation Valve at each Line end to be evaluated. | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6b777b8545b548d49fdf95e78ea238d5][1]_[2].png","originalImageName":"E108C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[cf25e9ca23084d14ac4d8780e3db13f0][2]_[21].png","originalImageName":"E108"} | YES | PIPING | ABB/CIMC | 30/12/2025 | CIMC | Pending KBR | 2025/12/22： Instrument air for material handling tools has been modelled as per P&id and Isolation valve has been added also. | [7 empty] | Piping |  |  |  | Piping | [10 empty] | Piping | [5 empty] | 22/12/2025 | ID: 842
E109C | M13R |  | M13R-E109C | General Comment : Support for all the manifold is missing and to be Modelled | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[9130174812b643a582791704ac3bf453][1]_[2].png","originalImageName":"E109C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[3de56222d73a4e258d5579f22177934a][2]_[11].png","originalImageName":"E109"} | YES | PIPING | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/09: Support for all the manifold has been added. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 11-12-2025 (Alvim) - Manifold supports have been added in the model. Punch cleared. | Alvim |  | 10/12/2025 |  | Piping |  | 10/12/2025 | 6.00000000000000 |  |  | 18/12/2025 | ID: 537
E110C | M13R |  | M13R-E110C | Isolation Valve at Level-1 shall be Moved close to Level-1 Safety Shower and For Level-2 safety shower, additional Isolation valve to be added. | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d84c416ae7234be09ff84a157e448dcd][1]_[2].png","originalImageName":"E110C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[3cf1ff564efa4e8bbd1bf3ca080b763c][2]_[10].png","originalImageName":"E110"} | NO | PIPING | ABB/CIMC | 18/12/2025 | CIMC | Close | 2025/12/09: Isolation Valve at Level-1 has been moved close to Level-1 Safety Shower and For Level-2 safety shower, additional Isolation valve has been added. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 22.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 12-12-2025 - Two valves have been shifted to close to the safety shower. Punch cleared. | Alvim |  | 11/12/2025 |  | Piping |  | 11/12/2025 | 19.0000000000000 |  |  | 01/01/2026 | ID: 539
E111C | M13R |  | M13R-E111C | Shift the Valve VALV-52528091 to the expansion tank Platform | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c7486d9ee66245829756d5fccf3cc7dc][1]_[2].png","originalImageName":"E111C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[d073f3244123466eb1043cce36044411][2]_[14].png","originalImageName":"E111"} | NO | PIPING | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/06,this valve had been move to expansion tank platform 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 05/12/2025 | 11.0000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 12-12-2025 - Valve has been shifted to the tank platform. Item cleared. | Alvim |  | 11/12/2025 |  | Piping |  | 11/12/2025 | 5.00000000000000 |  |  | 17/12/2025 | ID: 537
E112C | M13R |  | M13R-E112C | Fire Extinguisher and Damper Valve Panel shall be swaped to provide access for valve | Bruno/Danilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d82b925208a2445589536bc5f3d23538][1]_[2].png","originalImageName":"E112C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[600f40a2b54545f08f5f0b3367282481][2]_[14].png","originalImageName":"E112C-20251209"} | YES | PIPING | ABB/CIMC | 07/12/2025 | CIMC | Close | 2015/12/08 Fire Extinguisher and Damper Valve Panel has been swaped. 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 12-12-2025 - Damper Valve Panel has been swaped on the current model. Item cleared. | Alvim |  | 11/12/2025 |  | Piping |  | 11/12/2025 | 5.00000000000000 |  |  | 18/12/2025 | ID: 537
E113C | M17 |  | M17-E113C | General Comment:Nozzle Location shall be Moved outside of Equipment Panel including Future Space Panel | Danilo/Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a971d1095ea14bd187c7eb55b33e83a5][1]_[2].png","originalImageName":"E113C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[245ab58fafed47f794714c25b6296c90][2]_[25].png","originalImageName":"E113"} | YES | SAFETY | ABB/CIMC | 09/12/2025 | CIMC | Close | 2025/12/10： Nozzle Location has been moved outside of Equipment Panel including Future Space Panel. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 09/12/2025 | 16.0000000000000 | [5 empty] | Safety |  |  |  | Piping | [5 empty] | 26dec25: This punch can be closed. | Danilo |  | 25/12/2025 | Punch transferred to Safety | Safety | [5 empty] | 26/12/2025 | ID: 372
E114C | M13R |  | M13R-E114C | General Comment:Nozzle Location shall be Moved to Moved outside of Equipment Panel including Future Space Panel | Danilo/Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8ba0ebca55fa4ca39dd28a31faebad33][1]_[2].png","originalImageName":"E114C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[88dc319dc59b4c9380c31c9f19a495ea][2]_[19].png","originalImageName":"E114"} | YES | SAFETY | ABB/CIMC | 09/12/2025 | CIMC | Close | 2025/12/10： Nozzle Location has been moved outside of Equipment Panel including Future Space Panel. 2025/12/11, as per discussion and feedback by PB Danilo , this punch can be transfer to PB close. | 09/12/2025 | 16.0000000000000 | [5 empty] | Safety |  |  |  | Piping | [5 empty] | 26dec25: This punch can be closed. | Danilo |  | 25/12/2025 | Punch transferred to Safety | Safety | [5 empty] | 26/12/2025 | ID: 372
E115C | M13R |  | M13R-E115C | Nozzle Location Layoutto be updated as per 3D MODEL | Danilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b143b38bf31b4fe6ab0fa44686ab4f6b][1]_[2].png","originalImageName":"E115C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9c6a24291b6e4328bcf607f0f6c6f1d5][2]_[13].png","originalImageName":"E047C-20251210"} | NO | SAFETY | ABB | 18/12/2025 | ABB | Rejected | 2025/12/09, nozzle location layout had been updated as per 3D model | 09/12/2025 | 15.0000000000000 | 23 Dec 25: 1. It is noted that there is a duplication in the nozzle tag number for nozzles below raise floor and nozzle below the ceiling in the close-out snapshot provided by ABB. 2. ABB to clarify the tag number change in Rev D noted that Rev D has not been issued officially. 3. ABB to note that any change in nozzle tag number will have to be aligned with I-DE-3010.2S-5425-260-TY9-201 PIPING AND NOZZLE ARRANGEMENT DRAWING-IG-541 SYSTEM (CN-5425501A/B, CN-5425503A/B) issued by IG-541 Vendor. | 22/12/2025 | Indra/ Hong |  |  | Safety |  |  |  | Safety | [10 empty] | Safety | [5 empty] | 26/12/2025 | ID: 539
E116C | M13R |  | M13R-E116C | Small Coaming with 30mm to be provided for Safety Shower drain Box and Drain box to be Moved as per Snapshot | Danilo/Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[475fb81a6ed047e89379dcab9e41c703][1]_[2].png","originalImageName":"E116C_M13R"} | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot2][32]_[e9a318d2aee545b3a8b97ab08ae1ddc4][1]_[4].png","originalImageName":"E116C-M13R_1"} | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[fdb06238572e4845bf1710c606e5fad8][2]_[79].png","originalImageName":"M13R E116C new"} | Re-work | SAFETY | ABB/CIMC | 11/12/2025 | CIMC | Pending Petrobras | 2025/12/08, the required coaming had been added ,the drain box also shifted to required position. 2025/12/09,the small coaming had been added for safety shower for level 1 & 2 2025/12/11, as per discussion and feedback by PB Danilo , Evaluate swaping the position of the Hydrant and the Safety Shower, which will: 1) Allow more space for hydrant operation; 2) Clear space in front of the stair instead of having the small coaming right in front of the stair landing; 3) Avoid the safety shower being in the way of the hose and hydrant operation, during emergency. 2025/12/17, the hydrant and safety shower on the 2 level has been updated as per the requirement from PB. the safety show and coaming on the 1 level has been updated. 2025/12/25 The 3D model has been update as per comment. | 07/12/2025 | 34.0000000000000 | 23 Dec 2025: Both coaming and drain pit provided for Z-5434411/2. 30 Dec 2025: ABB has adjusted coaming to fit the safety showers. | 29/12/2025 | Indra/ Hong |  |  | Safety |  | 22/12/2025 | 0.625000000000000 | Safety |  | Gan Wei Chang |  | 23/12/2025 | 18.3750000000000 | 23dec25: In the 3D Model dated from 23/12/25 the coaming size needs to be adjusted. See the snapshot. Once this is corrected, this punch can be closed, since the position of the safety shower is approved. | Danilo |  | 22/12/2025 |  | Safety | [5 empty] | 12/01/2026 | ID: 96
E117C | M17 |  | M17-E117C | Small Coaming with 30mm to be provided for Safety Shower drain Box | Danilo/Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[36ad155fbac9441aac73fb3b78b9181f][1]_[2].png","originalImageName":"E117C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2c0150cdbb83459a94f2832229ce67c6][1]_[9].png","originalImageName":"E117C-20251209"} | Re-work | SAFETY | ABB/CIMC | 18/12/2025 | CIMC | Close | 2025/12/09, the small coaming with 30mm had been added for safety shower and drain box 2025/12/11, as per discussion and feedback by PB Danilo, this punch can be transfer to PB close. | 08/12/2025 | 14.0000000000000 | KBR has verified on the 3D model dated on 22 Dec 25 that coaming and drain pit has been provided for safety shower Z-5434414. | 21/12/2025 | Indra/ Hong |  |  | Safety |  | 21/12/2025 | 1.62500000000000 | Safety |  | Gan Wei Chang |  | 23/12/2025 | -0.625000000000000 | 23dec25: This punch can be closed. | Danilo |  | 22/12/2025 |  | Safety | [5 empty] | 23/12/2025 | ID: 372
E118C | M17 |  | M17-E118C | VALV-54230199 Valve Height to be Elevated to 2.2m | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[de696efe05054d85b750b8802fcca668][1]_[2].png","originalImageName":"E118C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c698a37525d0481887ce130531bb106d][2]_[11].png","originalImageName":"E118C-20251206"} | NO | SAFETY | ABB/CIMC | 05/12/2025 | CIMC | Close | 2025/12/06,this valve had been elevated to 2.2m 2025/12/08, as per close out meeting discussion , customer agreed to close this punch. | [7 empty] | Safety |  |  |  | Safety | [8 empty] | 07/12/2025 | 08dec25: This punch can be closed. | Safety | [5 empty] | 15/12/2025 | ID: 19
E119C | M17 |  | M17-E119C | Lighting JB CXE-L-M17-225 shall be moved away from HVAC Grill to avoid water fall into JB | Tammer | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7d5e922bffdb4e95aba5edda8860a87c][1]_[1].png","originalImageName":"E119C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a65ddbcce2554e9c97f72600b61e6849][2]_[30].png","originalImageName":"119"} | NO | ELECTRICAL | ABB/CIMC | 07/12/2025 | CIMC | Close | 2025/12/08, Lighting JB CXE-L-M17-225 had been moved away from HVAC Grill to avoid water fall into JB | 07/12/2025 | 32.0000000000000 | 2 Jan: JB relocated away from HVAC grill, no further comment | 01/01/2026 |  | 12 Dec: Transferred to ELECTRICAL |  | Electrical |  |  |  | Electrical |  | Shichen Li | 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | 2.40694444444671 | [U5D6 - 09/JAN/2026] As aligned with electrical team, closed. | U5D6 |  | 08/01/2026 |  | Instrumentation |  | 08/01/2026 | 0 |  |  | 09/01/2026 | ID: 399
E120C | M17 |  | M17-E120C | Tubing Cable Tray to be clear from return air duct actuator damper DG-5250932 Manintenance volume | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[9a09578235eb4fa98ebc6bac96420ecc][1]_[1].png","originalImageName":"E120C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[dbd75d2951594e358a3e5c70de4eb350][2]_[34].png","originalImageName":"120"} | YES | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Close | 2025/12/09, the tubing cable tray had been shifted to avoid clash with maintenance space 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 08/12/2025 | 31.0000000000000 | [5 empty] | Instrument |  |  |  | Instrumentation | [5 empty] | [U5D6 - 09/JAN/2026] As per closeout snapshot, the trays have been shifted. | U5D6 |  | 08/01/2026 |  | Instrumentation | [5 empty] | 09/01/2026 | ID: 399
E121C | M17 |  | M17-E121C | Tubing Cable Tray to be clear from supply air duct DG-5250931 Manintenance volume | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[460e6c6ab19d4dfa8f0717146fc3389b][1]_[1].png","originalImageName":"E121C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[625c97236e154ed5bdfa401edbb9da2f][2]_[38].png","originalImageName":"121"} | YES | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Close | 2025/12/09, the tubing cable tray had been shifted to avoid clash with maintenance space 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 08/12/2025 | 31.0000000000000 | [5 empty] | Instrument |  |  |  | Instrumentation | [5 empty] | [U5D6 - 09/JAN/2026] As per closeout snapshot, tubing tray has been moved to solve the clash. | U5D6 |  | 08/01/2026 |  | Instrumentation |  | 08/01/2026 | 0 |  |  | 09/01/2026 | ID: 399
E122C | M17 |  | M17-E122C | Instrument air Tubing Clashing with Actuator maintenance volume | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1e4dd7c27768434bb24ac7967e8465de][1]_[1].png","originalImageName":"E122C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[3215491535e046689d58a7831409b78c][2]_[12].png","originalImageName":"E122C-20251209"} | YES | PIPING | ABB/CIMC | 09/12/2025 | CIMC | Close | 2025/12/09, this tubing had been shifted to right side to avoid clash with maintenance space 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 12-12-2025 - Tubing has been shifted away from the obstruction volume. Punch cleared. | Alvim |  | 11/12/2025 |  | Piping |  | 11/12/2025 | 5.00000000000000 |  |  | 18/12/2025 | ID: 537
E123C | M17 | All level | M17-E123C | General Comment : PDIT tag no shall be updated in D&ID (I-DE-3010.2S-5250-326-AIW-002)and instrument Layout (I-DE-3010.2S-5250-326-AIW-020) | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[60636938b52e47339000288f32a7f229][1]_[1].png","originalImageName":"E123C-M17"} |  |  | NO | INSTRUMENTATION | ABB | 24/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | Instrument |  |  |  | Instrumentation | [10 empty] | Instrumentation | [5 empty] | 25/12/2025 | ID: 539
E124C | M17 |  | M17-E124C | Transformer room 1 PDIT to be removed as per D&ID | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[64bf089dbe1548d69918b98b4a5aa57f][1]_[1].png","originalImageName":"E124C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[453733a711384f3caabe0c6ac000c284][1]_[7].png","originalImageName":"E124C-20251209"} | Re-work | INSTRUMENTATION | ABB/CIMC | 08/12/2025 | CIMC | Close | 2025/12/09, this PDIT had been removed from 3D as per DID 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 08/12/2025 | 31.0000000000000 | [5 empty] | Instrument |  |  |  | Instrumentation | [5 empty] | [U5D6 - 09/JAN/2026] PDIT has been removed as per comment. | U5D6 |  | 08/01/2026 |  | Instrumentation |  | 08/01/2026 | 0 |  |  | 09/01/2026 | ID: 399
E125C | M17 |  | M17-E125C | Cable tray to be clear or cut before the Actuator from Maintenance Volume | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7a3d95a98da34095a083f5e4637842a6][1]_[1].png","originalImageName":"E125C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[4b8e04f5414e460d90ace3f684cacbc3][2]_[30].png","originalImageName":"E125C"} | NO | INSTRUMENTATION | ABB/CIMC | 08/12/2025 | CIMC | Close | 12/09/2025:3D model updated 2025/12/12, as per close out meeting ,this punch remain open ,this cable trayo shift to another side. 12/19/2025:This cable tray already been shifted to another side. | 18/12/2025 | 21.0000000000000 | KBR has no comments. | 23/12/2025 | Roberto |  |  | Instrument |  |  |  | Instrumentation |  | Guanyu Zhu | 26/12/2025: no comment | 26/12/2025 | 13.4041666666672 | [U5D6 - 09/JAN/2026] Cable tray has been shifted. | U5D6 |  | 08/01/2026 |  | Instrumentation |  | 08/01/2026 | 0 |  |  | 09/01/2026 | ID: 399
E126C | M17 |  | M17-E126C | General comments: Tubing clashes with cable tray to be cleared | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[54080e7e6b5b452ab1ba0928b8b87e42][1]_[1].png","originalImageName":"E126-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a7c71e1b2be04763b35808f207609b67][1]_[9].png","originalImageName":"E126C-20251209"} | YES | PIPING | ABB/CIMC | 08/12/2025 | CIMC | Close | 2025/12/09,these tubing had been shifted to avoid clash with cable tray 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Piping |  |  |  | Piping | [5 empty] | 12-12-2025 - Tubing has been shifted to avoid clash with cable tray. Punch cleared. | Alvim |  | 11/12/2025 |  | Piping |  | 11/12/2025 | 5.00000000000000 |  |  | 18/12/2025 | ID: 537
E127C | M17 |  | M17-E127C | Resolve clashes between maintenance Volume for the Gas Damper (DG-5250924) and LV Panel PN-5143004 | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e38fcef2fb4d4d59b56fd1a58dc14edd][1]_[1].png","originalImageName":"E127C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1ac9d95226414d91bf25851b68a70df9][1]_[8].png","originalImageName":"E127C-20251210"} | NO | PIPING | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/10, the maintenance volume had been adjusted to avoid clash with panel . 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 09/12/2025 | 7.00000000000000 | [5 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 17/12/2025 | ID: 537
E128C | M17 |  | M17-E128C | Delete the Support in front of Gas Damper (DG-5250924) | Chen | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c153b56b221e4848b7dec16623db7099][1]_[3].png","originalImageName":"E128C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[557518aaa80342308e545bcf01dd2e73][1]_[9].png","originalImageName":"E128C-20251209"} | NO | INSTRUMENTATION | ABB/CIMC | 08/12/2025 | CIMC | Pending Petrobras | 2025/12/09, this support had been deleted. | 08/12/2025 | 23.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | HVAC |  | Mun | Noted, closed. | 02/01/2026 | -1.41666666666424 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E129C | M17 |  | M17-E129C | Resolve clashes between maintenance Volume for the Gas Damper (DG-5250951) and cable tray | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4416e232b79745e59bd7ccc4444fc4c7][1]_[2].png","originalImageName":"E129C-M17"} |  |  | Re-work | HVAC | ABB | 30/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 29/12/2025 | ID: 539
E130C | M17 |  | M17-E130C | Damper comtrol Panel to be modelled along with cable tray and Tubing | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6521a25812894706850b55a1a41c5c37][1]_[2].png","originalImageName":"E130C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2574d1e016394edf81c69741f99d2662][1]_[6].png","originalImageName":"E130C-20251210"} | YES | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10,the tubing had been adjusted to align with damper control panel and tray . 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 09/12/2025 | 7.00000000000000 | [5 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 18/12/2025 | ID: 537
E131C | M17 |  | M17-E131C | Ball ValV-HV-5250681 to be shifted inside the Air lock Room | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[cf58aaf278f842eba61c0969e961a337][1]_[2].png","originalImageName":"E131C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[cb1da2c0186f4447bf321dc1ee8cc3a4][2]_[26].png","originalImageName":"E131"} | YES | PIPING | ABB/CIMC | 16/12/2025 | CIMC | Pending Petrobras | 2025/12/17： Ball ValV-HV-5250681 has been shifted inside the Air lock Room. |  |  | 18Dec25: Noted on shifting the ball valve inside. Provide a snap of the new location (with height dimension). | 18/12/2025 | Allan |  |  | HVAC |  |  |  | HVAC |  | Mun | The ball valve tag HV-5250681B was relocated to the AFT air lock of Transformer Room as per verification in 3d model, the valve height is approx. 1.2m from the floor. This comment can be closed. | 02/01/2026 | -1.37500000000000 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E132C | M17 |  | M17-E132C | General Comment Maintenance volume for all the Damper actuator shall be updated as per the drawing | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7919848d28d8442082a9e3df2ec97330][1]_[2].png","originalImageName":"E132C-M17"} |  |  | Re-work | HVAC | ABB | 30/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 29/12/2025 | ID: 539
E133C | M17 | All level | M17-E133C | Cable Tray Support or Cable Tray routing to be modified as it is clash with Maintenance Volume of Gas Damper DG-5250982 ,DF-5250662,DG-5250922,DG-5250942,DF-5250641 | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[552a109b33f744b9bd6163e40dd19d23][1]_[2].png","originalImageName":"E133C-M17"} |  |  | Re-work | INSTRUMENTATION | ABB | 18/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | Instrument |  |  |  | Instrumentation | [10 empty] | Instrumentation | [5 empty] | 07/01/2026 | ID: 539
E134C | M17 |  | M17-E134C | Gas Damper actuator DG-5250929 quantity to be updated as per Lattest vendor drawing | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[43b4f91d96614ff19daedbe5c348f0f8][1]_[2].png","originalImageName":"E134C-M17"} |  |  | YES | HVAC | ABB | 30/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 18/12/2025 | ID: 537
E135C | M17 |  | M17-E135C | Hand Valve HV-5250691B to be relocated near to the door for accesibilty | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0e911f70bdb74115b0a032e7d624e70b][1]_[2].png","originalImageName":"E135C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[40ff7d4682ac4e1e9f4168bd47a305c6][2]_[20].png","originalImageName":"E135"} | YES | PIPING | ABB/CIMC | 16/12/2025 | CIMC | Pending Petrobras | 2025/12/17： Hand Valve HV-5250691B has been relocated near to the door. |  |  | 18Dec25: Noted. Ensure height is as per Ergonomics requirement. | 18/12/2025 | Allan |  |  | HVAC |  |  |  | HVAC |  | Mun | Noted. ABB to ensure height is as per Ergonomics requirement. | 02/01/2026 | -1.37500000000000 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E136C | M17 |  | M17-E136C | Cable Tray support to be shifted for providing proper access for operation of Temperature sensor TE-5250621,TE-5250623&TE-5250625 | Bruno/Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e3912aedba0f403a94db6c010b95a15b][1]_[2].png","originalImageName":"E136C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[58dd507375a34c4cbdc4c67892685873][2]_[20].png","originalImageName":"E136C-20251220"} | Re-work | INSTRUMENTATION | ABB/CIMC | 18/12/2025 | CIMC | Pending Petrobras | 2025/12/20，this cable tray and support had been raised up to avoid clash with operation space | 19/12/2025 | 12.0000000000000 | KBR has no comments | 23/12/2025 | Roberto |  |  | Instrument |  |  |  | HVAC |  | Mun | Noted, closed. | 02/01/2026 | -1.37500000000000 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E137C | M17 |  | M17-E137C | Add duct inspection hatch for duct cleaning for both Battery room 1 and Battery room 2 | Tamer | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0dca8fee36b64ee7ac9c8408afe078dc][1]_[2].png","originalImageName":"E137C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[61d156923a3c4efebca1ba02e117ed92][2]_[14].png","originalImageName":"20251216-E137C-R0"} | NO | HVAC | ABB | 16/12/2025 | ABB | Pending Petrobras | 20251216-Duct inspection hatches with size of 600x600mm have been added in 3D model for both battery room supply ducts. | 15/12/2025 | 16.0000000000000 | 17Dec25: Noted on the addition of hatches. | 16/12/2025 |  |  |  | HVAC |  |  |  | HVAC |  | Mun | Noted, closed. | 02/01/2026 | -1.37500000000000 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E138C | M17 |  | M17-E138C | According to ABS requirement, automatic fire damper shall be capable of being closed manually from both sides of the bulkhead or deck. Provision of hand valve in fire damper served compartment/ location to be further confirmed with ABS. | Mun/Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b8c8f4d0e1a648f19e6947a11f7084ad][1]_[2].png","originalImageName":"E138C-M17"} |  |  | YES | HVAC | ABB | 30/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 18/12/2025 | ID: 537
E139C | M17 |  | M17-E139C | General Comment :Proper Support to be provided for the following Hand Valve,HV-5250631B HV-5250671B HV-5250641B HV-5250691B HV-5250694B HV-5250652B HV-5250651B HV-5250681B HV-5250662B HV-5250661B | Tamer/Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[13bbdb4674cb483ebede6fa844c2b1b0][1]_[2].png","originalImageName":"E139C-M17"} |  |  | YES | PIPING | ABB/CIMC | 18/12/2025 | CIMC | Pending KBR | 2026/01/09： Support for HV has been added. | [7 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 09/01/2026 | ID: 842
E140C | M17 |  | M17-E140C | Cable tray support to be shifted it is clash with Damper Maintenance volume | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[986cc6a6a7d2412e89358aa376c1e275][1]_[2].png","originalImageName":"E140C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7912f0cb819742d091298e77a294c8cc][2]_[23].png","originalImageName":"E140C-20251218"} | Re-work | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/18, this support had been shift to avoid clash with damper maintenance space |  |  | KBR has no comments. | 23/12/2025 | Roberto |  |  | Instrument |  |  |  | HVAC |  | Mun | Noted, closed. | 02/01/2026 | -1.37500000000000 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E141C | M17 | Level 5 | M17-E141C | cable Tray clash with Mantainenace Volume | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1ce27da6f55c4e41be1d9e574cd70669][1]_[2].png","originalImageName":"E141C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[aa5dd731c0df4ebbb329ccadd5a91ef4][2]_[31].png","originalImageName":"141"} | YES | INSTRUMENTATION | ABB/CIMC | 24/12/2025 | CIMC | Pending Petrobras | 2025/12/25: cable tray is shifted to another derection and the clash is cleared. | 24/12/2025 | 7.00000000000000 | KBR has no comments. | 29/12/2025 | Roberto |  |  | Instrument |  |  |  | HVAC |  | Mun | Noted, closed. | 02/01/2026 | -1.37500000000000 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E142C | M17 |  | M17-E142C | Lower the PDIT Height (1.4 m from the Deck floor) for Ventilation Fan VT-5254002A,B,C;VT-5254001A,B,C for operation point of view | Tamer/Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[af6a5c7bd49948c9b9f91240179228dc][1]_[2].png","originalImageName":"E142C-M17"} |  |  | NO | HVAC | ABB | 11/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 17/12/2025 | ID: 539
E143C | M17 |  | M17-E143C | PDG to be included for all the Ventilation Fan VT-5254002A,B,C;VT-5254001A,B,C | Allan | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7831ce39e2b94279a6a7c3879b1b1330][1]_[2].png","originalImageName":"E143C-M17"} |  |  | NO | HVAC | ABB | 24/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 29/12/2025 | ID: 539
E144C | M17 |  | M17-E144C | PDIT is missing for all Battery room Exhaust Fan EXT-5255001A,B;EXT-5255002A,B | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[44c3f3bae4e7449b8202b91cade9cdc3][1]_[2].png","originalImageName":"E144C-M17"} |  |  | NO | HVAC | ABB | 11/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 17/12/2025 | ID: 539
E145C | M17 |  | M17-E145C | Shift the Push Button to the Platform Level, individually for each Fan not as group support. | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a04fee32d1724da6a0af47f3a7833d18][1]_[4].png","originalImageName":"E145C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[68882eb06b014436a32b8043c8206d69][2]_[24].png","originalImageName":"E145C-20251211"} | YES | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/09, these push button had been shift to platform level. 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 08/12/2025 | 8.00000000000000 | [5 empty] | Instrument |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 18/12/2025 | ID: 537
E146C | M17 |  | M17-E146C | Tubing to be modelled for PDIT and PDIT shall be located to the same level as Push button (E-145C-M17) PDIT-5250930~936 | Mun | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[2fb16e0c60ae4ad18f1fc7c54022790d][2]_[30].png","originalImageName":"~"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6b36a2c851a54bbe8e391d2cfe14d678][2]_[27].png","originalImageName":"E146"} | YES | PIPING | ABB/CIMC | 18/12/2025 | CIMC | Pending Petrobras | 2025/12/22: Tubing has been modelled for PDIT-5250930~936 and PDIT has been located to the same level as Push button (E-145C-M17). |  |  | 2025Dec30: Noted | 30/12/2025 | Allan |  |  | HVAC |  |  |  | HVAC |  | Mun | Noted, closed. | 02/01/2026 | -1.37500000000000 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E147C | M13R |  | M13R-E147C | To check the feasbilty to shift the fire Damper DF-5250689 from the Bulk Head | Bruno/Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6e962c1fda024bf8b292fb690f3b1985][1]_[2].png","originalImageName":"E147C-M13R"} |  |  | YES | HVAC | ABB | 30/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 18/12/2025 | ID: 537
E148C | M13R |  | M13R-E148C | Cable tray clash with maintenance Volume of Fire Damper DF-5250688, DF-5250602 | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c856dfd6d722480297e261d642f3e3e7][1]_[2].png","originalImageName":"E148C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[09e6078cb58343be87b6c51c03fc3597][2]_[19].png","originalImageName":"20260101_E148C_R0"} | Re-work | HVAC | ABB | 30/12/2025 | CIMC | Pending Petrobras | 01/01/2026:The cable trays have been moved to avoid clashing with the maintenance volume of fire damper DF-5250688, DF-5250602. |  |  | 02Jan26: Noted | 02/01/2026 | Allan |  |  | HVAC |  |  |  | HVAC |  | Mun | Noted, closed. | 02/01/2026 | -1.41666666666424 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E149C | M13R |  | M13R-E149C | General Comment :Proper Support to be provided for the following Hand Valve HV-5250687B HV-5250689B HV-5250682B HV-5250688B HV-5250602B HV-5250683B HV-5250684B | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[15c01c1034a04907968047f340236ae7][1]_[2].png","originalImageName":"E149C-M13R"} |  |  | YES | PIPING | ABB/CIMC | 18/12/2025 | CIMC | Pending KBR | 2026/01/09： Support for HV has been added. | [7 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 09/01/2026 | ID: 842
E150C | M13R |  | M13R-E150C | Hand Valve HV-5250682B & HV-5250683B to be moved inside the Battery Room Level-1 & Battery Room Level-2 respectively in accessible way | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7d99dd4d56a44f73be3a8b4fb433e0fd][1]_[2].png","originalImageName":"E150C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[4f3ea86e0f214ad8a49e620006d0d8bb][2]_[15].png","originalImageName":"E150"} | YES | PIPING | ABB/CIMC | 18/12/2025 | CIMC | Close | 2025/12/17: Hand Valve HV-5250682B & HV-5250683B has been moved inside the Battery Room Level-1 & Battery Room Level-2 respectively. |  |  | 18Dec25: Noted on the new locations. Ensure height is as per Ergonomics requirement. | 18/12/2025 | Allan |  |  | HVAC |  |  |  | HVAC |  | Mun | Noted, ABB to ensure height is as per Ergonomics requirement. | 02/01/2026 | 11.2131944444409 | Valve was move inside | Julius Orzales |  | 13/01/2026 | Valve was move inside | HVAC |  | 13/01/2026 | -1.58819444444089 |  |  | 13/01/2026 | ID: 484
E151C | M13R |  | M13R-E151C | Tubing to be clear from Fire Damper DF-5250682 Maintenance Volume | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[19f18be007a54f1fb676aabc02e06ea3][1]_[2].png","originalImageName":"E151C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[31b308f733584dedb62151070877db5b][2]_[12].png","originalImageName":"E151C-20251211"} | YES | PIPING | ABB/CIMC | 10/12/2025 | CIMC | Pending Petrobras | 2025/12/11, the tubing had been adjusted to avoid obstruct maintenance volume 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 10/12/2025 | 6.00000000000000 | [5 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 18/12/2025 | ID: 537
E152C | M13R |  | M13R-E152C | Cable Tray/Instrument Tubing/cable tray Support clashes with Fire Damper DF-5250621. DF-5250686,DF-5250684,DF-5250685,DF-5250623 Maintenance Volume to be recitified | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8b4ac5c9071a44939941b0c3a722a9b6][1]_[2].png","originalImageName":"E152"} |  |  | Re-work | HVAC | ABB | 30/12/2025 | ABB | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 29/12/2025 | ID: 539
E153C | M13R |  | M13R-E153C | Ball ValV-HV-5250684B to be shifted inside the Air lock Room | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c19a130e09324439ac78d2b0a0963409][1]_[2].png","originalImageName":"E153C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b702ed688fea4cfba75d74a9341d4a69][2]_[24].png","originalImageName":"E153"} | YES | PIPING | ABB/CIMC | 16/12/2025 | CIMC | Pending Petrobras | 2025/12/22: PDA-M13-E-05 has been located in the M13-203 Room, so Valve HV-5250684B need to be located outside the room instead of inside the air lock room. |  |  | 2025Dec30: Noted. ABB / CIMC to ensure that the locations of the valve and the damper panel are clear of any obstruction. | 30/12/2025 | Allan |  |  | HVAC |  |  |  | HVAC |  | Mun | Noted, ABB to ensure the new hand valve (HV-5250684B) location is not obstructed by CXE-L-M13-038. | 02/01/2026 | -1.41666666666424 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E154C | M13R |  | M13R-E154C | M13R Level-2 Generator Power Panel Room PDIT to be removed in D&ID and 3D Model | Mun/Allan | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[20c8afa5e172465a87f155204cdf08e9][1]_[2].png","originalImageName":"E154C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9059e8b1325d4b5f9d05de23b6fb0b34][1]_[9].png","originalImageName":"E154C-20251211"} | Re-work | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, this PDIT had been removed from 3D model 2025/12/19: KBR mentioned tubing has been deleted,please review by the latest model | 18/12/2025 | 24.0000000000000 | 19-Dec: CIMC to remove the tubing since the instrument has been removed. Refer attachment E154C.png. 24-Dec: KBR has no comments. | 23/12/2025 | Roberto |  |  | Instrument |  |  |  | HVAC |  | Mun | Noted, closed. | 02/01/2026 | 11.1645833333387 | removed from model | Julius Orzales |  | 13/01/2026 | removed from model | HVAC |  | 13/01/2026 | -1.58125000000291 |  |  | 13/01/2026 | ID: 484
E155C | M13R |  | M13R-E155C | Cable tray to be clear from Temperature Sensor TE-5250603 /TE-5250604 | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[2bfb4ad770e34d3fb53b41cad7c65b60][1]_[2].png","originalImageName":"E155C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[0ee34001adc6434b827161903c44d426][2]_[10].png","originalImageName":"E155C"} | YES | INSTRUMENTATION | ABB/CIMC | 18/12/2025 | CIMC | Pending Petrobras | 2025/12/12：The cable tray has been moved away from the temperature sensor 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 11/12/2025 | 5.00000000000000 | [5 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 18/12/2025 | ID: 537
E156C | M13R |  | M13R-E156C | General Comments- 3 way Valve is required as per the drawing and to be Modelled ,HV-5250687B,HV-5250689B,HV-5250682B,HV-5250688B,HV-5250602B,HV-5250683B,HV-5250684B | Mun | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0c96d805a64e4552ae7a6247bd264239][1]_[2].png","originalImageName":"E156C-M13R"} |  |  | Re-work | HVAC | ABB | 18/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 14/01/2026 | ID: 539
E157C | M17 |  | M17-E157C | General Comments- 3 way Valve is required as per drawing and to be Modelled ,HV-5250631BHV-5250671B HV-5250641B HV-5250691 BHV-5250694 BHV-5250652B HV-5250651B HV-5250681B HV-5250662B HV-5250661B | Mun | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1c48e795d0a64201b0e2f62d87be88eb][1]_[2].png","originalImageName":"E157C-M17"} |  |  | Re-work | HVAC | ABB | 18/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 14/01/2026 | ID: 539
E158C | M13R |  | M13R-E158C | Shorten the length of the PDIT support PDIT-5250905 | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d1e3bf4d9e48412c920288f412b29e03][1]_[4].png","originalImageName":"E158C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7bb11364c4914f158b197a3961b4e6ec][2]_[17].png","originalImageName":"E158C"} | YES | INSTRUMENTATION | ABB/CIMC | 21/12/2025 | CIMC | Close | 2025/12/12：The PDIT support had been shorten. | 11/12/2025 | 30.0000000000000 | KBR has no comments. | 23/12/2025 |  |  |  | Instrument |  |  |  | HVAC |  | Mun | Noted, closed. | 02/01/2026 | 10.2194444444467 |  | Julius Orzales |  | 12/01/2026 |  | HVAC |  | 12/01/2026 | -1.63611111111095 |  |  | 12/01/2026 | ID: 484
E159C | M13R |  | M13R-E159C | Tubing to be modelled for PDIT-5250903, PDIT-5250904 PDIT-5250905 &PDIT-5250906 | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4fddb2a40e094ec4be58aa97b4bb5b7e][1]_[2].png","originalImageName":"E159C-M13R"} |  |  | YES | PIPING | ABB | 18/12/2025 | ABB | Pending ABB/CIMC | lack of Hookup drawing | [7 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 26/12/2025 | ID: 539
E160C | M13R |  | M13R-E160C | Valve and instrument mounted on Expansion tank to be Modelled | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[fc5323e1468a498da53a96984b808657][1]_[2].png","originalImageName":"E160C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1094fcc9e3b24f7da1b0b808f53b246b][2]_[15].png","originalImageName":"20251223-E160C-R0"} | NO | HVAC | ABB/CIMC | 18/12/2025 | CIMC | Pending Petrobras | 20251223:CIMC have splited the valve and instrument on 3D model. |  |  | 2025Dec30: Noted. ABB / CIMC to ensure that the dimension of valves and instrument are correct. | 30/12/2025 | Allan |  |  | HVAC |  |  |  | HVAC |  | Mun | Noted. ABB / CIMC to ensure that the dimension of valves and instrument are correct. | 02/01/2026 | -1.41666666666424 | [5 empty] | HVAC | [5 empty] | 02/01/2026 | ID: 101
E161C | M17 |  | M17-E161C | Insulation for the Penetration to be removed for all AHU | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[96d39e39f0634cb3b135a104f49b827d][1]_[2].png","originalImageName":"E161C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1ca15a523f7f41778b5417370be6f58f][2]_[10].png","originalImageName":"E161C-20251209"} | NO | PIPING | ABB/CIMC | 08/12/2025 | CIMC | Pending Petrobras | 2025/12/09, the insulation below penetration had been removed 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 5.00000000000000 | [5 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 15/12/2025 | ID: 19
E162C | M13R |  | M13R-E162C | Insulation for the Penetration to be removed for all AHU | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[9467c3f1d3fd4fdba80eb6596ff409cc][1]_[2].png","originalImageName":"E162C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[882b0add7b1a4bcca52d54c324158c70][1]_[9].png","originalImageName":"E162C-20251209"} | NO | PIPING | ABB/CIMC | 08/12/2025 | CIMC | Close | 2025/12/09, the insulation below penetration had been removed 2025/12/10, as per close out meeting discussion , the punch can be transfer to PB close | 08/12/2025 | 33.0000000000000 | [5 empty] | HVAC |  |  |  | HVAC | [5 empty] | Insulation below penetration was remove | Julius Orzales |  | 12/01/2026 |  | HVAC |  | 12/01/2026 | -1.64513888888905 |  |  | 12/01/2026 | ID: 484
E163C | M17 |  | M17-E163C | Spreaker COR-5518454B to right side near to column to add vertical cable tray as current location is not able to add due to limit space | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[831adce14b4841fbb90ea9008217670d][1]_[2].png","originalImageName":"E163C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a5db96ff2c5347418145dc4d29baf1f4][2]_[20].png","originalImageName":"163"} | Re-work | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10,the spreaker had been removed | 09/12/2025 | 19.0000000000000 | Agreed with ABB/CIMC action. | 25/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Speaker relocated based on punch. | 29/12/2025 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 98
E164C | M17 |  | M17-E164C | Branch Cable tray is missing for the speaker COR-5518456B | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[142780f48aa2440691b3a0addc051fba][1]_[2].png","originalImageName":"E164C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[71cfe9ce4d354f469d01c6e09823bb5d][2]_[22].png","originalImageName":"164"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10 the cable rtay had been added | 09/12/2025 | 19.0000000000000 | Agreed with ABB/CIMC action. | 25/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Field cable tray added (TC-M17-S-B-TRAY-01525-TRAY-0001) | 29/12/2025 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 98
E165C | M17 |  | M17-E165C | Junction box CDI-5518021B Shall be moved up and provide Branch cable tray cosnidering cable list mentioned in Single Line diagram | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[feb65630150b49008a8d13ad34ffc76e][1]_[2].png","originalImageName":"E165C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2c897dec049d48d5a4d1ae9e33f7fa9f][2]_[21].png","originalImageName":"165"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 19.0000000000000 | Agreed with ABB/CIMC action. | 25/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | JB shifted and field cable tray modelled. | 29/12/2025 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 98
E166C | M17 |  | M17-E166C | Junction box AU-5518002 Shall be moved right side to avoid clash with network cable tray | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[41b48d14234c49c29f077258cfb8f5f5][1]_[2].png","originalImageName":"E166C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[61b1416d4a64437084e90e2fbc13b38e][2]_[27].png","originalImageName":"166c"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated 2026/01/05：closeout snapshot has been updated, please refer to latest model, there is no potential clash issue about the door openning. | 04/01/2026 | 0 | Agreed with ABB/CIMC action. | 25/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Refer to email sent to Junwei on 30 Dec 25. Will the door opening of AU-5518002 blocked by the cable tray? Seatrium 6-Jan-26: Well noted. The current location of AU is okay. | 05/01/2026 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 06/01/2026 | ID: 98
E167C | M17 |  | M17-E167C | Telecom support tagging shall be updated as per the telecom tagging Procedure | Manohar | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1a7f31a764e94bfcacd3bf2163b2fda4][1]_[2].png","originalImageName":"E167C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2798f63d320d49748bae1e3cc99d7467][1]_[4].png","originalImageName":"167"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, All relecom support name has been updated | 09/12/2025 | 19.0000000000000 | Agreed with ABB/CIMC action | 25/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Hierarchy updated as per punch comment. | 29/12/2025 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 98
E168C | M17 |  | M17-E168C | Spreaker COR-5518457A clashe with Door shelter shall be relocated | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[02b0e7c66fd045f8b97d3613eaf857dc][1]_[2].png","originalImageName":"E168C-M17","serverRelativeUrl":null,"id":null,"serverUrl":null,"thumbnailRenderer":null} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a35dd4f882c04b50976f2570c24cc0e8][2]_[20].png","originalImageName":"168"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 19.0000000000000 | Agreed with ABB/CIMC action | 25/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Speaker shifted upward. | 29/12/2025 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 98
E169C | M17 |  | M17-E169C | Branch cable tray for Camera CAM-5514114 is mssing and to be modelled | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b1f43857cd3646c4b63030fd11dd7b27][1]_[2].png","originalImageName":"E169C-M17","serverRelativeUrl":null,"id":null,"serverUrl":null,"thumbnailRenderer":null} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[cc32a142a9564e25a23a07e49d400ccc][2]_[19].png","originalImageName":"169"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 18.0000000000000 | Agreed with ABB/CIMC action | 25/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | Verified in 3D Model dated 2025-12-26. Branch cable tray for CAM-5514114 has been modelled. | 29/12/2025 | -1.63888888889051 | [5 empty] | TELECOM | [5 empty] | 29/12/2025 | ID: 105
E170C | M17 |  | M17-E170C | Camera CAM-5514156 Name Plate shall be moved to bottom of the camera | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[805794dfaf744fd6ba83aa2d8d74227d][1]_[2].png","originalImageName":"E170C-M17","serverRelativeUrl":null,"id":null,"serverUrl":null,"thumbnailRenderer":null} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[0f31079a624a4a1bb9bfedd82956cc1d][2]_[20].png","originalImageName":"170"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated 2025/12/29: nameplate is not blocked by cable tray, if SEA's suggestion must to be followed, please confirm if the installation height can be adjust to 2.95m | 28/12/2025 | 1.00000000000000 | Agreed with ABB/CIMC action | 25/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2025/12/29: Consider raising the CAM-5514156 mounting height slightly so that camera nameplate is fully visible and not obscured by the cable tray 2025/12/30: Noted on the nameplate location confirmation. | 30/12/2025 | -0.677777777775191 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 105
E171C | M17 |  | M17-E171C | Camera CAM-5514156 shalll be lowered down to a height of 2.8m and to be inlin with Typical installation, | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[567d91f018164c929d0c48f70244af5f][1]_[2].png","originalImageName":"E171C-M17","serverRelativeUrl":null,"id":null,"serverUrl":null,"thumbnailRenderer":null} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bc38cfc605e3487fb5fc19a5930bbc16][2]_[61].png","originalImageName":"171"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated 2025/12/29: close out snapshot is revised, installation height is align with typical installation drawing(2.8m) 2026/01/04：camera installation height is raised up to 2.95m to avoid nameplate blocking as per SEA advice. 2026/01/05: sufficient access clearance can be ensured for camera installation and maintenance, front side has been completely cleared without any blockage. | 04/01/2026 | 1.00000000000000 | Attached snapshot is incorrect, kindly update the correct snapshot. | 24/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2025/12/29: Incorrect closing snapshot. Please recheck camera installation height, it is currently too near with electrical cable tray. 2025/12/30: Camera is located behind the cable tray, which may restrict installation and future maintenance access. Please review and confirm whether this arrangement provides sufficient access clearance. 2026/01/05: Nameplate is ok. However, cable tray remains as a physical obstruction in the access path, regardless camera elevation. ABB/CIMC to confirm whether sufficient access clearance for installation and maintenance is achievable with the current arrangement. 2026/01/07: Noted on ABB/CIMC confirmation | 07/01/2026 | -1.40972222221899 | [5 empty] | TELECOM | [5 empty] | 07/01/2026 | ID: 105
E172C | M17 |  | M17-E172C | Seatrium to reevalute the location of POB Beacon to Bulk head location instead of current installation as Standalone based on coverage study BLE-5511335,BLE-5511337,BLE-5511357 | Ratha | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7dcd2ba61ed341669cc917af9d0b8cce][1]_[2].png","originalImageName":"E172C-M17","serverRelativeUrl":null,"id":null,"serverUrl":null,"thumbnailRenderer":null} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[dff1734e9f1b4e9381b325070a02e879][2]_[20].png","originalImageName":"172C"} | Re-work | TELECOM | Seatrium | 09/12/2025 | Seatrium | Pending Petrobras | 2025/12/18, please Seatrium to coordinate and confirm 2025/12/29：BLE-5511335,BLE-5511337,BLE-5511357,BLE-5511358 are shifted to bulkhead as per SEA advice in the email. | 28/12/2025 | 1.00000000000000 | [5 empty] | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2025/12/24: Recommended to relocate POB beacons to nearby bulkheads as per verified by coverage simulation by Vendor. Please refer to email sent to ABB/CIMC on 2025/12/24 for details. 2025/12/30: Verified with 3D model dated 2025-12-26. Noted on the beacon's relocation. | 30/12/2025 | -0.719444444446708 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 105
E173C | M17 |  | M17-E173C | Support for POB Beacon BLE-5511343 is missing and to be modelled | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8fc55afb870c40849a4fca9e41be198d][1]_[2].png","originalImageName":"E173C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bc8a940fe7bf48cc88d4bbf989a95283][2]_[20].png","originalImageName":"173"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 19.0000000000000 | Agreed with ABB/CIMC action | 24/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Support for POB beacon modelled. | 29/12/2025 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 98
E174C | M17 |  | M17-E174C | ACO-5515001 directional coupler shall be relocated as per the markup | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[07d2162237ed4a988d20f16b8dbd5208][1]_[2].png","originalImageName":"E174C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[d8d9a39f95b44e76abef6d76a57c4b30][2]_[32].png","originalImageName":"174"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated 2026/01/01: the punch description is updated and the tag no is corrected as ACO-5515001, the jumper cable simulation model is also added for easy understanding of cable bending. | 31/12/2025 | 3.00000000000000 | Agreed with ABB/CIMC action | 24/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2025/12/31: The punch description is for ACO-5515004 but the images are ACO-5515001. Please confirm which equipment is correct. 2026/01/05: Noted on ABB/CIMC update. | 05/01/2026 | -1.39236111110949 | [5 empty] | TELECOM | [5 empty] | 05/01/2026 | ID: 105
E175C | M17 |  | M17-E175C | Power spiltor is with 3 way , one connector deleted and ensure proper cable bending radius for cooxial cables | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[572e9704ba0b49c595254957936174f7][1]_[2].png","originalImageName":"E175C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[0d08f0547a634c5da38d5c1524fc2dbf][2]_[20].png","originalImageName":"175"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 20.0000000000000 | Agreed with ABB/CIMC action | 24/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2025/12/31: Verified with 3D model dated 2025-12-26. Agreed with ABB/CIMC updates. | 31/12/2025 | -1.42708333333576 | [5 empty] | TELECOM | [5 empty] | 31/12/2025 | ID: 105
E176C | M17 |  | M17-E176C | Cable to the juction box is 2 nos as per SLD , 4Nos OF Cable glands to be deleted | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[101bfb2170b546b9b827505c09d8c2e2][1]_[2].png","originalImageName":"E176C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c022a16eb1cf4c92ae2db8fbce0b43dc][2]_[19].png","originalImageName":"176"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 19.0000000000000 | Agreed with ABB/CIMC action | 24/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Cable entry quantity updated as per OLD | 29/12/2025 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 98
E177C | M17 |  | M17-E177C | TRX-5515002 Transceiver shall be installed in the console by Screw type arrangement | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b53df7a13aa74e7ea4f5e110e574f6e9][1]_[2].png","originalImageName":"E177C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1b027970100f4d7eb029ed4fc1e8d0fe][2]_[20].png","originalImageName":"177"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 19.0000000000000 | Agreed with ABB/CIMC action | 24/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Radio base station relocated as per punch comment. | 29/12/2025 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 98
E178C | M17 |  | M17-E178C | Acess point location not align with Support | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[fd5640286f644138a9a5d6ff7ab68925][1]_[2].png","originalImageName":"E178C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[17af0ab49cdb40ec8d9fea78e381fed6][2]_[19].png","originalImageName":"178"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 19.0000000000000 | Agreed with ABB/CIMC action | 24/12/2025 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | PA-5517064 is now relocated to the WLAN support, | 29/12/2025 | -1.00000000000000 | [5 empty] | TELECOM | [5 empty] | 30/12/2025 | ID: 98
E179C | M17 |  | M17-E179C | Additional Support to be provided for the camera support to avoid vibration | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d7489dbefc744d7fa14b46ddb762076c][1]_[2].png","originalImageName":"E179C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[41427f3030e0455fa9abc2f583f80f94][1]_[4].png","originalImageName":"E179C"} | Re-work | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated | 09/12/2025 | 28.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/08: Additional support has been included. | 08/01/2026 | -1.60416666666424 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 105
E180C | M17 |  | M17-E180C | Branch cable tray for Camera CAM-5514126 is mssing and to be modelled | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[17347924b96942b5a616fc3cb0823608][1]_[2].png","originalImageName":"E180C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[05eb1957cddd43d19d18f7b82f86241a][1]_[4].png","originalImageName":"E180C"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated | 09/12/2025 | 28.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/08: Cable tray has been modelled. | 08/01/2026 | -1.61527777777519 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 105
E181C | M17 |  | M17-E181C | POB Beacon shall be lower down to a height of 1.8m | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7f2cca7d974f499a80ad43624724f5fa][1]_[2].png","originalImageName":"E181C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b99d7812b0eb402aa0f3a6248a5daa59][2]_[21].png","originalImageName":"E181"} | Re-work | TELECOM | ABB/CIMC | 18/12/2025 | CIMC | Pending Petrobras | 2025/12/17, this POB beacon had been lower down to 1.8m height | 16/12/2025 | 21.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/08: POB beacon (tag number: BLE-5511345) has been lowered to 1.8m. | 08/01/2026 | -1.62986111111240 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 105
E182C | M17 |  | M17-E182C | General Comments :Branch cable tray for alll the telecom devices shall be extended upto the devices | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[eb115be423384739bccab04b8828d652][2]_[25].png","originalImageName":"182c"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[06aee72d445e485da1d4d24c89e6684a][1]_[4].png","originalImageName":"E183C"} | Re-work | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Rejected | 12/10/2025：3D model updated 2026/01/12： punch snapshot is changed to correct one, please review again | 11/01/2026 | 0 | Agreed with ABB/CIMC action,but check the snapshot is correct? | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | 2026/01/09: Punch snapshot is showing POB Beacon which does not required any cable tray nearby. ABB/CIMC to confirm that all telecom devices have an extended cable tray up to the devices as per punch comment. 2026/01/13: Please check the field tray of COR-5518454A, ANT-5515008, PA-5517067, PA-5517068, CAM-5514141. | 09/01/2026 | 2.58750000000146 | [5 empty] | TELECOM | [5 empty] | 13/01/2026 | ID: 98
E183C | M17 |  | M17-E183C | Outdoor Speaker support shall be shorten and move close to the Bulk head COR-5518466B COR-5518466A COR-5518465A | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[196168179933421b86f10ff7ea940bab][1]_[2].png","originalImageName":"E183C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[038abbb7895e4db280bc9c64e974f40f][1]_[4].png","originalImageName":"E183C"} | Re-work | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated | 09/12/2025 | 29.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | COR-5518466B COR-5518466A COR-5518465A Speaker support was shortened. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E184C | M17 |  | M17-E184C | Speaker support COR-5518463A is not in line speaker location | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d26573f2e85448279aaca07ab31c25f9][1]_[2].png","originalImageName":"E184C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[dec56910039d40ed800f8ac6c95ee7f3][2]_[24].png","originalImageName":"E184"} | YES | TELECOM | ABB/CIMC | 16/12/2025 | CIMC | Pending Petrobras | 2025/12/17,this speaker support had been updated. | 16/12/2025 | 22.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Speaker COR-5518463A model updated to align with support. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E185C | M17 |  | M17-E185C | Speaker COR-5518465B Shall be relocated to the right side and to be install in the structure | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6a77d74a86cd49ad902df603ac2192b2][1]_[2].png","originalImageName":"E185C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[00f25422c3fb4559976878a86171bce1][2]_[22].png","originalImageName":"E185"} | Re-work | TELECOM | ABB/CIMC | 16/12/2025 | CIMC | Pending Petrobras | 2025/12/17, This speaker had been relocated on structure column. | 16/12/2025 | 22.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Speaker had been relocated on structure column. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E186C | M17 |  | M17-E186C | coaxial cable bending radius to be ensured for terminating to Power Spliter DIV-5515004 | Christiano/Manohar | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[130f30167b7b44dd91b99b57edfb2bed][1]_[2].jpg","originalImageName":"E186C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[aca5f0195e3a4b5fba26c35e099d3a52][2]_[28].png","originalImageName":"E186C"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated 2026/01/09: The coaxial cable simulations have been shown at the splitter ports | 08/01/2026 | -1.00000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/08: Suggest for ABB/CIMC to show coaxial cable simulation at the splitter ports to verify that minimum cable bending radius can be complied with the current arrangement. 2026/01/09: Noted on the coaxial cable simulation model. | 09/01/2026 | -1.58055555555620 | [5 empty] | TELECOM | [5 empty] | 09/01/2026 | ID: 105
E187C | M17 |  | M17-E187C | Electrical and instrument cable tray Clash shall be resolved | Christiano/Manohar | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6135845904ae496f9c567534962647ba][1]_[2].png","originalImageName":"E187C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[db0ad3add3ae4211901a3c8b9157cdf7][2]_[21].png","originalImageName":"E187"} | NO | TELECOM | ABB/CIMC | 18/12/2025 | CIMC | Pending Petrobras | 2025/12/17, the clash had been cleared | 16/12/2025 | 22.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Clash was resolved. However, the punch snapshot is not correct. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E188C | M17 |  | M17-E188C | Antenena Height shall be installed at a height of 2.5m in line Telecom typical installation details | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a4827f06328a4c02994d372ebabf5c5e][1]_[2].png","originalImageName":"E188C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b76bc2c07bba4bb8973dd2892d618d45][2]_[20].png","originalImageName":"E188"} | Re-work | TELECOM | ABB/CIMC | 16/12/2025 | CIMC | Pending Petrobras | 2025/12/17,the antenena height had been relocated on 2.5m | 16/12/2025 | 22.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | The antenena height had been relocated on 2.5m | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E189C | M17 |  | M17-E189C | Name Plate of telephone system BLT-5516041,BLT-5516042,BLT-5516043 , shall be relocated at the bottom of Equipment Support | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[775aba362c6d4074916b3cc240390eb0][1]_[2].png","originalImageName":"E189C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a192c8d2564a45fc9f368b1f5e9f1531][1]_[5].png","originalImageName":"E189C"} | NO | TELECOM | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated | 10/12/2025 | 28.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Name Plate of telephone system BLT-5516041,BLT-5516042,BLT-5516043 relocated to the bottom of support | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E190C | M17 |  | M17-E190C | Shift the camera CAM-5514140 to the left side as the current postion is block by Column | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[39043e7ccd844180bc87b9f1e2c0853d][1]_[2].png","originalImageName":"E190C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[fed7f18fb677441183cb03e617392faa][1]_[5].png","originalImageName":"企业微信截图_17654438074230"} | NO | TELECOM | ABB/CIMC | 10/12/2025 | CIMC | Pending Petrobras | 12/11/2025：3D model updated | 10/12/2025 | 28.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | CAM-5514140 shifted as per punch comment. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E191C | M17 |  | M17-E191C | General comment: ALL indoor PAGA Speaker support shall be modified to avoid clash with Cable Entry Location | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[f3991e0632e348b9ac45793bf6795900][1]_[2].png","originalImageName":"E191C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[ceb83819719948d88a2c2a870752a1ed][1]_[4].png","originalImageName":"E191C"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated 2026/01/12: punch description is changed to PAGA speaker, please review again | 11/01/2026 | 0 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | 2026/01/09: Punch is for all indoor cameras, however the images captured are speakers. Please provide correct snapshots. 2026/01/13: Speaker support was updated with L bracket at top without protruding at the rear. | 13/01/2026 | -1.38888888889051 | [5 empty] | TELECOM | [5 empty] | 13/01/2026 | ID: 98
E192C | M17 |  | M17-E192C | Lightning Arrestor PS-5515002 & PS-5515009 shall be updated as per Vendor drawing to add mounting bracket | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[19bfe92302474258b47c8f436adb9570][1]_[2].png","originalImageName":"E192C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c6f7db1519a14dbc92132b4aca375c9a][1]_[5].png","originalImageName":"企业微信截图_17654438451999"} | NO | TELECOM | ABB/CIMC | 10/12/2025 | CIMC | Pending Petrobras | 12/11/2025：3D model updated | 10/12/2025 | 28.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/09: Lightning arrestors have been modelled consistent with vendor drawing. | 09/01/2026 | -1.42083333332994 | [5 empty] | TELECOM | [5 empty] | 09/01/2026 | ID: 105
E193C | M17 |  | M17-E193C | The Branch Cable tray shall be extended upto the TMD-5517930 | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7622559450854db49ffa39bb19e89d0f][1]_[2].png","originalImageName":"E193C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[08a7ccf1a59e4f5e97d0831e8b9477d8][2]_[19].png","originalImageName":"企业微信截图_17654438839802"} | NO | TELECOM | ABB/CIMC | 10/12/2025 | CIMC | Pending Petrobras | 12/11/2025：3D model updated | 10/12/2025 | 28.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | TC-M17-S-A-TRAY-03527-TRAY-0202 added. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E194C | M17 |  | M17-E194C | Camera Located in indoor Level-4 shall be rise upto the height of 2.3 instead of 2.2m in line Level-1,level-2 &Level-3 | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[67984b18b5e04b1ba892c45da5998ba2][1]_[2].png","originalImageName":"E194C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[68cbcebca53740f5a99c816cd37130da][1]_[4].png","originalImageName":"E194C"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated | 09/12/2025 | 29.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Agreed with ABB/CIMC action. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E195C | M17 |  | M17-E195C | Vertical Branch tray for the camera CAM-5514147 shall be moved to right side for proper cable entry, Camera CAM-5514147 & CAM-5514148 smounting accessories to be align with Vendor drawing | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[dc7ba31517d343af801a100041ce45d4][1]_[2].png","originalImageName":"E195C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[71258da81072402b86e4d2eefdf98db8][1]_[4].png","originalImageName":"E195C"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated | 09/12/2025 | 29.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Cable tray shifted and swivel support was modelled. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E196C | M17 |  | M17-E196C | POB BLE-5511366 Shall be relocated to the right side and to be install in the structure | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[138768dfea7f442db2f091dfc9cced2b][1]_[2].png","originalImageName":"E196C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[387a02e3229244509bb26143ebccde39][1]_[4].png","originalImageName":"E196C"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated | 09/12/2025 | 29.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/08: Beacon has been updated as per punch. | 08/01/2026 | -0.740972222221899 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 105
E197C | M17 |  | M17-E197C | Leaky cable Crf-DIV-5515006.003 shall be rerouted | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[06d11020f48c4a14a7ca82ef9ee35d5f][1]_[2].png","originalImageName":"E197C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[13bb19b042014647ae2195bdb57b4ffb][1]_[4].png","originalImageName":"E197C"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Rejected | 12/10/2025：3D model updated | 09/12/2025 | 29.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/09: Punch snapshot and closing snapshot look the same & do not demonstrate the rerouted leaky cable as per punch comment. ABB/CIMC to clearly show the rerouted cable. In addition, ABB/CIMC to ensure the route of the leaky cable is not obstructed by any structure below it to prevent coverage degradation. | 09/01/2026 | -1.61597222222190 | [5 empty] | TELECOM | [5 empty] | 09/01/2026 | ID: 539
E198C | M17 |  | M17-E198C | POB BLE-5511367 shall installed in Stand alone telecom support instead of Installing in Lighting Support | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[3fed18c3957b4fe8b73c89e3d3d837ee][1]_[2].png","originalImageName":"E198C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[23a037a01c9c44028a68878011ef7a9f][2]_[23].png","originalImageName":"e198c"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/10/2025：3D model updated 2026/01/12: original punch was cancelled during Electrical design review session, close out snapshot is updated. | 11/01/2026 | 0 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/08: ABB/CIMC to re-check closing snapshot not aligned with 3D model dated 2026-01-06. 2026/01/13: Noted on ABB/CIMC update. | 13/01/2026 | -1.41527777777810 | [5 empty] | TELECOM | [5 empty] | 13/01/2026 | ID: 105
E199C | M17 |  | M17-E199C | POB BLE-5511372 , BLE-5511372 shall moved to Telecom support instead of Lighting Support | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[89b164aee95e4923a1eb1c173e310102][1]_[2].png","originalImageName":"E199C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6708690af3e5405fb13a25f55156e712][1]_[4].png","originalImageName":"企业微信截图_17653319344643"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 29.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/08: Beacon has been relocated as per punch. | 08/01/2026 | -0.747916666667152 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 105
E200C | M17 |  | M17-E200C | Speaker COR-5518492A shall be move to right side and Cameraa CAM-5514149 shall be moved to Speaker Location as per the markup | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[49db47a63a634ba38dce07b8d4298f24][1]_[2].png","originalImageName":"E200C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[325db84028c141ffbd89c5a70d49283c][1]_[4].png","originalImageName":"企业微信截图_17653312173403"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 29.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | CAM-5514149 and COR-5518492A location updated as per punch comment. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E201C | M17 |  | M17-E201C | Camera and Paga Hirerachy Shall be properly updated in SP3D | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[801730b2f9db4f369be2f99e0de4313a][1]_[2].png","originalImageName":"E201C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7e3126c24d0b488f98cc9aacd59e4fa1][1]_[4].png","originalImageName":"企业微信截图_17653312173403"} | NO | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 29.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Camera transfer to correct hierarchy. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E202C | M17 |  | M17-E202C | Paga speaker shall be relocated as it is blocking by structure | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d8c2c129450248dea8cfa01ae3cd5da5][1]_[2].png","originalImageName":"E202C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[ea5a76e9ef2a482496d7ac3df8a1412e][1]_[4].png","originalImageName":"企业微信截图_17653311527463"} | YES | TELECOM | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 2025/12/10, the model has been updated | 09/12/2025 | 29.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | COR-5518497A relocated. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E203C | M17 |  | M17-E203C | PA-5517079 Access point Enclosure Clashes with Maintenanace Volume | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1f1f93506f034e4b8637580bd82b432c][1]_[2].png","originalImageName":"E203C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[8015e3dd9df4478cbda782871f480a77][1]_[5].png","originalImageName":"企业微信截图_17654354324942"} | NO | TELECOM | ABB/CIMC | 10/12/2025 | CIMC | Pending Petrobras | 2025/12/11, the model has been updated |  |  | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Agreed with ABB/CIMC action. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E204C | M17 |  | M17-E204C | Detector Clashes with Cable tray and Support to be recified for the Detector YST-M17-201-C019,YST-M17-201-C018,YST-M17-201-C019 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[04340e35b1d842108bcd57a9dc9617d5][1]_[2].png","originalImageName":"E204C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[df0b6ed589ad4c2ca802694c6b503c64][1]_[4].png","originalImageName":"E204C"} | NO | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Close | 12/10/2025：3D model updated 2026/01/12: the access for the smoke detector located in raised floor is above floor, it's unneccessary to do maintenance from below side. | 11/01/2026 | 0 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 18.3750000000000 | [U5D6 - 11/JAN/2026] The cilinder volume associated with the instrument is too small. we need the volume to be expanded untill the floor of the level where it is placed, and all clashes to be cleared. Is this accessible? [U5D6 - 13/JAN/2026] Given that detector is in raised floor, noted. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION | [5 empty] | 13/01/2026 | ID: 399
E205C | M17 |  | M17-E205C | Detector YST-M17-201-D026 shall be relocated to provide the access for maintenance | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[07e46f0d8a3d45e9a0e3b7f136bc912c][1]_[2].png","originalImageName":"E205C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a2c51ca6f22d40b38f22d08b62b17029][1]_[4].png","originalImageName":"E205C"} | NO | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Close | 12/10/2025：3D model updated | 09/12/2025 | 31.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | [U5D6 - 11/JAN/2026] Detector is moved as per comment. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E206C | M17 | Level 2 | M17-E206C | Detector YST-M17-202-D001 shall be relocated to provide the access for maintenance | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[037a95e4f02842fd81f0bdcbd7ea0942][1]_[2].png","originalImageName":"E206C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6297802bd0ca49dca38453043e795968][2]_[15].png","originalImageName":"E206C-20251226"} | Re-work | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2025/12/26, The detector maintenance volume clash had been cleared .ABB propose to use lifting table (max 6m ) and handling tools(max 3m) to replace detector. | 25/12/2025 | 15.0000000000000 | KBR has no comments. | 30/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2026: ABB proposal is subjected to PB approval | 01/01/2026 | 8.31319444444671 |  |  |  |  | [U5D6 - 11/JAN/2026] This punch requires operation team agreement. I am consulting them, discussion is still ongoing. | INSTRUMENTATION | [5 empty] | 11/01/2026 | ID: 399
E207C | M17 | Level 2 | M17-E207C | Detector YST-M17-202-D004 shall be relocated to provide the access for maintenance | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[679c9dae17994acf8bc012cc2d1c5218][1]_[2].png","originalImageName":"E207C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[d2f3ee3675d145ad89852c9de0ec92c6][2]_[15].png","originalImageName":"E207C-20251226"} | Re-work | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2025/12/26, The detector maintenance volume clash had been cleared .ABB propose to use lifting table (max 6m ) and handling tools(max 3m) to replace detector. | 25/12/2025 | 15.0000000000000 | KBR has no comments. | 30/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2026: ABB proposal is subject to PB team approval | 01/01/2026 | 8.31250000000000 |  |  |  |  | [U5D6 - 11/JAN/2026] This punch requires operation team agreement. I am consulting them, discussion is still ongoing. | INSTRUMENTATION | [5 empty] | 11/01/2026 | ID: 399
E208C | M17 |  | M17-E208C | Instrument Shall be Moved to the right side as per Markup | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[424421fbe6324fb3ba5328c0bfc7b5c1][1]_[2].png","originalImageName":"E208"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[279c7a90524e43b6aca7c9e294dbfb9f][2]_[21].png","originalImageName":"E208"} | Re-work | INSTRUMENTATION | ABB/CIMC | 16/12/2025 | CIMC | Close | 2025/12/17, this instrument had been moved to right side |  |  | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | [11/JAN/2026] Instrument has been moved as per comment | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E209C | M17 |  | M17-E209C | 220 Socket (SKN-M17-011) shall be Moved to the Left side as per Markup | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[95f85cce42a3434ab2302d21d379e1ca][1]_[2].png","originalImageName":"E209"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bf3a563f92a3408e93530dab1123b2ca][2]_[20].png","originalImageName":"E209"} | Re-work | ELECTRICAL | ABB/CIMC | 16/12/2025 | CIMC | Close | 2025/12/17, this socket had been moved to left side |  |  | 24 Dec: Socket is adjusted. Vendor to ensure accessibility of the socket location. No further comment | 23/12/2025 | Tee | 19-Dec; Transferred to ELECTRICAL. |  | Electrical |  |  |  | Electrical |  | Shichen Li | 26-Dec-2025: 3D model has been updated as per comments. | 26/12/2025 | 15.6166666666686 | [U5D6 - 11/JAN/2026] Socket has been moved as per comment | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E210C | M17 |  | M17-E210C | CIMC hull to check and Modify clash with E-House primary Structure | Li shichen/ ST Ang | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[dcebd9a02e8c4290b7b3292ab97184d4][1]_[2].png","originalImageName":"E210"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6ad0969885a84610b0b2a0cd60c678c8][2]_[24].png","originalImageName":"E210C-20251226"} | YES | STRUCTURAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/24， please Seatrium to coordinate with CIMC hull to solve clash . 2025/12/26, as per battery limt meeting discussion ,CIMC hull already adjusted the structure and clear clash | 23/12/2025 | 20.0000000000000 | [5 empty] | Structure |  |  |  | STRUCTURAL |  | Shichen Li | 28-Dec-2025: 3D model has been updated and clash cleared. Pls PB close-out the punch. | 28/12/2025 | 15.4506944444438 | Noticed. However, all clash shall be automatically captured and solved in the clash management report. It is not necessary to open a punch for this, as already agreed. | Maxwell |  | 07/01/2026 |  | STRUCTURAL | [5 empty] | 14/01/2026 | ID: 539
E211C | M17 |  | M17-E211C | CIMC hull to check and Modify clash with E-House primary Structure | Li shichen/ ST Ang | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[fe3a95c8bec34d98a81c55153d91607e][1]_[2].png","originalImageName":"E211"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a37487140ae34dd1988faeb9d3932473][2]_[23].png","originalImageName":"E211C-20251226"} | YES | STRUCTURAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/24， please Seatrium to coordinate with CIMC hull to solve clash 2025/12/26, as per battery limt meeting discussion ,CIMC hull already adjusted the structure and clear clash | 23/12/2025 | 20.0000000000000 | [5 empty] | Structure |  |  |  | STRUCTURAL |  | Shichen Li | 28-Dec-2025: 3D model has been updated and clash cleared. Pls PB close-out the punch. | 28/12/2025 | 15.4486111111109 | Noted. However, all clash shall be automatically captured and solved in the clash management report. It is not necessary to open a punch for this, as already agreed. | Maxwell |  | 07/01/2026 |  | STRUCTURAL | [5 empty] | 14/01/2026 | ID: 539
E212C | M17 |  | M17-E212C | Smoke Detector YST-M17-301-E001 shall be relocated as the maintanenace volume clashes with cable tray | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4bfc398d898c41768d1f31da7b53819a][1]_[2].png","originalImageName":"E212C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[8980ec0987a84a54bb1b6c88d4f12f53][2]_[12].png","originalImageName":"212"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/17, the model has been updated | 16/12/2025 | 24.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | [U5D6 - 11/JAN/2026] Instrument has been moved to clear clash. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E213C | M17 | Level 3&4 | M17-E213C | Relocate the following Smoke Detector to have Maintenance access YST-M17-301-E006, YST-M17-301-F005 YST-M17-301-F007 YST-M17-301-F008 YST-M17-401-G007 YST-M17-401-H002 YST-M17-401-H004 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[47bd918075994b3490826f86d1c56606][1]_[2].png","originalImageName":"E213C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[dfae468a9d0a4d8badc25c8219af05db][2]_[15].png","originalImageName":"E213C-20251230"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2025/12/30, the maintenance access for commented detector had been cleared ,refer to attached ppt. | 29/12/2025 | 11.0000000000000 | KBR has no comments. | 04/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 05/01/2025: no comment | 05/01/2026 | 4.30763888888760 |  |  |  |  | [U5D6 - 11/JAN/2026] This punch requires operation team agreement. I am consulting them, discussion is still ongoing. | INSTRUMENTATION | [5 empty] | 11/01/2026 | ID: 399
E214C | M17 |  | M17-E214C | According to PB safety guideline criteria ,the quantity of Manual Call point considered for the Battery room 1 and Battery Room 2 to be Evaluated.Seatrium to confirm. | Julimar/Deivission/Daneilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8c1437d741e34fffaf2b948ecb0ffbc5][1]_[2].png","originalImageName":"E214C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2ddbdc80e33243a89b67a6e4eb90c9a1][2]_[28].png","originalImageName":"E214C-20260113"} | YES | INSTRUMENTATION | Seatrium | 30/12/2025 | Seatrium | Pending Petrobras | 2025/12/18, please Seatrium to coordinate and confirm. 2026/01/13， please find advance coply of F&G layout drawing in attachment ,the mentioned MCP had been added in both 3D model and document.(consider RevD layout had not return to us ) 2026/01/13: according to FG cable block diagram , the related cable loop sketch is attached for your easy understanding, there have no loop cable pass through same space twice, please review again 2026/01/13: 1. kindly take note that there have no AFDS loop cable pass through any air lock,please check carefully. 2. the original punch is seatrium to be requested to evaluate the MCP quantity for the common air lock outside. this punch shall be acted by Seatrium first. | 12/01/2026 | 0 |  |  |  | Transferring to Safety |  | Safety |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 26/12/2025: The main reason for rejection is that ABB is required to provide the latest Battery Room 1 and 2 F&G location layout drawings, consistent with the current 3D model, for Seatrium’s review. 13/01/2026: as IMO FSS Code "no loop will pass through a space twice". ABB to check and confirm that current MCP location and loop routing compliance from IMO FSS requriement. 13/01/2026: ABB reply is not accepted. please refer to I-DE-3010.2S-1428-855-AIW-002. and ensure the AFDS loop is not entry the airlock twice. 14/01/2026: no comment. | 13/01/2026 | -0.875000000000000 | [5 empty] | INSTRUMENTATION | [5 empty] | 14/01/2026 | ID: 99
E215C | M17 | Level 4 | M17-E215C | Support for the Junction Box JBIF-1428-001 to be Modelled | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0ce90c2877bc448e9c73f6f453deb967][1]_[2].png","originalImageName":"E215C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[48e5759e03b64917821e77d1f4fefd73][2]_[17].png","originalImageName":"E215C-20251230"} | YES | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/30,Support for the Junction Box JBIF-1428-001 had been Modelled | 29/12/2025 | 11.0000000000000 | KBR has no comments. | 04/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 05/01/2026: no comment | 05/01/2026 | 5.30694444444089 | [U5D6 - 11/JAN/2026] Support has been modeled as per comment | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E216C | M17 |  | M17-E216C | Smoke detector YST-M17-402-G012 shall be relocated as per the Markup | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[f35c7064b78049adbb8ba93cd9e03004][1]_[2].png","originalImageName":"E216C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a38e8596e2144931aef9f533f9b4fcbf][1]_[4].png","originalImageName":"E216C"} | NO | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Close | 12/11/2025：3D model updated | 10/12/2025 | 30.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | [U5D6 - 11/JAN/2026] Instrument has been relocated as per comment | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E217C | M17 | Level 4 | M17-E217C | Maintenance space to be evaluated for the Detector YST-M17-402-H009 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7a48e74aaf014d1eb937fe7de820bd5d][1]_[2].png","originalImageName":"E217C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[cf6ab0f3bde843d89d957f324d6322c9][2]_[18].png","originalImageName":"E217C-20251226"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2025/12/26, The detector maintenance volume clash had been cleared . | 25/12/2025 | 15.0000000000000 | KBR has no comments. | 30/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2026: no comment | 01/01/2026 | 8.31250000000000 |  |  |  |  | [U5D6 - 11/JAN/2026] This punch requires operation team agreement. I am consulting them, discussion is still ongoing. | INSTRUMENTATION | [5 empty] | 11/01/2026 | ID: 399
E218C | M17 | Level 4 | M17-E218C | Instrument Cable tray Shall be moved to provide the Maintenance acess for the Detector YST-M17-402-H010 | Julimar/Deivission/Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[3d13d1c5a2194f63b0f8914a9efdcdba][1]_[2].png","originalImageName":"E218C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[dd5293148e064dc39dd2244dbbc6e498][2]_[16].png","originalImageName":"E218C-20251226"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 25/12/26, The detector maintenance volume clash had been cleared . | 25/12/2025 | 15.0000000000000 | KBR has no comments. | 30/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2025: no comment | 01/01/2026 | 8.30763888888760 |  |  |  |  | [U5D6 - 11/JAN/2026] This punch requires operation team agreement. I am consulting them, discussion is still ongoing. | INSTRUMENTATION | [5 empty] | 11/01/2026 | ID: 399
E219C | M17 |  | M17-E219C | Smoke detector YST-M17-403-G015 shall be relocated as per the Markup | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[fcd0ef36180e4b1983514a2a2bb02b6e][1]_[2].png","originalImageName":"E219C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[44f10a088a6a492e940098d307407846][1]_[4].png","originalImageName":"E219C"} | NO | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Close | 12/11/2025：3D model updated | 10/12/2025 | 30.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | [U5D6 - 11/JAN/2026] Comment has been implemented. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E220C | M17 | All level | M17-E220C | For all Detector relocation , coverage study to be done based on the datasheet | Julimar/Deivission/Danilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[aa0186b6b84f441aba98584ac9aafde9][1]_[2].png","originalImageName":"E220C-M17"} |  |  | NO | INSTRUMENTATION | ABB | 13/01/2026 | ABB | Pending KBR | 2026/01/14, F & G layout drawing had been updated based on current 3D extraction ,refer to attachment . | 13/01/2026 | -1.00000000000000 | [5 empty] | Instrument |  |  |  | INSTRUMENTATION | [10 empty] | INSTRUMENTATION | [5 empty] | 14/01/2026 | ID: 539
E221C | M17 |  | M17-E221C | Evaluate to relocate the support for H2 Detector AST-H2-M17-403-G013 to provide More access for the detector | Julimar/Deivission/Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[7cf0cd2d3c7d49ad81c1353419f3deb6][1]_[2].png","originalImageName":"E221C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b03ce965e63b448e98ee150b099a1732][1]_[4].png","originalImageName":"E221C"} | NO | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Pending Petrobras | 12/11/2025：3D model updated 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 10/12/2025 | 30.0000000000000 | [5 empty] | Instrument |  |  |  | INSTRUMENTATION | [9 empty] | [U5D6 - 11/JAN/2026] This punch requires operation team agreement. I am consulting them, discussion is still ongoing. | INSTRUMENTATION | [5 empty] | 11/01/2026 | ID: 399
E222C | M17 |  | M17-E222C | 1.General Comments: Branch Cable Tray to be Modelled for the fresh air in take Gas detector. 2. Fresh air intake Detector shall be lowered down for Maintenance access, Gas detector Located in front of staircase 3.General Comments:CH4 Detector shall be at top and Co2 Detector at the bottom for all Air intake Gas detector. | Julimar/Deivission/Bruno/Ratha | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[51efcce3532442d5803fce9497a79b8b][1]_[2].png","originalImageName":"E222C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1f558f76d75a4c2ca074ab11f1b92ac9][2]_[21].png","originalImageName":"222c"} | YES | INSTRUMENTATION | ABB/CIMC | 09/12/2025 | CIMC | Close | 12/11/2025：3D model updated 2026/01/08：cable tray and support are modeled as per comment. | 07/01/2026 | 4.00000000000000 | 31 Dec: CIMC to provide tray supports for the added tray. 12 Jan: KBR has no comments. | 11/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 12/01/2026: no comment | 12/01/2026 | 0.349999999998545 | [U5D6 - 13/JAN/2026] As per closeout snapshot , can be closed | U5D6 |  | 12/01/2026 |  | INSTRUMENTATION |  | 12/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 399
E223C | M17 |  | M17-E223C | Evaluate to add Manual Call point at Level-5 .Seatrium/KBR to confirm | Julimar/Danilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[34523ae242664d319f91b5dc09796d7d][1]_[2].png","originalImageName":"E223C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[12a8f007556d4a63ad1d3e20238d33e6][2]_[34].png","originalImageName":"E223C-20260113"} | YES | INSTRUMENTATION | Seatrium | 30/12/2025 | Seatrium | Pending Petrobras | 2025/12/18, please Seatrium to coordinate and confirm. 2026/01/13， please find advance coply of F&G layout drawing in attachment ,the mentioned MCP had been added in both 3D model and document.(consider RevD layout had not return to us ) | 12/01/2026 | -1.00000000000000 |  |  |  | Transferring to Safety |  | Safety |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 26/12/2025: The main reason for rejection is that ABB is required to provide the latest L5 F&G location layout drawings, consistent with the current 3D model, for Seatrium’s review. 13/01/2026: no comment | 13/01/2026 | -1.45833333333576 | [5 empty] | INSTRUMENTATION | [5 empty] | 13/01/2026 | ID: 99
E224C | M17 |  | M17-E224C | General Comment: CH4 Detector shall be at left and Co2 Detector at the Right General Comments: Branch Cable Tray to be Modelled for the fresh air in take Gas detector. | Julimar/Danilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[f24ed769c6214f888a66b308e47e37a5][1]_[2].png","originalImageName":"E224C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[186429a62cae4a3c999ae716a4369a68][2]_[24].png","originalImageName":"224c"} | YES | INSTRUMENTATION | ABB/CIMC | 24/12/2025 | CIMC | Close | 2025/12/25,CH4 detector had been located on left side and CO2 detector located on right side , the branch cable tray had been added ,refer to latest 3D model on 25-Dec-25. 2026/01/04: cable tray and support are updated as per KBR comment. | 03/01/2026 | 6.00000000000000 | 31-Dec: CIMC to provide one more support to IC-M17-S-S-TRAY-05064. 06 Jan: KBR has no comments. | 05/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 07/01/2026: 3D model is updated | 07/01/2026 | 3.64791666666861 | [U5D6 - 11/JAN/2026] Can be closed as per action comment and snapshot. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E225C | M17 |  | M17-E225C | Shift the Junction Box JBIF-5425995-3 as per markup | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8180f6cfeb53491ca55e2c39d6b708d5][1]_[2].png","originalImageName":"E225C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[e7a3b52eb5b047e7a7c36f81d2e6e9f3][1]_[5].png","originalImageName":"225"} | YES | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 12/11/2025：3D model updated | 10/12/2025 | 30.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | [U5D6 - 11/JAN/2026] Can be closed as per closeout snapshot | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E226C | M17 |  | M17-E226C | Change IG541 warning light as hanging type instead of installed on the support | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4dd71ac84a6c405f9a9478ceb1f0ccdb][1]_[2].png","originalImageName":"E226C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6b2d83a39b9c4f309d6a6288b16e95e8][1]_[5].png","originalImageName":"226"} | NO | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 12/11/2025：3D model updated | 10/12/2025 | 30.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | [U5D6 - 11/JAN/2026] Can be closed as per closeout snapshot | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E227C | M17 | Level-1 | M17-E227C | Extend the Support for outdoor IG 541 warning Light YL-5425987 | Julimar/Danilo/Bruno/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[bb1043777b5b41a5bada78774e875771][1]_[2].png","originalImageName":"E227C-m17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c31c81eba92e4967b725c711ceb6dff4][1]_[5].png","originalImageName":"227"} | Re-work | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 12/11/2025：3D model updated 2025/12/25: according to vendor information, this warning light weight is only 3.65kg, there is no vibration issue based on current support length which is confrimed by strength analasis engineer. thanks! | 24/12/2025 | 18.0000000000000 | 19 Dec: CIMC to confirm that a 550 mm extension of this type of steel will pose no issues (e.g., vibration, wobbling). 30 Dec: KBR has no comments. | 29/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2026: noted that ABB evaluation. subject PB approval | 01/01/2026 | 11.3048611111080 | [U5D6 - 13/JAN/2026] As per closeout snapshot , can be closed | U5D6 |  | 12/01/2026 | [U5D6 - 11/JAN/2026] This needs operation team agreement. I am discussing with them. Discussion ongoing. | INSTRUMENTATION |  | 12/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 399
E228C | M17 |  | M17-E228C | Pnuematic Air Horn to be shown in Safety Plan drawing | Julimar/Danilo | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c7c421a981994121b53405b76baa7ed8][1]_[2].png","originalImageName":"E228C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bf58aa3a25714308b7c1e75eb85fd7ed][2]_[16].png","originalImageName":"M17 E228C"} | NO | SAFETY | ABB/CIMC | 24/12/2025 | CIMC | Close | 25/12/25： The air horn has been update in safety plan, please refer to the new version drawing. 2026/01/04，offical safety plan had been submited in pims . | 24/12/2025 | 18.0000000000000 | 30 Dec 2025: Rev C of M17 safety plan (I-DE-3010.2S-1428-947-AIW-001) not officially issued. ABB to officially issue safety plan to close out comment. 5 Jan 2026: Rev C of M17 safety plan (I-DE-3010.2S-1428-947-AIW-001) has been officially issued. Pneumatic air horn has been included. Comment can be closed. | 04/01/2026 | Indra/ Hong | 05-Jan: Transferred to SAFETY |  | Safety |  | 04/01/2026 | 7.62500000000000 | Safety |  | Tsen Tze Jia | 12 Jan: PB to refer to latest revision of I-DE-3010.2S-1428-947-AIW-001 and close this punch. | 12/01/2026 | 0.375000000000000 | [U5D6 - 13/JAN/2026] Closed as per snapshot. | U5D6 |  | 12/01/2026 |  | INSTRUMENTATION |  | 12/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 399
E229C | M17 | All level | M17-E229C | Door Limit switch Junction Box JBIF-5425981-3,JBIF-5425981-4,JBIF-5425982-3,JBIF-0402001,JBIF-0403002,JBIF-5425966-2,JBIF-5425966-3 shall be lowered down | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0062b27de12d4ddd9f40489c1bc634da][1]_[2].png","originalImageName":"E229C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[47a39f2e7ff94abc8f1c4922f967050a][2]_[15].png","originalImageName":"229c"} | YES | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2026/01/04: punched door limit switch Jb height are lowered properly, please review as per latest model. 2026/01/06: ABB/CIMC confirmed that there haven't any mandatory requirement about the door limit switch Junction box elevation during DR90. The prerequisite for elevation modification is to ensure that the new location will not affect other item visibility, accessibility,operability. Meanwhile, make sure that the Jucntion box maintenance also can be done without any obstruction. current design can meet above requirement, if further lowered, maybe it will block signage or something elso. please let PB operation team to confirm the acceptance. | 05/01/2026 | 4.00000000000000 | 06-Jan: CIMC to advise if the elevation (>2m) is acceptable. JB tags are as follows: JBIF-0402001, JBIF-5425981-4, JBIF-0403002, JBIF-5425966-2, and JBIF-5425966-3. The punch was to lower the listed JB. 07-Jan: CIMC provided their action comments in response to the Jan-06 KBR response. CIMC stated that as long as the JBs are obstruction-free and accessible, it is acceptable. The average elevation of the mentioned JBs is 2.4m. SEA to advise and confirm acceptance. | 06/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 07/01/2026: ABB highlighted difficulty for further lowering down. Subject to PB approval. | 07/01/2026 | 2.37500000000000 |  |  |  |  | [U5D6 - 11/JAN/2026] This needs operation team agreement. I am discussing with them. Discussion ongoing. | INSTRUMENTATION | [5 empty] | 11/01/2026 | ID: 399
E230C | M17 |  | M17-E230C | Support Length for Lighting Fixture LEM-355-05-M17-005 shall be reduced to have Maintainenace acess for Warning Light | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e66972e883814bfe9cab5c7e1056cc92][1]_[2].png","originalImageName":"E230C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[95ca48ae40ee4e949a7f3ed7b5673f23][1]_[5].png","originalImageName":"E230C"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 12/11/2025：3D model updated | 10/12/2025 | 31.0000000000000 | 18 Dec: lighting support is shortened to ensure warning light accessibility, no further comment. Operation team to confirm acceptance. | 17/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated, PB operation team confirm to close the punch. | 24/12/2025 | 17.3388888888876 | 11/01/26-UR7U-Noted. Support adjusted. | Welton |  | 10/01/2026 | 09.01.2025-RTWG- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E231C | M17 |  | M17-E231C | Double Door vendor Supplied Cable tray for Door Limit Switch to be Modelled | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8b8a63f487b14be68f7b4694012e3bc6][1]_[2].png","originalImageName":"E231C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[f72bd7c5dc40455799cafc654d7baa2d][2]_[21].png","originalImageName":"E231C"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 12/19/2025：3D model updated | 18/12/2025 | 22.0000000000000 | KBR has no comments. | 23/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 26/12/2026: no comment | 26/12/2025 | 15.4027777777810 | [U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. I'm Assuming that is a tray in the door itself, as per ABB/KBR/SEA confirmation. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E232C | M17 |  | M17-E232C | Cable Tray for Door Limit Switch ZSL-5425982-3 is missing | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e86f6b5cbbb2435c935118b7eb465755][1]_[2].png","originalImageName":"E232C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[f9f8781af78748119e6163bda147859d][2]_[27].png","originalImageName":"232c"} | YES | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/20,this missing cable tray had been added 2026/01/04: cable tray location and support are updated as per KBR comment | 03/01/2026 | 6.00000000000000 | 30-Dec: CIMC should improve the tray support, as it currently has only one point of support. 06-Jan: KBR has no comments. | 05/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 07/01/2025: 3D model updated | 07/01/2026 | 3.64652777778247 | [U5D6 - 11/JAN/2026] As per closeout snapshot, tray has been modeled. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E233C | M17 |  | M17-E233C | Change the Location of Junction Box JBIF-5425999-2 as per markup | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[217da1eae0e04c899a85822f5fa01dc1][1]_[2].png","originalImageName":"E233C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[e04528442086408ea5a2f6505ea9e068][2]_[26].png","originalImageName":"233C"} | YES | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 12/11/2025：3D model updated 2026/01/01: JBIF-5425999-2 location has been changed as per comment and support is modeled | 31/12/2025 | 9.00000000000000 | Dec 19: CIMC to model the JB support at the new location. Jan 2: KBR has no comments. | 01/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 05/01/2026: no comment | 05/01/2026 | 5.30277777777519 | [U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E234C | M17 | Level-3 | M17-E234C | Change the Location of Junction Box JBIF-5425999-3 as per markup | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e48e912c7a5b423ea2ff74d15bf76516][1]_[2].png","originalImageName":"E234C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b661edb14a184ff3ab6cc5c03dc12974][2]_[25].png","originalImageName":"234c"} | Re-work | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 12/11/2025：3D model updated 2026/01/01: JBIF-5425999-3 location has been changed as per comment and support is modeled | 31/12/2025 | 9.00000000000000 | 19 Dec: CIMC to model the JB support at the new location. 02 Jan: KBR has no comments. | 01/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 05/01/2026: no comment | 05/01/2026 | 5.30069444444234 | [U5D6 - 11/JAN/2026] JB is laying down, Not ideal, but in principle ok. I'll talk to operation team, if needed, i'll reopen. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E235C | M13R |  | M13R-E235C | M13R Warning Lighting YL-5425952B to be relocated as per Markup | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[89aac2a23e214d70a196dc3de205faf2][1]_[2].png","originalImageName":"E235C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[79ec556a36c143e48e22757270bf48ce][1]_[7].png","originalImageName":"E235C"} | YES | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2024/12/12：The warning light YL-5425952B has been reinstalled as marked | 11/12/2025 | 29.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 |  | U5D6 |  | 10/01/2026 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E236C | M13R |  | M13R-E236C | Double Door vendor Supplied Cable tray for Door Limit Switch to be Modelled | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[89007cd768754fe5b4c313a7dd756b26][1]_[2].png","originalImageName":"E236C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[5ac712a621534f0a8afb9f32e477e5f6][2]_[15].png","originalImageName":"M13-E236C"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 12/19/2025： Added the missing cable tray. | 18/12/2025 | 22.0000000000000 | KBR has no comments. | 29/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2025: no comment | 01/01/2026 | 9.30416666666861 | U5D6 - 11/JAN/2026] As per closeout snapshot, PB understands ABB/SEA/KBR has confirmed a cable tray will be inbuilt in the door. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E237C | M13R |  | M13R-E237C | 1.General Comment: CH4 Detector shall be at left and Co2 Detector at the Right For Level 1 & Level2 2.General Comment: CH4 Detector shall be at Top and Co2 Detector at the Bottom for Level-3 3.General Comment: Branch Cable Tray to be Modelled for the fresh air in take Gas detector. | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[3475abc541db428b87f5fa14647f91f4][1]_[2].png","originalImageName":"E237C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9b031f7deca64cdc9266742538eacee1][2]_[11].png","originalImageName":"E237C"} | YES | INSTRUMENTATION | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/12：The detector and cable tray have been modeled as required | 11/12/2025 | 29.0000000000000 | KBR has no comments. | 30/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2026: no comment | 01/01/2026 | 9.30208333333576 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E238C | M13R |  | M13R-E238C | Maintenance access for Air In take Gas detector to be Evaluated for Level-1,Level-2 &Level-3 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[90a6332729084e14906694a346a8d6d4][1]_[2].png","originalImageName":"E238C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[499b1329d4f949d4ba2caea8af6a32cb][2]_[16].png","originalImageName":"E238C-20251222"} | YES | INSTRUMENTATION | ABB | 30/12/2025 | ABB | Pending Petrobras | 2025/12/22, consider the height requirement and escape route limit ,ABB propose to use lifting cart for maintenance of detectors. | 21/12/2025 | 19.0000000000000 | KBR has no comments and finds the proposal acceptable. SEA to advise. | 30/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2026: no comment | 01/01/2026 | 8.30138888888905 |  |  |  |  | [U5D6 - 11/JAN/2026] This needs operation team agreement. I am discussing with them. Discussion ongoing. | INSTRUMENTATION | [5 empty] | 11/01/2026 | ID: 399
E239C | M13R |  | M13R-E239C | Detector Sampling direction shall be rotated to 180 Degree | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[f8885419f7a948bdbc9ade79dda832c7][1]_[2].png","originalImageName":"E239C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[34e6e0832c724328a47041400634c222][1]_[6].png","originalImageName":"E239C"} | YES | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated |  |  | KBR has no comments. |  |  |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E240C | M13R |  | M13R-E240C | Relocate the Smoke Detector to have Maintenance access as per Markup YST-M13-103-A003 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[ccead3aafe73485593e99c5105da7fef][1]_[2].png","originalImageName":"E240C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[65459e84b7444a86a05ee6c8ff91be17][1]_[7].png","originalImageName":"E240C"} | YES | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated |  |  | KBR has no comments. |  |  |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E241C | M13R |  | M13R-E241C | Evaulate the Smoke Detector to relocate to have proper maintenance Access YST-M13-103-B002 YST-M13-103-A004 YST-M13-203-C002 YST-M13-203-C005 YST-M13-203-C006 YST-M13-203-C013 (Located below the Panel, to be moved away from the panel) YST-M13-203-D003 YST-M13-203-D010 (Located below the Panel, to be moved away from the panel) YST-M13-203-D012 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[3445feb693b341dbbcb715314fb81919][1]_[2].png","originalImageName":"E241C-M13R"} | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot2][32]_[62efb870e4b5472b8b34a7d5158693cc][1]_[8].png","originalImageName":"E241C"} |  | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2025/12/15：The positions of all the smoke detectors mentioned above have been modified | 14/12/2025 | 26.0000000000000 | KBR has no comments. | 04/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 05/01/2026: no comment | 05/01/2026 | 4.29930555555620 |  |  |  |  | [U5D6 - 11/JAN/2026] This needs operation team agreement. I am discussing with them. Discussion ongoing. | INSTRUMENTATION | [5 empty] | 11/01/2026 | ID: 399
E242C | M13R |  | M13R-E242C | Relocate the Smoke Detector as per Markup YST-M13-103-A014 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c215feb9a75d4bd3ba55c586050a679e][1]_[2].png","originalImageName":"E242C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[21755faff4034800a8786dc795c70855][1]_[7].png","originalImageName":"E242C"} | YES | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated | 10/12/2025 | 30.0000000000000 | KBR has no comments. |  |  |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E243C | M13R |  | M13R-E243C | Relocate the Smoke Detector as per Markup YST-M13-103-A015 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[01f41ca0dbb0448097a8a379a38064f3][1]_[2].png","originalImageName":"E243C-M13R","serverRelativeUrl":null,"id":null,"serverUrl":null,"thumbnailRenderer":null} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[435840e40c4b49d387c545fcd6eafd87][1]_[7].png","originalImageName":"E243C","serverRelativeUrl":null,"id":null,"serverUrl":null,"thumbnailRenderer":null} | YES | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated | 10/12/2025 | 30.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E244C | M13R | Level 1 | M13R-E244C | Relocate the Smoke Detector as per Markup YST-M13-103-B013 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[19aaefe9bd1f4412b8a38beff7af3b73][1]_[2].png","originalImageName":"E244C-M13R","serverRelativeUrl":null,"id":null,"serverUrl":null,"thumbnailRenderer":null} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b8e29ea89c184e06be1fa3333528318c][2]_[31].png","originalImageName":"244c"} | YES | INSTRUMENTATION | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated 2026/01/01: YST-M13-103-B013 location has been changed as per comment | 31/12/2025 | 9.00000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: ABB to check if the smoke detector has been shifted as the punch list. what I see in the evidence picture is that detector still at same position. 1/1/2025: no comment | 01/01/2026 | 9.29930555555620 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E245C | M13R |  | M13R-E245C | Relocate the Fie Damper Tubing to have proper access for H2 Detectors AST-H2-M13-202-C007 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[daccc72d19cf43f583ae8afb8f41c78f][1]_[2].png","originalImageName":"E245C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2c4f5b53f70f4d3086c5bd29e1064280][2]_[15].png","originalImageName":"E245"} | YES | PIPING | ABB/CIMC | 25/12/2025 | CIMC | Close | 2025/12/23： The Fie Damper Tubing has been rearranged to have proper access for H2 Detectors AST-H2-M13-202-C007. |  |  | KBR has no comments. | 29/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2026: no comment | 01/01/2026 | 9.29513888889051 | U5D6 - 11/JAN/2026] Tubing has been relocated away from detector. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E246C | M13R |  | M13R-E246C | 1.Relocate the Smoke detector YST-M13-202-D009, 2.Sampling direction for the AST-H2-M13-202-C009 & AST-H2-M13-202-D008 shall be rotated to 90 Degree | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1d12e09d2bc0447685d2cb1bf6f77158][1]_[2].png","originalImageName":"E246-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[3965bef509134a79b2c2c343323e8fac][1]_[7].png","originalImageName":"E246C"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/13：The smoke detector and hydrogen detector have been modified as required | 12/12/2025 | 28.0000000000000 | KBR has no comments. | 29/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 1/1/2026: no comment | 01/01/2026 | 9.29374999999709 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E247C | M13R | Level 2 | M13R-E247C | Support for the Junction Box JBIF-1424-001 to be Modelled | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a5dbc59fd1a549faa57e92cc15771821][1]_[2].png","originalImageName":"E247C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[f28c610e6eba4ef9bc2588b8f4b77859][2]_[15].png","originalImageName":"247C"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/29: JBIF-1424-001 Support is model as per vendor drawing | 28/12/2025 | 12.0000000000000 | KBR has no comments. | 04/01/2026 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 05/01/2026: no comment | 05/01/2026 | 5.29791666667006 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E248C | M13R |  | M13R-E248C | Relocate the Smoke Detector as per Markup YST-M13-203-D013 | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[55cb128cbab040aeb87028edcd03cf93][1]_[2].png","originalImageName":"E248C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bad1aa83836144bf864ea99d206cd889][1]_[7].png","originalImageName":"E248C"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/12：The smoke detector YST-M13-203-D013 has been reinstalled according to the markings | 11/12/2025 | 29.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E249C | M13R |  | M13R-E249C | Evaluate to add Manual Call point at Level-3 .Seatrium/KBR to confirm | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[355043b0bdc64d4f8f1848f338c48f5a][1]_[2].png","originalImageName":"E249C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[16dc4bb5667f46e191b945a5f1877499][2]_[23].png","originalImageName":"E249C-20260113"} | YES | INSTRUMENTATION | Seatrium | 30/12/2025 | Seatrium | Pending Petrobras | 2025/12/18, please Seatrium to coordinate and confirm. 2026/01/13， please find advance coply of F&G layout drawing in attachment ,the mentioned MCP had been added in both 3D model and document.(consider RevD layout had not return to us ) | 12/01/2026 | -1.00000000000000 |  |  |  | Transferring to Safety |  | Safety |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 26/12/2025: The main reason for rejection is that ABB is required to provide the latest L3 F&G location layout drawings, consistent with the current 3D model, for Seatrium’s review. 13/01/2026: no comment | 13/01/2026 | -1.45555555554893 | [5 empty] | INSTRUMENTATION | [5 empty] | 13/01/2026 | ID: 99
E250C | M13R |  | M13R-E250C | 1.Cable tray support to be slightly moved /deleted to have proper access for Cable pulling space | Ratha | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c7cbaa4e399848bd8123c7d1956d1f72][2]_[14].png","originalImageName":"E250C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[68e3fdb5953d47b1843dd348efb6895e][2]_[32].png","originalImageName":"250C"} | YES | ELECTRICAL | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated 2025/12/26: The useless support(snapshot top marked one) is deleted and another support(snapshot bottom marked one) is shifted slightly to aft side to enlarge the cable pulling space as per discussion during DR90 | 25/12/2025 | 16.0000000000000 | Vendor to provide clear close-out model snap showing updates done in model, complete with clear descriptions of actions taken by vendor to resolve the punch. 2 Jan: Noted on the update. No further comment | 01/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: KBR comments need to be implemented. 6-Jan-2026: 3D Model has been updated as per punch comments. | 06/01/2026 | 5.57152777777810 | Support Shifted | Julius Orzales |  | 12/01/2026 |  | ELECTRICAL |  | 11/01/2026 | -1.16736111111095 |  |  | 12/01/2026 | ID: 484
E251C | M13R |  | M13R-E251C | Cable distribution from MCT to the vertical ladder to level-2 and the Harizontal at Level-1, interference with Support and other cable tray shall be Demonstrated. | Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[9681bf46aa264317bfac3db35b96ef81][2]_[26].png","originalImageName":"E251C"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b9e0b10dea6c430f87f7175251528c81][2]_[35].png","originalImageName":"251c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/20 the model has been updated 2026/01/01: cable simulation model are added to show the cable bending as pe KBR advice | 31/12/2025 | 10.0000000000000 | 24 Dec: Vendor to clearly descripted and demonstrate the cable routing on this location. Not able to identify the changes in closeout snapshot 2 Jan: Cable stimulation shown. Vendor to ensure sufficient support and bending radius for the cables in this cable trays transition. No further comment | 23/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL | Vendor to ensure sufficient support and bending radius for the cables in this cable trays transition | Shichen Li | 25-Dec-2025: KBR comment need to be considered and implemented. 6-Jan-2026: 3D Model has been updated as per punch comments. | 06/01/2026 | 4.40208333333430 | 11/01/26-UR7U-Noted. | Welton |  | 10/01/2026 | 09.01.26-NA53- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E252C | M13R |  | M13R-E252C | General Comments:Lighting Cable tray to use Standard accessories to avoid additional level of cable trays | Tee | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[401f14bbfdfd422fb113f505eddee4fe][1]_[2].png","originalImageName":"E252C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[5091383fc76a4c3faa543dc44d3353e8][2]_[15].png","originalImageName":"252c"} | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending KBR | 2026/01/07：standard Tee part are applied for lighting branch cable tray 2026/01/13: cable tray continuity is not the mandatory requirement, cable branch from different elevation cable tray without proper fitting is also acceptable. | 12/01/2026 | -1.00000000000000 | 8 Jan: missing branch connection for EC-M13R-L-N-TRAY-02529 at level 2, please implement the same concept to the lighting tray on the roof 13Jan: Level 2 lighting cable channel connected with proper fitting. Please implement the same concept to the lighting cable channel on the roof top. Observed there are different layer of cable channel. | 12/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 13-Jan-2026: KBR comments need to be implemented. | 13/01/2026 | -1.36805555555475 | [5 empty] | ELECTRICAL | [5 empty] | 13/01/2026 | ID: 839
E253C | M13R |  | M13R-E253C | Instrument Cable tray shall be slightly extended | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[f41d49caa6764992b3086ba333b7b039][1]_[2].png","originalImageName":"E253C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[8674f4a532d84c7eb998d0c8a2f05bd7][1]_[7].png","originalImageName":"E253C"} | NO | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/12：The instrument cable tray has been lengthened | 11/12/2025 | 29.0000000000000 | KBR has no comments. | 18/12/2025 | Roberto |  |  | Instrument |  |  |  | INSTRUMENTATION |  | Guanyu Zhu | 24/12/2025: no comment | 24/12/2025 | 17.3750000000000 | U5D6 - 11/JAN/2026] As per closeout snapshot, can be closed. | U5D6 |  | 10/01/2026 |  | INSTRUMENTATION |  | 10/01/2026 | -1.00000000000000 |  |  | 11/01/2026 | ID: 399
E254C | M13R |  | M13R-E254C | Add Cable tray bend to Align with the MCT | Julimar/Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[f20e16b9ccc3440d96d40978c28df489][1]_[2].png","originalImageName":"E254C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bf65e9ecfff54bd891e6f25449ad0a06][1]_[7].png","originalImageName":"E254C"} | NO | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Rejected | 2025/12/12：The cable tray has been aligned with the MCT 2025/12/26: the vertical distance between MCT and cable ladder bottom is 354mm, according to IEC 61892-6 chapter 14.10, cable support gap is recommented within 400mm , MCT block can be considered as a special support for cable, hence, from CIMC view point,it's unneccesary to add support for the mentioned vertical cable, please confirm again. | 25/12/2025 | 14.0000000000000 | 24 Dec: Vendor to check and study adequate cables support from horizontal cable tray to the MCT (missing support for vertical cable routing) 9 Jan: Recommendation is to not consider MCT as a primary option for cable support. Trays and suitable tray support to be employed by vendor as primary means to support cable. Design shall maintain adequate cable support. Suitable tray fitting to be used as much as possible as a general recommendation. | 08/01/2026 | Tee | 19-Dec: Transferred to ELECTRICAL. |  | Electrical |  |  |  | Electrical |  | Shichen Li | 26-Dec-2025: KBR comment need to be studied and implemented. 10-Jan-2026: KBR comment need to be studied and implemented. | 10/01/2026 | -1.47916666666424 | [5 empty] | INSTRUMENTATION | [5 empty] | 10/01/2026 | ID: 579
E255C | M13R |  | M13R-E255C | General Comments : Cable tray connection accessories to be added for the Straight "T "connection | Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4062a35c089242b18e39b02718632195][1]_[2].png","originalImageName":"E255C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bde75d4c2a34480d91c6bc891580d664][2]_[15].png","originalImageName":"255"} | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/25: standard Tee part are added for the mentioned arae. | 24/12/2025 | 14.0000000000000 | 2 Jan: Tee fitting added for cable trays connection. No further comment | 01/01/2026 |  |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | 2.40208333333430 | 09/01/26-UR7U- Noted.. Tee connection added. Cable tray connection accessories to be used for all connections. | Welton |  | 08/01/2026 |  | ELECTRICAL |  | 08/01/2026 | -1.00000000000000 |  |  | 09/01/2026 | ID: 398
E256C | M13R |  | M13R-E256C | Vertical Cable tray bend to provide for proper cable bending of the cable from MCT to tray | Tee | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[fcff9970174d445c869ddcb113a9f951][1]_[2].png","originalImageName":"E256C-M137"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[038deba1a32f4c0980c2ef39360bf148][2]_[32].png","originalImageName":"256"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Rejected | 2025/12/12：The cable has been displayed. 2525/12/25: additional cable tray bending part is not recommented by construction team due to feild complexity. according to cable schedule and cable vendor information, the cables OD and min. bending radius is 29.4mm and 176.4mm(6D), the current cable simulation model is 35mm and 218mm,it has ensured enough bending space.meanwhile, short piece stright cable is also ensured at front and rear side of MCT block, please refer to the new snapshot | 24/12/2025 | 15.0000000000000 | 18 Dec: No tray fitting/riser was added in model to consider punch close-out. Vendor to provide the required model based on punch description. Cable model provided by vendor does not satisfy punch close-out. Cables exiting the MCT must maintain a straight section of adequate length before any bend to prevent stress and ensure compliance with installation standards. 9 Jan: Please refer to the attached image. The areas with inadequate cable support are highlighted in circles. We propose relocating the MCT to align with the level of the T‑branch so that the cable can run straight. After that, review and optimize the routing to and from PCC‑BT‑5147001B to ensure proper bending radius. Cable tray design should also take constructability and long‑term cable sustainability into consideration. | 08/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: KBR comment need to be considered and implemented. 10-Jan-2026: KBR comment need to be considered and implemented. | 10/01/2026 | -1.48333333332994 | [5 empty] | ELECTRICAL | [5 empty] | 10/01/2026 | ID: 579
E257C | M13R |  | M13R-E257C | Vertical Cable tray shall be moved to the left side for Cable connection to the Battery | Julimar/Deivission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a0cccbf7c73543c5ab82ea6a87e057fb][1]_[2].png","originalImageName":"E257C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[913e7398a17d460ebf48c355ae35df3c][2]_[11].png","originalImageName":"E257C"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/13：The cable tray has been moved | 12/12/2025 | 29.0000000000000 | 18 Dec: Vertical cable tray moved to left for better cable connection to the battery. No further comment | 17/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated as per comments. | 24/12/2025 | 17.3583333333299 | 11/01/26-UR7U-Noted. The cable tray has been moved. | Welton |  | 10/01/2026 | 09.01.2026-NA53-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E258C | M13R |  | M13R-E258C | PDD-5517002 Hireachy shall be in Data Folder,Camera and Paga Hirerachy Shall be properly updated in SP3D | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[f373853510df4e7bbf90aafcc0ac24f8][1]_[2].png","originalImageName":"E258C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[49921a91a1bf44e8a9e95afaeed05ef3][2]_[10].png","originalImageName":"E258C"} | YES | TELECOM | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/12 the model has been updated |  |  | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | PDD-5517003 was transferred to DATA hierarchy | 07/01/2026 | 4.67777777777519 | Moved to DATA hierarchy | Julius Orzales |  | 12/01/2026 |  | TELECOM |  | 12/01/2026 | -0.677777777775191 |  |  | 12/01/2026 | ID: 484
E259C | M13R |  | M13R-E259C | Make the support Stronger than Current support for the camera CAM-5514084 & CAM-5514085to the right side as it is close temporary Scaploading | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4ce20246b782489c94e960c4ae2544cd][1]_[2].png","originalImageName":"E259C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[f62174a94dd143ea9fcd3b2d80d0c07f][1]_[8].png","originalImageName":"E259C"} | YES | TELECOM | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2025/12/15:The support specifications and positions of the cameras CAM-55140844 and CAM-5514085 have been modified | 14/12/2025 | 24.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/09: Camera supports have been modified as per punch action. | 09/01/2026 | -1.40763888888614 | [5 empty] | TELECOM | [5 empty] | 09/01/2026 | ID: 105
E260C | M13R |  | M13R-E260C | General comment: ALL indoor PAGA speaker support shall be modified to avoid clash with Cable Entry Location | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0da3e7c8f0fd4083a397f2d099f41019][1]_[2].png","originalImageName":"E260C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7ba5dff0f6cc42c585327a0e8481fdbd][1]_[5].png","originalImageName":"E260C"} | YES | TELECOM | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2025/12/13：All indoor camera supports have been modified 2026/01/12: punch description is changed to PAGA speaker, please review again | 11/01/2026 | 0 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | 2026/01/09: ABB/CIMC to confirm which equipment supports were modified for this punch, indoor cameras or speakers? Closing snapshot is for speaker. 2026/01/13: Speaker support was updated with L bracket at top without protruding at the rear. | 13/01/2026 | -1.39236111110949 | [5 empty] | TELECOM | [5 empty] | 13/01/2026 | ID: 98
E261C | M13R |  | M13R-E261C | Branch Cable cable tray and support to be Modelled for the Speaker COR-5518337B | Weng Kit | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[11099c0706d64197b428e1c3cbe97554][1]_[2].png","originalImageName":"E261C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[713f2964520247b6a6b00773fc658092][2]_[10].png","originalImageName":"E261C"} | YES | TELECOM | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/12 the model has been updated |  |  | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Field tray to the speaker was modelled. | 07/01/2026 | 5.65763888888614 | Cable tray branch and support added | Julius Orzales |  | 13/01/2026 |  | TELECOM |  | 13/01/2026 | -1.65763888888614 |  |  | 13/01/2026 | ID: 484
E262C | M13R |  | M13R-E262C | The Mounting height of outdoor Speaker COR-5518336B to be in line Typical Installation | Manohar | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[f88ef5ba7bad45aca8fcfc2e66a73287][1]_[2].png","originalImageName":"E262C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[fc4e2a43beba4acca991e99593d82f86][2]_[10].png","originalImageName":"E262C"} | YES | TELECOM | ABB/CIMC | 10/12/2025 | CIMC | Pending Petrobras | 2025/12/11, the model has been updated |  |  | Noted as per ABB/CIMC Update | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | 2.5m from deck to speaker bracket, align with typical. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E263C | M13R |  | M13R-E263C | Vibration Support with clamp to be added for Standalone Support for BLE-5511264 | Allan | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[45160ec8b6d84e3ca1dc25dd098fda07][1]_[2].png","originalImageName":"E263C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[d549c08b19984a8f88c5cbe8d48e259a][2]_[22].png","originalImageName":"264"} | YES | TELECOM | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated 2026/01/08: the tag No has been rectified as BLE-5511264, close out snapshot is also updated. | 07/01/2026 | 4.00000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/08: Please check correct tag number for punched item, BLE-5511264 or BLE-5511265? 2026/01/09: Noted on ABB/CIMC update. | 09/01/2026 | 2.78402777777228 | BLE-5511264 vibration support was added | Julius Orzales |  | 11/01/2026 | BLE-5511264 vibration support was added | TELECOM |  | 11/01/2026 | -0.166666666664241 |  |  | 12/01/2026 | ID: 484
E264C | M13R |  | M13R-E264C | Shift theTelephone system as per the markup | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[22960632bd694c518bf9b629d3cf4d0e][1]_[2].png","originalImageName":"E264C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b9c443f48e6f41d1861b2fc5517e7e24][2]_[10].png","originalImageName":"E264C"} | YES | TELECOM | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated |  |  | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Agreed with ABB/CIMC action. | 07/01/2026 | 5.65972222221899 | Shifted | Julius Orzales |  | 13/01/2026 |  | TELECOM |  | 13/01/2026 | -1.65972222221899 |  |  | 13/01/2026 | ID: 484
E265C | M13R |  | M13R-E265C | Support for Leaky Cable support to be provided for every one meter | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c7040728c9bd4deba95feaec0a44f489][1]_[2].png","originalImageName":"E265C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[4ef4e44c9d444e949604b80b834578ee][2]_[10].png","originalImageName":"E265C"} | YES | TELECOM | ABB/CIMC | 10/12/2025 | CIMC | Rejected | 2025/12/11, the model has been updated | 10/12/2025 | 28.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/09: Closing image does not show leaky cable support for every 1meter as per punch comment. ABB/CIMC to confirm the support has been provided and show in the closing snapshot. | 09/01/2026 | -1.46458333333430 | [5 empty] | TELECOM | [5 empty] | 09/01/2026 | ID: 539
E266C | M13R |  | M13R-E266C | Shift Antenna to the Left to reduce the cable bending | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[3ee3a579df9144cc94924b5b463af2d6][1]_[2].jpg","originalImageName":"E266C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[25047bf4e8e7473ab445d56e27dfce60][2]_[10].png","originalImageName":"E266C"} | YES | TELECOM | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated | 09/12/2025 | 34.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Nur Haedzerin | 2026/01/08: Antenna has been shifted as per punch. | 08/01/2026 | 4.91527777777810 | Shifted | Julius Orzales |  | 13/01/2026 |  | TELECOM |  | 13/01/2026 | -0.668055555557657 |  |  | 13/01/2026 | ID: 484
E267C | M13R |  | M13R-E267C | Vertical Support for the camera CAM-5514075 is missing and to be Modelled | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[198ef89514de459f95ea2433840cabd1][1]_[2].jpg","originalImageName":"E267C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[842a3a1abf8140dbba11c2855e1b2409][1]_[7].png","originalImageName":"E267C"} | NO | TELECOM | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/12：The support for the camera CAM-5514075 has been modeled | 11/12/2025 | 31.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Agreed with ABB/CIMC action. | 07/01/2026 | 4.69097222221899 |  | Julius Orzales |  | 12/01/2026 |  | TELECOM |  | 12/01/2026 | -0.690972222218988 |  |  | 12/01/2026 | ID: 484
E268C | M13R |  | M13R-E268C | Additional Horizontal support from the nearby support to be added to avoid vibration of the Camera CAM-5514083 & CAM-5514081 | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4fc94555b2c04fbf96d74cf1cbd0ea62][1]_[2].png","originalImageName":"E268C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[4a479a67a0254f0e941c21895d65ab6d][1]_[5].png","originalImageName":"E268C"} | NO | TELECOM | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2025/12/13：The support for the cameras CAM-5514083 and CAM-5514081 has been modified | 12/12/2025 | 26.0000000000000 | Agreed with ABB/CIMC action. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Agreed with ABB/CIMC action. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 98
E269C | M13R |  | M13R-E269C | Location of the Camera at Roof top to be Evaluated CAM-5514157 and Camera Type to be confirmed by Seatfrium/KBR | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6aa504d9b8ac428587fc9aba10339571][1]_[2].png","originalImageName":"E269-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[8264555fec7c4ed2968ae803439215ad][2]_[26].png","originalImageName":"269"} | YES | TELECOM | Seatrium | 30/12/2025 | Seatrium | Pending KBR | 2025/12/29: camera location is shifted as per comment. please SEA/KBR to confirm the camera type 2026/01/08: close out snapshot is added, please review again | 07/01/2026 | 0 | Close out snapshot missing here. | 07/01/2026 | Manogar |  |  | TELECOM |  |  |  | TELECOM |  | Chew Weng Kit | Close out snapshot missing here. Camera type remains unchanged. | 07/01/2026 | 0 | [5 empty] | TELECOM | [5 empty] | 08/01/2026 | ID: 839
E270C | M13R |  | M13R-E270C | Penetration Opening for PRD opening Shall be Closed with Structure | Devission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[9fbedbad6b3d4033b3f7e5537fffaefb][1]_[2].png","originalImageName":"E270C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[5982d47d6b35446a8bf2dea65a8bf64d][2]_[33].png","originalImageName":"E270"} | NO | STRUCTURAL | ABB/CIMC | 16/12/2025 | CIMC | Pending KBR | 2025/12/17：PRD opening has updated the model 2026/01/08：Please refer to the attached latest Revision B drawing for the updated position of the PRD penetration opening. | 07/01/2026 | 0 | KBR STR (22 Dec 2025): Noted as per ABB/CIMC updates | 22/12/2025 | Bobby Pramayudha |  |  | Structure |  |  |  | STRUCTURAL |  | Caryn Tan | 24-Dec-25: Model updated. | 23/12/2025 | 15.0000000000000 | The structural drawing I-DE-3010.2S-1424-140-AIW-010_A was not updated to reflect the 3D model alteration. Since the structural drawing is the document to be used by construction and it is not revised, the punch cannot be closed. | Maxwell |  | 07/01/2026 |  | STRUCTURAL | [5 empty] | 08/01/2026 | ID: 841
E271C | M13R |  | M13R-E271C | Cable tray Cover to be Modelled For EIT- External areas | Marcus | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1c62141f68b14d95a096d543d61c949c][1]_[2].png","originalImageName":"E271C-M13R"} |  |  | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | Electrical |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 18/12/2025 | ID: 537
E272C | M13R |  | M13R-E272C | Branch Cable Tray to be provided upto to Lighting Fixture | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[97397c625b794addb44175f4582ff1ca][1]_[2].png","originalImageName":"E272C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9ab74f34e8a8417ea08a45bbc4f30235][1]_[9].png","originalImageName":"E272C"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/13：The cable tray has been modified to be near the lighting fixtures | 12/12/2025 | 29.0000000000000 | 18 Dec: tray is located near to the light fitting. no further comment | 17/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated as per comments. | 24/12/2025 | 17.3750000000000 | 11/01/26-UR7U-Noted. The cable tray has been modified | Welton |  | 10/01/2026 | 09.01.2026-NA53-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E273C | M13R |  | M13R-E273C | Lighting Fixture U Clamp to be provided at the Middle instead of Top rail LNO-223-08-M13-003,LNO-223-08-M13-005 &LNO-223-04-M13-010 | Welton/Tee | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[49249949e34f4a11a521e5ee36809ed8][1]_[2].png","originalImageName":"E273C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[4c6495599a3b4fd7891d35cc3c7ed75e][2]_[12].png","originalImageName":"E273C"} | YES | ELECTRICAL | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/12：The U-shaped clip of the lighting fixture has been modified in the middle | 11/12/2025 | 27.0000000000000 | 18Dec: the 3 mentioned lighting pole clamp location has been modified to the middle rail. Vendor to ensure all lighting pole clamp location near stair landing to be at the middle rail as per typical installation. | 17/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated as per comments. | 24/12/2025 | 15.3527777777781 | 09/01/26-UR7U-Noted. Lighting pole clamp location has been modified. | Welton |  | 08/01/2026 |  | ELECTRICAL |  | 08/01/2026 | -1.00000000000000 |  |  | 09/01/2026 | ID: 398
E274C | M13R |  | M13R-E274C | Lighitng Fixture Junction Box CXE-L-M13-120,CXN-L-M13-038, CXE-L-M13-109 shall be Lowered down | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[746cf5b2bf2b462e98209f8184e6bad0][1]_[2].png","originalImageName":"E274C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b78c4035a0d14a8c93f5cae81aea052a][2]_[16].png","originalImageName":"E274C"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/23：The lighting fixture junction boxes CXE-L-M13-120, CXN-L-M13-038 and CXE-L-M13-109 have been lowered | 22/12/2025 | 19.0000000000000 | 24 Dec: Vendor to confirm the JB height shall be as per installation details (E204) which is 1300-1500mm for accessibility & ergonomic requirement. Unless it is not possible, then higher level can be accepted case by case basis, depend on PB acceptance. | 23/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model updated as per comments, PB confirm the acceptance. | 25/12/2025 | 16.3312500000029 | 11/01/26-UR7U-Noted. JBs relocated. | Welton |  | 10/01/2026 | 09.01.2026-NA53- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E275C | M13R |  | M13R-E275C | Lighting Fixture LES-311-09-M13-002 ,LES-311-09-M13-004to be evaulated ,if required to be delete meeting the Lighting Lux requirement | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[5cf1c31b7252401a9ee2d5d063493757][1]_[2].png","originalImageName":"E275C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b84343b7d7fb42b7acdb8442c96b791f][1]_[6].png","originalImageName":"E275C"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/13：The positions of the lighting fixtures LES-311-09-M13-002 and LES-311-09-M13-004 have been modified 2025/12/26: both LES-311-09-M13-002 and LES-311-09-M13-004 are moved to handrail outside to ensure the illumination will not be blocked by hvac duct. | 25/12/2025 | 16.0000000000000 | 18 Dec: Vendor to provide clear description what has been modified for both lighting. Observed LES-311-09-M13-004 illumination direction is blocking by the HVAC duct. Please justify with calculation the lighting is required. 2 Jan: Noted. Vendor has ensured there is no blocking of illumination after moving the lighting fixture. no further comment | 01/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: KBR comment need to be considered and implemented. 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | 4.39236111110949 | 11/01/26-UR7U-Noted. Ligthing fixture modified. | Welton |  | 10/01/2026 | 09.01.2026-NA53 - Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E276C | M13R |  | M13R-E276C | Lighting Fixture JB CXN-L-M13-030 to be moved to nearby structure as per Markup | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[143483dafe5b46089d8415aaf1b5d8a2][1]_[2].png","originalImageName":"E276C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[d62d52127a964d38a966ecbf2158770b][2]_[28].png","originalImageName":"276c"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/13：The junction box CXN-L-M13-030 has been moved near the structure 2025/12/26: the branch cable tray is revised to resolve the cable connection concern form KBR | 25/12/2025 | 16.0000000000000 | 18 Dec: refer to attached, observed tray is routed underneath JB may cause cable entries issue. Please evaluate and ensure no issue for JB cable entries with current arrangement. 2 Jan: Noted vendor is ensured no cable entries issue with current arrangement. No further comment. | 01/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: secondary cable routing need to be adjusted to keep cable pulling and entering properly. 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | 4.39166666667006 | 11/01/26-UR7U-Noted. JBs relocated. | Welton |  | 10/01/2026 | 09.01.2026-RTWG- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E277C | M13R |  | M13R-E277C | Lighting Fixture LNO-223-10-M13-002 shall be arranged as per the markup as the lighting focuses on out side moduel | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[e26ed85f73884c3eb36447d162578ed5][1]_[2].png","originalImageName":"E277C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[eb8370a8c1d74a679f71d10df7411780][1]_[8].png","originalImageName":"E277C"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/13：The lighting fixture LNO-223-10-M13-002 has been modified | 12/12/2025 | 29.0000000000000 | 18 Dec: lighting orientation adjusted. no further comment | 17/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated as per comment. | 24/12/2025 | 17.3506944444453 | 11/01/26-UR7U-Noted Lighting Fixture relocated. | Welton |  | 10/01/2026 | 09.01.2026-NA53-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E278C | M13R |  | M13R-E278C | Lighitng Fixture Junction Box CXN-L-M13-027 shall be Lowered down | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8c889af815414e5092a24035a99e552a][1]_[2].png","originalImageName":"E278C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b1a974fb64df43c191d0bdf128cbe708][1]_[7].png","originalImageName":"E278C"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/12：The lighting fixture junction box CXN-L-M13-027 has been lowered | 11/12/2025 | 30.0000000000000 | 18Dec: Lighting JB has lower down as per installation standard height. no further comment | 17/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated as per comment. | 24/12/2025 | 17.3458333333401 | 11/01/26-UR7U-Noted. JBs relocated. | Welton |  | 10/01/2026 | 09.01.2026-NA53- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E279C | M13R |  | M13R-E279C | Lighitng Fixture Junction Box CXE-L-M13-079,CXN-L-M13-009 shall be fixed near to the Lighting Fixture | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b2e722de63bd418eb7dbabc873759143][1]_[2].png","originalImageName":"E279C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[74ec30b686f34b339a832b1ecea72593][2]_[25].png","originalImageName":"279c"} | YES | ELECTRICAL | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/12 the model has been updated 2026/01/01: cable tray support length is reduced and cable entry issue can be resolved. 2026/01/06：cable tray support is not blocking cable entry, because the Junction box support is longer than cable tray support, please review again. | 05/01/2026 | 7.00000000000000 | 18 Dec: refer to attached, Please evaluate and ensure no issue for JB cable entries with current arrangement (support near to cable entry location) 02 Jan: Cable tray support member is just 150mm away from CXN-L-M13-009, blocking cable entries. | 01/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: secondary routing need to be re-route to keep cable entry properly. 6-Jan-2026: KBR comments need to be implemented and cable tray support need to reroute to keep cable entry clearance. 10-Jan-2026: 3D model updated, cable tray support is not blocking cable entry. | 10/01/2026 | 3.18402777778101 | shifted near lighting | Julius Orzales |  | 13/01/2026 |  | ELECTRICAL |  | 13/01/2026 | -0.674305555556202 |  |  | 13/01/2026 | ID: 484
E280C | M13R |  | M13R-E280C | KBR to align the E0L Lighting with M13R lighting Support 5 Jan: AOL lighting and JB have been aligned with M13R Lighting Support. | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b23ac9493cca4c81af1769504fc096ad][1]_[2].png","originalImageName":"E280C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1333141660864eec935ae3a64e7f2361][2]_[24].png","originalImageName":"E280C"} | YES | ELECTRICAL | Seatrium | 14/01/2026 | KBR | Pending Petrobras | 2025/12/26,please KBR to align the E0L Lighting with M13R lighting Support | 25/12/2025 | 10.0000000000000 | AOL lighting & JB has been aligned with M13R lighting Support | 04/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | -1.61597222222190 | [5 empty] | ELECTRICAL | [5 empty] | 06/01/2026 | ID: 579
E281C | M13R |  | M13R-E281C | Shift the Lighting Fixture Junction box CXE-L-M13-097 to the right side as the current postion is close to the ducting | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[180ed8bb137540b5ba3e885582b4e90c][1]_[2].png","originalImageName":"E281C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9774d62af84a4b33ba1554857cf60e88][2]_[10].png","originalImageName":"E281C"} | YES | ELECTRICAL | ABB/CIMC | 11/12/2025 | CIMC | Close | 2025/12/12 the model has been updated | 11/12/2025 | 30.0000000000000 | 18 Dec: JB adjusted. No further comment. | 17/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated as per comment. | 24/12/2025 | 17.3458333333328 | 11/01/26-UR7U-Noted. 3D model updated. | Welton |  | 10/01/2026 | 09.01.2026-NA53-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E282C | M13R |  | M13R-E282C | Lighting Junction Box for Exit and LED lighting fixture shall be lower down | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[ef93be899bb84c6097e96b3ab8c43db7][1]_[2].png","originalImageName":"E282C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[df8ea96d03d44cacb072f11ccd2ca5a3][1]_[8].png","originalImageName":"E282C"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/13：The lighting junction boxes for the exit and LED lamps have been lowered | 12/12/2025 | 29.0000000000000 | 18 Dec: JB location adjusted. No further comment | 17/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated as per comment. | 24/12/2025 | 17.3402777777810 | 11/01/26-UR7U-Noted. JBs relocated. | Welton |  | 10/01/2026 | 09.01.2026-NA53-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E283C | M13R |  | M13R-E283C | Maintainanence access for VFD Louver shall be evaluated and KBR to recheck having double base frame for the VFD CF-B-UH-TS-TG-5147001A | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[75e1175d4fb345218d36cb749798c6e3][1]_[2].png","originalImageName":"E283C-M13R"} |  |  | YES | ELECTRICAL | Seatrium | 14/01/2026 | Seatrium | Pending KBR | 2025/12/30,please KBR to check with vendor about maintainence access requirement and base frame height . | 29/12/2025 | -1.00000000000000 | [5 empty] | Electrical |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 30/12/2025 | ID: 539
E284C | M17 |  | M17-E284C | Lighting fixture LEM-354-11-M17-001 and Junction Box CXE-L-M17-412 to be relocated as the current position not accessible | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[86c8784765234719961b2d0b232c3a49][1]_[2].jpg","originalImageName":"E284C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[dcadf39f8f5f4e1e9c4f6414195d75eb][2]_[16].png","originalImageName":"E284C"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/19, the model has been updated | 18/12/2025 | 23.0000000000000 | 24 Dec: Lighting and JB relocated for accessibility. No further comment | 23/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model has been update as per comments. | 25/12/2025 | 16.3590277777766 | 11/01/26-UR7U-Noted. Lighting fixture and JB relocated | Welton |  | 10/01/2026 | 09.01.2026-RTWG-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E285C | M17 |  | M17-E285C | Lighting Fixture LEM-354-11-M17-005 not align with Lighting Support | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[9e612178b7194042a3195c50adcbfb8d][1]_[2].png","originalImageName":"E285C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[3cd760cef72a4a7d91d892d547ce2d67][1]_[5].png","originalImageName":"企业微信截图_17654350241243"} | YES | ELECTRICAL | ABB/CIMC | 10/12/2025 | CIMC | Close | 2025/12/11, the model has been updated | 12/12/2025 | 29.0000000000000 | 18 Dec: Lighting aligned with support. No further support | 17/12/2025 |  |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated as per comment. | 24/12/2025 | 17.3388888888876 | 11/01/26-UR7U-Noted. Lighting Fixture adjusted. | Welton |  | 10/01/2026 | 09.01.2026-RTWG-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E286C | M17 |  | M17-E286C | Lighting Junction Box CXE-L-M17-419 shall be close to lighting fixture LEM-354-11-M17-008 | Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a93dc595d3b64ec481ad4dc434c1a28f][1]_[2].png","originalImageName":"E286C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[8391f64704984dd8afcb800ae72be539][2]_[26].png","originalImageName":"286"} | YES | ELECTRICAL | ABB/CIMC | 10/12/2025 | CIMC | Close | Model update 2025/12/11 2025/12/25: close out snapshot is updated, kindly take note that this punch already not valid due to PB final advice(Punch-E337C),please review again. thanks! | 24/12/2025 | 17.0000000000000 | 18 Dec: Please update the close out snapshot. JB location updated in different location showing in close out snapshot. Ensure the updated location will not be impacted maintenance volume. 2 Jan: Noted on the punch to be reviewed together with Punch E337C on the mounting height concern. No further comment. | 01/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: KBR comment need to be implemented. 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | 4.36736111110804 | 11/01/26-UR7U-Noted. JB relocated. | Welton |  | 10/01/2026 | 09.01.2026-RTWG-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E287C | M17 |  | M17-E287C | Junction Box (CXE-L-M17-217 & CXE-L-M17-218 ) & (CXE-L-M17-236 &CXE-L-M17-235 )for Exit Lighting and LED Lighting shall be located to the Airlock Wall instead of Ceiling at a Height of 2.5 M | Bruno/Devission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[390da0b03c0044408941861e65afc8de][1]_[2].png","originalImageName":"E287C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[f54d20187e6d4893a4b0eecab16849b1][2]_[26].png","originalImageName":"287c"} | YES | ELECTRICAL | ABB/CIMC | 15/12/2025 | CIMC | Close | 2025/12/16 The model has been update 2026/01/01: junction box arrangement is modified, please review again | 31/12/2025 | 10.0000000000000 | 24 Dec: Vendor to ensure no issue on accessibility during relocation of JB. Observed a JB very closed to the door, possible risk hit by the door when someone open the door from outside during maintenance with stairs (refer attached) 2 Jan: JBs location adjusted. No further comment. | 01/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: KBR comments need to be implemented, CXE-L-M17-217 need to relocated far away from door and keep cable entry and termination properly. 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | 4.37500000000000 | 11/01/26-UR7U-Noted. JBs relocated. | Welton |  | 10/01/2026 | 09.01.2026-RTWG- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E288C | M17 |  | M17-E288C | Based on Lighting Lux calcualtion, Lighting fixture to be added in the middle corridor of Transformer Room Level-1 & Level-2 | Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6a2aa1c1c81d4242b01f011681ae91fc][1]_[2].png","originalImageName":"E288C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[32ec1177746b4ce1a373264256c8672c][2]_[16].png","originalImageName":"288"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/25: under the premise of meeting lux level requirement, LNO-228-01-M17-001 and LES-314-01-M17-003 are shifed to center corridor for level-1 transformer room. similarly, LES-314-04-M17-005 is shifted to center corridor and a new lighting(LES-314-04-M17-005) is added for level-2 transformer room. | 24/12/2025 | 14.0000000000000 | 2 Jan: Lightings are considered above center corridor to ensure sufficient lux level. Vendor to confirmed sufficient lux level requirement & accessibility. No further comment. | 01/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL | lighting illumination calculation report need to be provided in future to verify to meet project lux level requirement. | Shichen Li | 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | 2.37291666666715 | 09/01/26-UR7U- Lighting distribution adjusted. To be confimed by Lighting calculation report. | Welton |  | 08/01/2026 |  | ELECTRICAL |  | 08/01/2026 | -1.00000000000000 |  |  | 09/01/2026 | ID: 398
E289C | M17 |  | M17-E289C | The following Lighitng Fixture Junction Box Shall be Lowered down to have Maintanance Acces CXE-L-M17-234,CXE-L-M17-310,CXE-L-M17-294,CXE-L-M17-238 ,CXE-L-M17-312,CXN-L-M17-217,CXE-L-M17-352,sCXN-L-M17-218,CXE-L-M17-080,CXN-L-M17-188,CXE-L-M17-418,CXE-L-M17-424,CXE-L-M17-433 ,CXE-L-M17-434,CXE-L-M17-445,CXN-L-M17-236,CXN-L-M17-236,CXN-L-M17-203,CXN-L-M17-206,CXN-L-M17-230,CXE-L-M17-419,CXE-L-M17-431,CXN-L-M17-233,CXN-L-M17-235,CXN-L-M17-236,CXN-L-M17-237,CXN-L-M17-238,CXN-L-M17-239,CXN-L-M17-240,CXN-L-M17-241,CXN-L-M17-242 | Bruno/Devission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b21df4bfcec1413eb6e1628269cc3777][1]_[2].png","originalImageName":"E289C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2e65f7dd0768494ebb01c0f52bac07d7][2]_[19].png","originalImageName":"E289C-20251230"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Rejected | 2025/12/30,the these lighting fixture junction box had been lowered down ,refer to latest 3D model . | 29/12/2025 | 10.0000000000000 | 6 Jan: Refer to attached excel list comment | 05/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan-2026: KBR comments need to be implemented and open items need to be updated and re-replied. | 09/01/2026 | -1.00000000000000 | [5 empty] | ELECTRICAL | [5 empty] | 14/01/2026 | ID: 539
E290C | M17 |  | M17-E290C | Lighting Fixture Junction Box CXE-L-M17-336 ,CXE-L-M17-335,CXE-L-M17-349 CXE-L-M17-348,CXE-L-M17-242,CXE-L-M17-244,CXN-L-M17-006, shall be relocated to lower CXE-L-M17-352down | Bruno/Devission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[42b5bc1e563a41089b1146f9dd4cb22c][1]_[2].png","originalImageName":"E290"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[3217676865124a7594a80ce6aee36857][2]_[25].png","originalImageName":"E290C-20260114"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Rejected | 2025/12/30,the these lighting fixture junction box had been lowered down ,refer to latest 3D model . | 29/12/2025 | 14.0000000000000 | 6Jan: CXE-L-M17-335: try to avoid mounted behind the door CXE-L-M17-348 & 349: JBs are locating higher than lighting, please study again, if possible, to lower down as per other JBs. CXE-L-M17-352: mounting height around 2.7m, possible to lower down further? | 04/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan-2026: KBR comments need to be implemented and re-replied. | 09/01/2026 | 3.00000000000000 | [5 empty] | ELECTRICAL | [5 empty] | 14/01/2026 | ID: 539
E291C | M17 |  | M17-E291C | Lighitng Junction Box shall kept neear to the Lighting fixture | Bruno/Devission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[103c9d4e237c431d919215f992fd7474][1]_[2].png","originalImageName":"E291"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[cbadb75ec1374425afa05b9a50149d66][2]_[15].png","originalImageName":"E291C"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/19：The junction box has been moved close to the light fixture. | 18/12/2025 | 25.0000000000000 | 24 Dec: JBs has placed closed to the respective lighting, no further comment | 23/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model has been update as per comments. | 25/12/2025 | 18.3590277777766 | 14/01/26-UR7U-Noted. JBs relocated. | Welton |  | 13/01/2026 |  | ELECTRICAL | [5 empty] | 13/01/2026 | ID: 398
E292C | M17 |  | M17-E292C | Evaluate to reroute the IG541 above the 13.8kV Bus Duct Vertical Panel | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0d388eba25084521a5954019a7437968][1]_[2].png","originalImageName":"E292"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[e1ec22a6307a4f31b97308413041e515][1]_[9].png","originalImageName":"E292"} | Re-work | PIPING | ABB/CIMC | 16/12/2025 | CIMC | Pending KBR | 2025/12/17: The pipe of IG541 above the 13.8kV Bus Duct Vertical Panel has been rearranged. | [7 empty] | PIPING |  |  |  | PIPING | [10 empty] | PIPING | [5 empty] | 18/12/2025 | ID: 537
E293C | M17 |  | M17-E293C | Lighting Junction Box is too close to the lighting fixture , Shall be relocated | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[617397ab48464f638ee4ad0884bddf24][1]_[2].png","originalImageName":"E293"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c33ad36aaf224efca0cd71234b57849e][2]_[22].png","originalImageName":"293"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/15:The lighting fisxture JB has been moved 2025/12/25: construction team confirmed that there is no issue for JB and lighting cable connection. | 24/12/2025 | 17.0000000000000 | 18 Dec: JB still located quite near to the lighting fitting. Vendor to ensure feasible for cable entries to both JB & Lighting 2 Jan: Vendor confirmed construability, no further comment. | 01/01/2026 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: Lighting JB need to be relocated to more faraway from lighting fixture, and need to clear clash with secondary cable tray as well. 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | 4.37013888888760 | 11/01/26-UR7U-Noted. JB relocated. | Welton |  | 10/01/2026 | 09.01.2026-RTWG- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E294C | M17 |  | M17-E294C | Relocate the Lighitng Fixture as it is very close to the door | TEE | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[20d5f0d607dc4173bc2a8f79309ca3e4][1]_[2].png","originalImageName":"E294"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[94613a4dd06d4563aac38cb2833e6c67][2]_[24].png","originalImageName":"294"} | YES | ELECTRICAL | ABB/CIMC | 16/12/2025 | CIMC | Close | 2025/12/17 The model has benn update | 12/12/2025 | 30.0000000000000 | 18 Dec: lighting relocated to top of door. no further comment | 17/12/2025 | Tee |  |  | Electrical |  |  |  | ELECTRICAL |  | Shichen Li | 24-Dec-2025: 3D model has been updated as per comment. | 24/12/2025 | 18.3388888888876 | 12/01/26-UR7U-Noted. Lighting fixture relocated. | Welton |  | 11/01/2026 | 12.01.2026-NA53- Close | ELECTRICAL |  | 11/01/2026 | 0 |  |  | 12/01/2026 | ID: 398
E295C | M17 |  | M17-E295C | Junction Box shall be Lowered Down as per the markup for Maintenance access | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[565a944c2f2e43f78e86ffa2f4b274b9][1]_[2].png","originalImageName":"E295"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[987d5363108349b59b1fd2700b43926a][2]_[21].png","originalImageName":"295"} | YES | ELECTRICAL | ABB/CIMC | 15/12/2025 | CIMC | Close | 2025/12/16 The JB has been moved | 14/12/2025 | 27.0000000000000 | 18 Dec: JB adjusted to lower location. Vendor to ensure cable tray support is not blocking cable entry to the JB. | 17/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL | ABB/CIMC to ensure cable pulling and entry properly to relevant JBs. | Shichen Li | 24-Dec-2025: 3D model has been updated as per comment. | 24/12/2025 | 17.3256944444438 | 11/01/26-UR7U-Noted. Jbs relocated. | Welton |  | 10/01/2026 | 09.01.2026-RTWG- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E296C | M17 |  | M17-E296C | Junction Box CXE-L-M17-264,CXE-L-M17-250 shall be Lowered Down as per the markup for Maintenance access | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[77873711a7034766a40e0f03ad06bfe0][1]_[2].png","originalImageName":"E296"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[16847bfb63a64065b0038431cbb9a226][1]_[5].png","originalImageName":"296"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/15:The lighting fisxture JB has been moved | 14/12/2025 | 27.0000000000000 | 24 Dec: JB has lower down to the accessible height as per installation details. No further comment | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model has been update as per comments. | 25/12/2025 | 16.3520833333314 | 11/01/26-UR7U-Noted. JBs relocated. | Welton |  | 10/01/2026 | 09.01.2026-RTWG- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E297C | M17 |  | M17-E297C | Lighting Fixture U Clamp to be provided at the Middle instead of Top rail LEM-354-02-M17-008 & LEM-355-02-M17-006,LNO-228-14-M17-007,LEM-355-07-M17-001,LEM-354-10-M17-009,LEM-355-11-M17-001,LEM-355-11-M17-005 | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[11876dc19d644b3f91f0796d0146f9e1][1]_[2].png","originalImageName":"E297"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[99109bfc1ea94abe87a38311fe12c62c][1]_[5].png","originalImageName":"297"} | NO | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/15:The Lighting Fixture U Clamp to be provided at the Middle | 14/12/2025 | 27.0000000000000 | 24 Dec: Lighting Fixture U clamp close to stairs landing are consider on mid rail, vendor to ensure all lighting location has already consider on this requirement for both M17 & M13R. no further comment | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL | EC-M17-L-N-TRAY-01019-TRAY-0002 need to be re-route to avoid obstruct by lighting pole stiffener. | Shichen Li | 25-Dec-2025: 3D model has been updated as per comments. |  |  | 11/01/26-UR7U-Noted. U Clamp adjusted. | Welton |  | 10/01/2026 | 09.01.2026 - RTWG- Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E298C | M17 |  | M17-E298C | Junction Box shall be Lowered Down as per the markup for Maintenance access CXE-L-M17-439 - Lower Down (up to 2,80m) CXE-L-M17-015 - Lower Down (up to 2,80m) CXN-L-M17-055 - Lower Down (up to 2,80m) CXE-L-M17-016 - Lower Down (up to 2,80m) CXE-L-M17-438 - Lower Down (up to 2,80m) CXN-L-M17-225 - Lower Down (up to 2,80m) | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c4332b19443a4bbd88496788a9618225][1]_[2].png","originalImageName":"E298"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[917fa77649b647aaafc6df5b51683ba5][2]_[15].png","originalImageName":"E298C-20251230"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/30,the these lighting fixture junction box had been lowered down ,refer to latest 3D model . | 29/12/2025 | 12.0000000000000 | 2 Jan JBs has been relocated for accessibility. No further comment. | 01/01/2026 |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 6-Jan-2026: 3D model has been updated as per punch comments. | 06/01/2026 | 4.36944444444089 | 11/01/26-UR7U-Noted. JBs relocated. | Welton |  | 10/01/2026 | 09.01.2026-RTWG-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E299C | M17 |  | M17-E299C | CXN-L-M17-215 Junction box shall be relocated near to the socket SKN-M17-014 | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[13656ccb360e4d35a937bd7b1358a940][1]_[2].png","originalImageName":"E299"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[76d8c64945b440ea8f00acb4eccb706b][2]_[21].png","originalImageName":"E299C"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 12/22/2025：3D model updated. | 21/12/2025 | 20.0000000000000 | 24 Dec: JB has relocated. no further comment | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model has been update as per comments. | 25/12/2025 | 16.3520833333314 | 11/01/26-UR7U-Noted. JBs relocated. | Welton |  | 10/01/2026 | 09.01.2026-RTWG-Close | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E300C | M17 |  | M17-E300C | CXE-L-M17-318 Junction box shall be relocated as per markup | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6e3eac658dc3466bb4a2849a8a4cde10][1]_[2].png","originalImageName":"E300"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9397206c90ce418d8fe1b95acc5a068d][2]_[18].png","originalImageName":"E300"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Rejected | 2025/12/25: CXE-L-M17-318 installation method is changed to make the cable entry at below side, kindly take note that it's different with punch recommendation.please review. 2026/01/12: ABB/CIMC confirmed that the accessibility is possible because the clearence from damper control panel to JB front side is around 440mm. | 11/01/2026 | 1.00000000000000 | 6 Jan: there is a HVAC equipment PDA-M17-E-13 below the JB, Vendor to confirm the JB access. 13 Jan: Refer to the attached. It seems there is no improvement on the JB access, please find another better location with better access and close to the lighting | 12/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan-2026: CXE-L-M17-318 need to be re-located nearby to keep maintenance operation space. 14-Jan-2026: KBR comments need to be implemented. | 13/01/2026 | -1.00000000000000 | [5 empty] | ELECTRICAL | [5 empty] | 14/01/2026 | ID: 579
E301C | M17 |  | M17-E301C | Rotate the Lighitng Junction 90 Deg to make Cable Entry Bottom CXE-L-M17-358 - Rotate the JB - cable shall entry from below CXN-L-M17-146 - Rotate the JB - cable shall entry from below CXE-L-M17-351 - Rotate the JB - cable shall entry from below CXN-L-M17-147 - Rotate the JB - cable shall entry from below CXE-L-M17-357 - Rotate the JB - cable shall entry from below CXE-L-M17-362 - Rotate the JB - cable shall entry from below | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[78239fb3694a4c4b820769dbba6bc25d][1]_[4].png","originalImageName":"E301"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7e366ebcd6884edb8a74e434fcccc4ae][2]_[12].png","originalImageName":"301"} | YES | ELECTRICAL | ABB/CIMC | 16/12/2025 | CIMC | Close | 2025/12/17, the model has been updated | 16/12/2025 | 25.0000000000000 | 24 Dec: JB orientation update as per comment. No further comment | 23/12/2025 |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model has been update as per comments. | 25/12/2025 | 16.3472222222190 | 11/01/26-UR7U-Noted. JBs adjusted. | Welton |  | 10/01/2026 | 09.01.2026-RTWG - Close. | ELECTRICAL |  | 10/01/2026 | 0 |  |  | 11/01/2026 | ID: 398
E302C | M17 |  | M17-E302C | Installation arrangement to be modified for lighting fixture support to make lighting fall to the floor instead of foccuesing on the HVAC equipment LEM-354-10-M17-006 & LES-314-09-M17-003 | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[db4bee34026a4aaab6202338980985c0][1]_[2].png","originalImageName":"E302"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[0fd1e2dd515145ccb1ea42e49b34834b][1]_[5].png","originalImageName":"E302C"} | YES | ELECTRICAL | ABB/CIMC | 11/12/2025 | CIMC | Close | 12/12/2025：3D model updated 2025/12/12, as per close out meeting ,this punch can be transfer to PB close | 11/12/2025 | 31.0000000000000 | [5 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [5 empty] | 12/01/26-UR7U-Noted. | Welton |  | 11/01/2026 | 12.01.26 - NA53 - Close | ELECTRICAL |  | 11/01/2026 | 0 |  |  | 12/01/2026 | ID: 398
E303C | M17 |  | M17-E303C | Relocate the Lighting Junction box as per the Markup Location CXE-L-M17-431 | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[05f026f45a0a4c1ca7fd51f9833a8d7a][1]_[2].png","originalImageName":"E303"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b9807e5c48324ec8a6b65e659bbb876a][2]_[20].png","originalImageName":"303c"} | YES | ELECTRICAL | ABB/CIMC | 12/12/2025 | CIMC | Pending Petrobras | 2025/12/13, the model has been updated 2026/01/04: CXE-L-M17-431 location is updated as per final punch E337C, the height is lowered to 1.4m for easy maintenance. | 03/01/2026 | 5.00000000000000 | 24 Dec: observed JB location different from close out snapshot. Vendor to confirm final location and update the close out snapshot 6Jan: no further comment | 02/02/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: KBR comments need to be implemented. lighting JB was missing and not align with close-out snapshot. 10-Jan-26: 3D model updated as per punch comments. | 10/01/2026 | -1.54305555555766 | [5 empty] | ELECTRICAL | [5 empty] | 10/01/2026 | ID: 579
E304C | M17 |  | M17-E304C | Relocate the Lighting Junction box as per the Markup Location CXE-L-M17-424 | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a52f22ed371a4d6f94956ee2aa804480][1]_[2].png","originalImageName":"E304"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7297b1958add41c3845bbb9566eccbb8][2]_[29].png","originalImageName":"304c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending Petrobras | 2025/12/22, the model has been updated as per punch No.E337C 2026/01/01: CXE-L-M17-424 location has been changed as per Punch E337C, and make it more close to corresponding lighting fixture(LEM-354-11-M17-013) | 31/12/2025 | 8.00000000000000 | 24 Dec: relocated JB location too far from lighting, please study and propose better location 6 Jan: no further comment | 02/02/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: KBR comments need to be implemented. 10-Jan-26: 3D model updated as per punch comments. | 10/01/2026 | -1.55000000000291 | [5 empty] | ELECTRICAL | [5 empty] | 10/01/2026 | ID: 579
E305C | M17 |  | M17-E305C | Relocate the Lighting Junction box CXE-L-M17-431,CXN-L-M17-231 close to the Lighting fixture | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d1cfc2cc87064b7cb23fc017e8b64199][1]_[2].png","originalImageName":"E305"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a5ee40f57193401cba7532666655524d][2]_[18].png","originalImageName":"E305C-20251230"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/30,the two lighting junction had been shifted to close lighting fixtrure. | 29/12/2025 | 13.0000000000000 | 6 Jan: JB relocated closer to lighting with maintenance access. No further comment | 05/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 7-Jan-2026: 3D model updated as per punch comments. | 07/01/2026 | 4.05555555555475 | 12/01/26-UR7U-Noted. JB relocated. | Welton |  | 11/01/2026 | 12.01.26 - NA53 - Close | ELECTRICAL |  | 11/01/2026 | 0 |  |  | 12/01/2026 | ID: 398
E306C | M17 |  | M17-E306C | Relocate the Lighting Junction box as per the Markup Location CXE-L-M17-433 | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a8ad9dc1b3464da582d2091c203646c0][1]_[2].png","originalImageName":"E306"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[3a8f887d6f1342e28d414e681009ae25][2]_[14].png","originalImageName":"E306C"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/22, the model has been updated as per punch No.E337C | 21/12/2025 | 22.0000000000000 | 24 Dec: JB has relocated for maintenance accessibility, no further comment | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model has been update as per comments. | 25/12/2025 | 19.3472222222190 | 14/01/26-UR7U-Noted. JBs relocated. | Welton |  | 13/01/2026 |  | ELECTRICAL |  | 13/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 398
E307C | M17 |  | M17-E307C | Relocate the Lighting Junction box near to the Lighting Fixture CXE-L-M17-435,CXN-L-M17-207CXE-L-M17-434,CXE-L-M17-432,CXE-L-M17-089 | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[af3bf00c92f04fde9d109f80d2d7b14e][1]_[2].png","originalImageName":"E307"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9f014091600743c585fcd3dc9caac04f][2]_[14].png","originalImageName":"E307C-20251230"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Rejected | 2025/12/30,these lighting junction box had been shifted to close these lighting fixture. 2026/01/12: KBR mentioned CXE-L-M17-435 missing cable tray has beed added. Please review again. | 11/01/2026 | 1.00000000000000 | 6 Jan: JBs are relocated closer to lighting. CXE-L-M17-435 missing cable tray connection. Please update. 13 Jan: CXE-L-M17-435 is encroaching into VT-5254001C maintenance volume. Please check and update | 12/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan-2026: CXE-L-M17-435 clash with VT-5254001B need to be cleared. cable tray connection to lighting JB need to be designed properly. 14-Jan-2026: KBR comments need to be implemented. | 14/01/2026 | -1.43611111111386 | [5 empty] | ELECTRICAL | [5 empty] | 14/01/2026 | ID: 579
E308C | M17 |  | M17-E308C | Remove the Lighting fixture between the AHU as there is Manitainance access. | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a43afc8ed7c04beaa39ed73447d36e02][1]_[2].png","originalImageName":"E308"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[aa7c1cc9dba546dab23dc05210530905][2]_[14].png","originalImageName":"E308C"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending KBR | 2025/12/19, the model has been updated 2026/01/01: ABB/CIMC confirmed that the lux level can meet the requirement even if remove this lighting, which can be verified by LIGHTING LUX CALCULATION to be updated later 2026/01/14, please refer to attached calculation result based on remove this lighting fixture . consider there are no access requirement between two AHU ,the Illuminance value is lower normal level .please customer check again . | 31/12/2025 | 12.0000000000000 | 24 Dec: Lighting is removed. Vendor to ensure no impact on lighting illumination in this area. 9 Jan: Please provide lighting lux calculation for verification. | 08/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: KBR comments need to be implemented. lighting illumination report need to be attached for close-out the punch. 10-Jan-26: Please provide lighting lux calculation for verification. | 10/01/2026 | 2.45069444444380 | [5 empty] | ELECTRICAL | [5 empty] | 14/01/2026 | ID: 539
E309C | M17 |  | M17-E309C | Relocate the Lighitng Junction Box CXE-L-M17-090 near to the Lighitng Fixture | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[63970edf579e4702bb3e55713b8cfff3][1]_[2].png","originalImageName":"E309"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[d4294cbaeeb248aca7ba5bb7c76b9fe1][2]_[23].png","originalImageName":"309c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/19, the model has been updated 2026/01/01: CXE-L-M17-090 location has been changed as per Punch E337C, and make it more close to corresponding lighting fixture(LES-314-10-M17-009) | 31/12/2025 | 12.0000000000000 | 24 Dec: JB location shown in close out snapshot is not tally with latest model. General comment: please ensure clear description what has been done for close out and include clear close out snapshot with correct tag, so it is clear for reviewer to comment for punch closure. No JB tag in this close out snapshot 7 Jan: Vendor to ensure compliance with mounting height requirement for maintenance access. no further comment | 06/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: KBR comments need to be implemented. 7-Jan-2026: 3D model updated as per punch comments. | 07/01/2026 | 6.05625000000146 | 14/01/26-UR7U-Noted. JB relocated. | Welton |  | 13/01/2026 | 12.01.26 - NA53 - Close | ELECTRICAL |  | 13/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 398
E310C | M17 |  | M17-E310C | Relocate the Lighitng Junction Box as per the markup | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[3d150fd0278f4aa4b7094cff41a2e30f][1]_[2].png","originalImageName":"E310"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[bdf75531cd7b4ff8ae39ef6dcfcd1864][2]_[24].png","originalImageName":"310c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/19, the model has been updated 2026/01/01: lighting junction box location has been changed to markup area based Punch E337C, there have enough space(more than 300mm) for bottom cable entry | 31/12/2025 | 12.0000000000000 | 24 Dec: JBs has relocated for maintenance access. Vendor to ensure sufficient cable entry space when placing JB top and bottom. 7 Jan: Vendor has confirmed no issue for cable entry. No further comment | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: KBR comments need to be advised and implemented. properly cable entry clearance need to be maintained. 7-Jan-2026: 3D model updated as per punch comments. | 07/01/2026 | 6.05416666666861 | 14/01/26-UR7U-Noted. JB relocated. | Welton |  | 13/01/2026 | 12.01.26 - NA53 - Close | ELECTRICAL |  | 13/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 398
E311C | M17 |  | M17-E311C | Move the Junction box from the Ladder and Maintain 200 mm gap between JB and Ladder | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[ddd7af11d514471e87b6b313e3824b11][1]_[2].png","originalImageName":"E311"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[80cc429071ad448680010b582f39ca7c][2]_[15].png","originalImageName":"E311C-20251226"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/26,this junction box had been shifted to right side | 25/12/2025 | 18.0000000000000 | 6 Jan: JB shift to better location without blocking ladder access. no further comment. | 05/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 7-Jan-2026: 3D model updated as per punch comments. | 07/01/2026 | 6.06041666666715 | 14/01/26-UR7U-Noted. JB relocated. | Welton |  | 13/01/2026 | 12.01.26 - NA53 - Close | ELECTRICAL |  | 13/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 398
E312C | M17 |  | M17-E312C | Relocate the Lighitng Junction Box CXN-L-M17-233 as per the markup | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4c192be5bd934a9cb259fa6b023f5f12][1]_[2].png","originalImageName":"E312"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[3d5deb1e763f44189d0cd9224ca852c4][2]_[15].png","originalImageName":"E312C"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Close | 2025/12/19, the model has been updated | 18/12/2025 | 25.0000000000000 | 24 Dec: JB relocated for maintenance accessibility. No further comment | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model has been update as per comments. | 25/12/2025 | 19.3458333333328 | 14/01/26-UR7U-Noted. JB relocated. | Welton |  | 13/01/2026 |  | ELECTRICAL |  | 13/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 398
E313C | M13R |  | M13R-E313C | SOCKET Junction Box to be owered Down CXN-L-M13-042 | Bruno/Devission/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0dbc0d3802ac419d8e37cd1b0cec72b8][1]_[2].png","originalImageName":"E313"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[01d6dd5952d64b12bcc4388424f3a5c1][1]_[5].png","originalImageName":"E313C"} | YES | ELECTRICAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/13：The CXN-L-M13-042 socket junction box has been moved down | 12/12/2025 | 29.0000000000000 | 24 Dec: JB has relocated for maintenance accessibility. No further comment | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model has been update as per comments. | 25/12/2025 | 16.3472222222190 | 11/01/26-UR7U-Noted. JBs relocated. | Welton |  | 10/01/2026 | 09.01.2026-NA53-Close | ELECTRICAL | [5 empty] | 11/01/2026 | ID: 398
E314C | M17 |  | M17-E314C | PFP Modelleing above MCT to be updated | Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[309da567ed3741a49af2cc9ef6c9606c][1]_[2].png","originalImageName":"E314"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[e1c9e046d3974293a5aa5b6814b1332f][2]_[16].png","originalImageName":"E314C"} | NO | PAINTING | ABB/CIMC | 25/12/2025 | CIMC | Pending Petrobras | 2025.12.19: PFP model has been updated | 25/01/2026 | -19.0000000000000 | 6 Jan: PFP is clear from the MCT. No further comment | 05/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 7-Jan-2026: 3D model updated as per punch comments. | 07/01/2026 | -0.940972222218988 | [5 empty] | ELECTRICAL | [5 empty] | 07/01/2026 | ID: 579
E315C | M17 |  | M17-E315C | Missing connection and bendingbetween ET-M17-H-TRAY-00097-TRAY-0102 and ET-M17-H-TRAY-01001-TRAY-0001 | Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6fd59b6ef6f84c99aeccd267677b5438][1]_[4].png","originalImageName":"E315"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7260f28c8b044c0d97829cd92549bf6f][2]_[16].png","originalImageName":"315c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending KBR | 2026/01/04: proper bending or transit cannot be added due to space constraint,ABB/CIMC suggest to remain current design since there haven't cable bending issue. KBR/SEA/PB to confirm the acceptance. 2026/01/13：Considering KBR's advice, ABB/CIMC would like to request KBR to confirm following item first: 1. the acceptance for two layer HV cable tray clearence is 250mm 2. the acceptance to change ET-098 tie-in to elevation 38190(around) | 12/01/2026 | -1.00000000000000 | 9 Jan: This is a 13.8 kV HV single‑core cable, and adequate support with proper fittings is required. It is recommended that the vendor consider lowering the ET‑M17‑H‑TRAY‑00098 tray to allow sufficient space for ET‑M17‑H‑TRAY‑00097 to achieve the proper bending radius. In general, the cable tray layout should account for constructability as well as long‑term cable performance and sustainability. | 08/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan: KBR comments need to be implemented. | 10/01/2026 | 1.45486111110949 | [5 empty] | ELECTRICAL | [5 empty] | 13/01/2026 | ID: 839
E316C | M17 |  | M17-E316C | Distance between cable trays not meeting the requirment - ET-M17-M-TRAY-07001-TRAY-0011 and ET-M17-L-N-TRAY-07015-TRAY-0013 - IT-M17-S-S-TRAY-3002 and ET-M17-L-N-TRAY-03021 - IT-M17-S-S-TRAY-03004 and ET-M17-L-N-TRAY-03017 | Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[5cd78b7508b94c67950f2f1c073a30b8][1]_[2].png","originalImageName":"E316"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[db92a3b1d69a43bbbf199999ef38d0ea][2]_[23].png","originalImageName":"316c"} | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 07/01/2026 | ID: 839
E317C | M17 |  | M17-E317C | Cover to be provided for the MCT to avoid access by non-qualified (electrical) personnel | Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[770ee6cf75214a39852093b1e9d85c5b][1]_[2].png","originalImageName":"E317"} |  |  | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 18/12/2025 | ID: 537
E318C | M17 |  | M17-E318C | Transition from MCT to the internal Cable tray to be Evaluated at Level-1 | Deivision/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[93da7aa54a45448e8689c5c6e96a5551][1]_[2].png","originalImageName":"E318"} |  |  | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 18/12/2025 | ID: 537
E319C | M17 |  | M17-E319C | Cable tray Support Clash with Cable tray | Tee | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[a5d8ad333eab4aadbb36e7fa5cdf3b7d][1]_[2].png","originalImageName":"E319"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b7230ba5fc7a44478825bbe78fe40ab2][1]_[8].png","originalImageName":"319"} | No | ELECTRICAL | ABB/CIMC | 15/12/2025 | CIMC | Close | 2025/12/16Thet clash has been update |  |  | 24 Dec: Clash Cleared, no further comment | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 25-Dec-2025: 3D model has been update and clash cleared. | 25/12/2025 | 19.3506944444453 | 14/01/26-UR7U-Noted. Support updated. | Welton |  | 13/01/2026 |  | ELECTRICAL |  | 13/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 398
E320C | M17 |  | M17-E320C | Suitable Transistion accessoreis Cable tray to cable trays to be Evaluated | Deivision/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[0d020b367d5f48ff8428a9a222aed97e][1]_[4].png","originalImageName":"E320"} |  |  | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 18/12/2025 | ID: 537
E321C | M17 |  | M17-E321C | In the M17 cable tray penetration from piperack the distance between horizontal and vertical cable tray is very big. Check and review. E.g. ET-M17-L-N-TRAY-00078-TRAY-0042 and ET-M17-L-N-TRAY-03029-TRAY-0001 | Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b9e161e6a0d94d2585d50613eee8c530][1]_[2].png","originalImageName":"E321"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a00c8c61293a462883ccbebc1de84e22][2]_[13].png","originalImageName":"E321C"} | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending Petrobras | 2025/12/19, the model has been updated | 18/12/2025 | 21.0000000000000 | 9 Jan: distance between vertical tray and horizontal tray has been considered. No further comment | 08/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan: 3D model has been updated as per punch comments. | 10/01/2026 | -1.54861111110949 | [5 empty] | ELECTRICAL | [5 empty] | 10/01/2026 | ID: 579
E322C | M17 |  | M17-E322C | General Comment for the cable tray routing from Horizontal to the vertical in the transformer room- Cable Bending radius to be check and additional support to be added to secure cable at the bending area | Ratha | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4cd459fc98374d8b8c8c13ae54efe1ef][1]_[2].png","originalImageName":"E322C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[7a12727790594231ad39d86d75cf4eb3][2]_[15].png","originalImageName":"322c"} | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Rejected | 2026/01/04: cable tray bending part is added , please confirm the acceptance | 03/01/2026 | 8.00000000000000 | 6 Jan: no bending fitting for ET-M17-L-N-TRAY-06020 & ET-M17-L-N-TRAY-06021 | 05/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan: ET-M17-L-N-TRAY-06020 & ET-M17-L-N-TRAY-06021 not align with the horizontal cable trays, ABB/CIMC study to advise to add bend fitting as per KBR comments. | 10/01/2026 | 1.45625000000291 | [5 empty] | ELECTRICAL | [5 empty] | 13/01/2026 | ID: 839
E323C | M17 |  | M17-E323C | General Comments:Cable Transistion from MCT to vertical cable tray to be evaluated with proper cable bending | Deivision/Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c79bf3f4df31425f830c100581076f83][1]_[2].png","originalImageName":"E323C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[20939127fcbf4e6fac82f84a23349a9f][2]_[12].png","originalImageName":"323c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Rejected | 2026/01/04: cable tray bending part cannot be added because it will clash with bulkhead/MCT, cable tray is extended more or less, please confirm the acceptance | 03/01/2026 | 5.00000000000000 | 9 Jan: Provide updated model snap showing correct position of vertical tray (current snap provided is not accepted). Position of tray should be suitable for cable passing and bending before they penetrate the bulkhead via MCT. Provide cable model showing required bending. |  |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan: KBR comments need to be implemented. | 10/01/2026 | -1.54513888889051 | [5 empty] | ELECTRICAL | [5 empty] | 10/01/2026 | ID: 579
E324C | M17 |  | M17-E324C | Cable tray Missing is between from MCT to cable Tray | Tee | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[3e4242c997b54095851bdc2f62371060][1]_[2].png","originalImageName":"E324C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[93c4f4f452ca47c9993fa18148439074][2]_[21].png","originalImageName":"324c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Rejected | 2025/12/19, the model has been updated 2026/01/01: two short piece cable ladder are added, this MCT only corresponding two layer cable tray(refer to bulkhead opposite),please review again | 31/12/2025 | 8.00000000000000 | 24 Dec: Please explain clearer on this close out. 1. proper fitting shall be consider 2. 3 layer trays to 2 layers trays and MCT 3. Routing is not clear on this arrangement 7Jan: Vendor shall consider Tee fitting for tray branching, instead of small piece of tray for tray connection | 06/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | Electrical |  | Shichen Li | 26-Dec-2025: KBR comments need to be implemented. close-out description need to be cleared and completed edited. 10-Jan-2026: ABB/CIMC need to study and advise as per KBR latest comments. | 10/01/2026 | -1.54652777777665 | [5 empty] | Electrical | [5 empty] | 10/01/2026 | ID: 579
E325C | M17 |  | M17-E325C | Bending Cable tray Missing is between from MCT E-M17-L-MCT-111 to cable Tray | Tee | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[655961fc54364d7e91190f1941ac45e1][1]_[2].png","originalImageName":"E325C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[fed90f992d5e4ddc873a515b24554939][2]_[11].png","originalImageName":"E325C"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Rejected | 2025/12/19, the model has been updated | 18/12/2025 | 24.0000000000000 | 9 Jan: distance between tray and MCT should 400mm or less. | 08/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan: KBR comments need to be implemented. | 10/01/2026 | 1.44930555555766 | [5 empty] | ELECTRICAL | [5 empty] | 13/01/2026 | ID: 839
E326C | M17 |  | M17-E326C | Bottom Cable tray Connection to the MCT E-M17-L-MCT-138 is missing | Tee | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d3c17ef4feb04428a383fc76cc9b1dab][1]_[2].png","originalImageName":"E326C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[6ebd7044e1214b65a93abe1de055b63b][1]_[7].png","originalImageName":"326"} | NO | ELECTRICAL | ABB/CIMC | 16/12/2025 | CIMC | Pending Petrobras | 2025/12/17, the model has been updated | 16/12/2025 | 21.0000000000000 | 24 Dec: bottom cable tray is modified, no further comment | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | Electrical |  | Shichen Li | 26-Dec-2025: 3D model updated as per comments. | 26/12/2025 | 11.6236111111139 | [5 empty] | Electrical | [5 empty] | 08/01/2026 | ID: 19
E327C | M17 |  | M17-E327C | Cable tray Sizing and MCT Sizing to be verified as per the Project requirement | Marcus | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b3cc5738342c4b8ba55a7e97f38ce089][1]_[2].png","originalImageName":"E327C-M17"} |  |  | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 08/01/2026 | ID: 19
E328C | M17 |  | M17-E328C | General Comment :Suitable vertical cable tray /Modular Support to be provided for Transistion from Horizontal cable tray to the Panel MCT | Welton | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[525327b624fd41308e7c6a7b57dc22b6][1]_[2].png","originalImageName":"E328C-M17"} |  |  | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 08/01/2026 | ID: 19
E329C | M17 |  | M17-E329C | Sutiable space for cable pullling to be Evaluated for Level-3 Ceiling and Level-2 Ceiling | Ratha | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[cbd4307077a34cdfb7d21a10873dd264][1]_[2].png","originalImageName":"E329C-M17"} |  |  | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 08/01/2026 | ID: 19
E330C | M17 |  | M17-E330C | HVAC duct support clashing with Cable entry to the MCT | Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1d33b2a164c44346ae9ce436f442cf83][1]_[2].png","originalImageName":"E330C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[a305189e07ad4ba697496ff9f2dfdccb][1]_[7].png","originalImageName":"330"} | NO | ELECTRICAL | ABB/CIMC | 16/12/2025 | CIMC | Close | 2025/12/17, the model has been updated | 16/12/2025 | 27.0000000000000 | 24 Dec: MCT is cleared to cable tray. no further comment. | 23/12/2025 | Tee |  |  | ELECTRICAL |  |  |  | Electrical |  | Shichen Li | 26-Dec-2025: 3D model updated as per comments. | 26/12/2025 | 18.6229166666672 | 14/01/26-UR7U-Noted. HVAC duct relocated. | Welton |  | 13/01/2026 | 12.01.26 - NA53 - Close | Electrical |  | 13/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 398
E331C | M17 |  | M17-E331C | Multi support clashing with Cable entry to the MCT, Blockage to be cleared | Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[8db040157f804699a0b30198fb203df1][1]_[2].png","originalImageName":"E331C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2b45c97fd9214ce1a47912a593477dfa][2]_[14].png","originalImageName":"E331C-20251226"} | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending Petrobras | 2025/12/26,this multi support and detector had been shifted to another position to avoid clash with cable entry | 25/12/2025 | 14.0000000000000 | 7 Jan: Cable entry is cleared. No further comment | 06/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan: 3D model has been updated as per punch comments. | 10/01/2026 | -1.55208333333576 | [5 empty] | ELECTRICAL | [5 empty] | 10/01/2026 | ID: 579
E332C | M17 |  | M17-E332C | Suitable vertical cable tray /Modular Support to be provided for Transistion from Horizontal cable tray to the Panel MCT | Deivission | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[b87d2dc3553746e08f265228e157cf42][1]_[2].png","originalImageName":"E332C-M17"} |  |  | NO | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending ABB/CIMC | [8 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 08/01/2026 | ID: 19
E333C | M17 |  | M17-E333C | AHU cable Entry to be Evaluated to change as per the Cable routing EXT-5255001A, EXT-5255001B EXT-5255002A & EXT-5255002B | Ratha | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[45b4b0ae5fad468099aa4c07490009b2][1]_[2].png","originalImageName":"E333C-M17"} |  |  | YES | HVAC | ABB | 25/12/2025 | CIMC | Pending ABB/CIMC | [8 empty] | HVAC |  |  |  | HVAC | [10 empty] | HVAC | [5 empty] | 08/01/2026 | ID: 19
E334C | M17 |  | M17-E334C | Check the Possibity to Move the Veritcal beam to have access for Cable Pulling | Ratha | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[ef9b88bf69584bbea464557988fd9c02][1]_[2].png","originalImageName":"E334C-M17"} |  |  | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Rejected | 2026/01/02：the movement of punched structure is not recommended by structure engineer after strength analysis. ABB/CIMC intend to remain current arrangement.please confirm the acceptance. | 01/01/2026 | 7.00000000000000 | 7 Jan: Vendor to proof/demonstrate how the cable pulling activities can be done with current arrangement | 06/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan: ABB/CIMC advise to demonstrate how the cable pulling activities can be done with current arrangement. | 10/01/2026 | -1.55347222222190 | [5 empty] | ELECTRICAL | [5 empty] | 10/01/2026 | ID: 579
E335C | M13R |  | M13R-E335C | 1.Maintenance Access shall be provided for the Lighting Junction CXE-L-M13-046 -To change location (allow access) 2.CXE-L-M13-019 - two JB in same place - Junction box to be relocated near to Lighting Fixture | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c063f031851545f88678d6152f492fce][1]_[2].png","originalImageName":"E335C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b748fea30f03463eb62fb1006b94c428][2]_[11].png","originalImageName":"335c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending Petrobras | 2026/01/04: CXE-L-M13-046 is shifted to handrail outside and the front access can be ensuered, CXE-L-M13-019 duplication issue is resolved. | 03/01/2026 | 5.00000000000000 | 7 Jan: Both JBs relocated with maintenance access, no further comment | 06/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  | Shichen Li | 10-Jan: 3D model has been updated as per punch comments. | 10/01/2026 | -1.55763888888760 | [5 empty] | ELECTRICAL | [5 empty] | 10/01/2026 | ID: 579
E336C | M13R |  | M13R-E336C | All Lighting fixture and Small Power Junction shall be Lower down to 1.3 M at Level-3 Roof Top | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[96c5238d87e84fae98cb5df9296e518b][1]_[2].png","originalImageName":"E336C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1f18a0afc666496493a1b2164b04b20a][2]_[12].png","originalImageName":"E336C-20251230"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending Seatrium | 2025/2/30,All Lighting fixture and Small Power Junction had been Lowered down to 1.3 M at Level-3 Roof Top | 29/12/2025 | 14.0000000000000 | 14 Jan: Kindly refer to attached for the comment. | 12/01/2026 | Tee |  |  | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 14/01/2026 | ID: 592
E337C | M17 |  | M17-E337C | All Lighting fixture and Small Power Junction shall be Lower down to 1.3 M at Level-4 HVAC outer door Area and Level-5 Roof Top | Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[ca314505e18644e0b6927e61b2da9a36][1]_[2].png","originalImageName":"E337C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[8353089619614d8ebc8732f4988c7a0b][2]_[12].png","originalImageName":"337c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending KBR | 2026/01/04：All Lighting fixture Junction box had been lowered more or less for easy maintenance purpose at Level-4 HVAC outer door Area and Level-5 Roof Top | 03/01/2026 | 3.00000000000000 | [5 empty] | ELECTRICAL |  |  |  | ELECTRICAL | [10 empty] | ELECTRICAL | [5 empty] | 08/01/2026 | ID: 19
E338C | M13R |  | M13R-E338C | KBR to check the Handrail gap between Interface staircase M13R and M13 Module | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[52240cf6e7ed4d69bdcf41ce1769a20a][1]_[2].png","originalImageName":"E338C-M13R"} |  |  | NO | STRUCTURAL | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/17, please KBR to check the handrail gap betwwen interface. | 16/12/2025 | 27.0000000000000 | KBR STR (30 Dec 2025): What was highlighted is within M13 Module handrail. Please see attachment M13R-E388C KBR STR 20251229 for verification. The interface distance between M13R & M13 Module handrail is less than 125 mm as per Guardrail Standard. Suggest ABB to modify | 30/12/2025 | Bobby Pramayudha |  |  | Structure | Refer to M13R-E388C KBR STR 20251229.pdf attachment |  |  | Structure |  | Caryn Tan | 13-Jan-26: Model updated. | 12/01/2026 | 0 | The gap is in accordance with the standard guardrail drawing. | Maxwell |  | 14/01/2026 |  | Structure | [5 empty] | 14/01/2026 | ID: 539
E339C | M17 |  | M17-E339C | PB need clarity for safe handling the core on jacking and skidling rail to rotate 90 degree near transformer position ABB to Provide information for the handling tools (size and weight) for the Transformer core handling | Tulio/Juliana | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[daeeeb50f6a54a748e0d0aebb9d86c4e][1]_[2].png","originalImageName":"E339C-M17"} |  |  | NO | MATERIAL HANDLING | ABB/CIMC | 30/12/2025 | CIMC | Pending KBR | 25/12/25: The latest version of the Transformer core maintenance proposal has been uploaded. Please refer to Attachment P84 E-house material handling plan---Transformer.pptx. In this solution, during any process that requires operating the jack, the Core is fixed on the Rail platform. Moreover, the jack can be controlled through hoses remotely, and the operator does not need to operate under the Core. | 24/12/2025 | 13.0000000000000 | [5 empty] | Mechanical Handling |  |  |  | Mechanical Handling | [10 empty] | Mechanical Handling | [5 empty] | 08/01/2026 | ID: 19
E340C | M17 |  | M17-E340C | PFP to be extended for cable tray Support and Piping Support below Level-1 | Danilo Alexandre Lima Cardosoo/Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1278a137aa2b42aa995a7557ccb09185][1]_[2].png","originalImageName":"E340C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[dd3c84d7c6b74062835e1bc943e14d81][2]_[17].png","originalImageName":"E340C-20251230"} | NO | SAFETY | ABB/CIMC | 30/12/2025 | CIMC | Pending Petrobras | 2025.12.20： PFP model has been updated | 04/01/2026 | 6.00000000000000 | 5 Jan 2026: As per ABB closeout image, the PFP provision has complied with the coatback requirement of 450 mm as per Detail 4 of I-DE-3010.2S-1428-190-AIW-008_B M-17 - AUTOMATION AND ELECTRICAL - PASSIVE FIRE PROTECTION (PFP) LAYOUT, SECTIONS AND DETAILS. | 04/01/2026 | Indra/ Hong |  |  | Safety |  | 04/01/2026 | 7.65625000000000 | Safety |  | Tsen Tze Jia | 12 Jan: As per the latest model (20260109), the model is aligned with the drawing ( I-DE-3010.2S-1428-190-AIW-008_B ) | 12/01/2026 | -1.65625000000000 | [5 empty] | Safety | [5 empty] | 12/01/2026 | ID: 96
E341C | M17 |  | M17-E341C | Suitable solution to be provided to avoid water ingress in to battery room air lock door and Equipment room air lock door | Bruno/Alvim | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[dda899d2810446ee8a62f50c87aca1c4][1]_[2].png","originalImageName":"E341-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[9a506834bd60459e975b43afa515ddfd][2]_[20].png","originalImageName":"E341C-20260105"} | YES | PIPING | ABB/CIMC | 30/12/2025 | CIMC | Pending KBR | 2025/12/18, as per discussion , ABB/CIMC propose to add a slop in front of the door by using PFP ,refer to snapshot . | 17/12/2025 | 20.0000000000000 | [5 empty] | PIPING |  |  |  | PIPING | [10 empty] | PIPING | [5 empty] | 08/01/2026 | ID: 19
E342C | M17 |  | M17-E342C | ESA Antenna to ensure the Maintenance access | Tulio | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[1acb16f9942d469b918830fafc58f1e8][1]_[2].png","originalImageName":"E342C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[c76f06a7db514105b3fed9dd0a001def][2]_[21].png","originalImageName":"342c"} | YES | ELECTRICAL | ABB/CIMC | 14/01/2026 | CIMC | Pending Petrobras | 2025/12/19, the model has been updated 2026/01/01: close out snapshot is updated and tag no, hierachy is shown clearly. | 31/12/2025 | 6.00000000000000 | 24 Dec: Please include tag no. & hierarchy for the item in the punch for easier identify and review. 07-Jan: ESA antennas were positioned free from obstruction for accessibility. KBR has no comments. | 06/01/2026 | Roberto |  |  | Instrument |  |  |  | Electrical |  | Shichen Li | 26-Dec-2025: KBR comments need to be implemented. 7-Jan-2026: 3D model updated as per punch comments. | 07/01/2026 | -0.940972222218988 | [5 empty] | Electrical | [5 empty] | 08/01/2026 | ID: 19
E343C | M17 |  | M17-E343C | GAS detector support shall be changed to Welded Support instead of Bolt Supports | Deivissio/Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[4ac56188239f443caa4f91c5c026e371][1]_[2].png","originalImageName":"E343C-M17"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2e17ed05e91a4ebf8512546ee9f3bc99][2]_[11].png","originalImageName":"E343C-20251225"} | YES | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/25，the gas detector support had been changed to welded support ,refer to model on 25-Dec-25 | 24/12/2025 | 18.0000000000000 | KBR has no comments. | 29/12/2025 | Roberto |  |  | Instrument |  |  |  | Instrument |  | Guanyu Zhu | 08/01/2026: no comment | 08/01/2026 | 4.63541666666424 | [U5D6 - 13/JAN/2026] As per closeout snapshot , can be closed | U5D6 |  | 12/01/2026 | [U5D6 - 11/JAN/2026] This needs operation team agreement. I am discussing with them. Discussion ongoing. | Instrument |  | 12/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 399
E344C | M13R | Level 2 | M13R-E344C | GAS detector support shall be changed to Welded Support instead of Bolt Supports | Deivissio/Bruno | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[823f9a942c7e4852977bbac09a7ed39b][1]_[2].png","originalImageName":"E344C-M13R"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[f7a51986241f434a8372ef204cc1fc60][2]_[12].png","originalImageName":"E344C-20251225"} | YES | INSTRUMENTATION | ABB/CIMC | 30/12/2025 | CIMC | Close | 2025/12/25，the gas detector support had been changed to welded support ,refer to model on 25-Dec-25 | 24/12/2025 | 18.0000000000000 | KBR has no comments. | 30/12/2025 | Roberto |  |  | Instrument |  |  |  | Instrument |  | Guanyu Zhu | 08/01/2026: no comment | 08/01/2026 | 4.63402777777810 | [U5D6 - 13/JAN/2026] As per closeout snapshot , can be closed | U5D6 |  | 12/01/2026 | [U5D6 - 11/JAN/2026] This needs operation team agreement. I am discussing with them. Discussion ongoing. | Instrument |  | 12/01/2026 | -1.00000000000000 |  |  | 13/01/2026 | ID: 399
E089A | M17 | Level-5 | M17-E089A | Sufficient Maintanence Space to be provided in front of Supply Air in take for Transformer Room Supply Fan Ducting (VT-5254002A/2B/2C & VT-5254001A/1B/1C ) | Petrobras-Tamer | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d5fabe81c09648caa11e62f1ad49fabe][2]_[13].png","originalImageName":"E089A"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[2bcedf6da44c4d429edd277379809a88][2]_[30].png","originalImageName":"89A"} | YES | HVAC | Seatrium | 27/11/2025 | ABB | Pending Petrobras | 23 May 25：CIMC have already updated location of air intake according to double line drawing. 2025/9/12:There is no filter for transformer room air intake mist eliminator,and only one air intake towards to FWD shall be equiped with gas dectector, please confirm. 2025/09/30 The pneumatic tubing has been rerouted outside of the actuator maintenance volume. 2025/10/27,In current 3d model, there are three are air intakes drop eliminators but gas detectors are only installed in front of one of the air intakes, PB Safety to confirm this is acceptable before this punch can be closed. 7-Nov-25 I-RL-3010.2S-5400-98G-S2N-005 - DISPERSION ANALYSIS REPOR GAST to be submitted by KBR next week. pending KBR submission and close the punch. 28-Nov-25, already update the 3D model as per PB comments and delete all the H2S detector in 3D model according to I-RL-3010.2S-5400-98G-S2N-005_0 Tables 9-2 and 9-3, only reaming CH4 and CO2 detectors. PLS check the latest 3D model and close the punch. 26-DEC-25: Sufficient Maintanence Space can be ensured for Air intake for Transformer Room Supply Fan Ducting (VT-5254002A/2B/2C & VT-5254001A/1B/1C ), detector type is also revised as per dispersion analysis report. please review the latest model again. | 25/12/2025 | 6.00000000000000 | The revised locations of transformer room supply fans air intake shall consider the smoke and gas detectors. Currently, it seems that provision for the detectors is not provided. Also, the inlets are located directly below cable trays which can potentially have an issue to the filter / mist eliminators' maintenance and access. CIMC / ABB to re-evaluate the proposed locations. 15Sept25: The pneumatic tubing is directly routed on the damper actuator maintenance space. Suggest to reroute to avoid clash. 02Oct25: Noted 05Nov25: Gas detectors to be modelled only after submission of the dispersion analysis report. 11Nov25: Noted. Refer KBR comment dated 05Nov25 13Nov25: Transfer to DR90 due to dispersion analysis report available date. 28Nov25: Noted on the action in reference to I-RL-3010.2S-5400-98G-S2N-005_0 2025Dec30: Noted | 30/12/2025 | Allan |  |  | HVAC |  |  |  | HVAC |  | Mun Kek Chian | Please model the obstruction space required for air intake air filter replacement, mist eliminator cleaning and gas detector. It seems that the latest model layout has not considered the gas detector installation which may block the material handling path/ access way. 15-Sep-2025: Please address KBR's comment. 3-Oct-2025: Noted, closed. 2-Jan-2026: Noted, closed. | 02/01/2026 | -1.41666666666424 | 04nov25 This punch remains open. The location/coordinates of gas detectors in air intakes shall be confirmed by the I-RL-3010.2S-5400-98G-S2N-005 - DISPERSION ANALYSIS REPOR GAST, which has not been issued yet. Once this report is issued, Seller shall ensure that coordinates of the gas detectors in 3D model are consistent with the report recommendations and then submit this punch to Petrobras. 28nov2025 (Danilo): According to I-RL-3010.2S-5400-98G-S2N-005_0 Tables 9-2 and 9-3, only CH4 and CO2 detectors are required for these air intakes. Please correct. 02dec2025: The position of these detectors shall be confirmed based on all the cases of gas plumes that come from the process plant, according to I-RL-3010.2S-5400-98G-S2N-005_0. | Kleber / Danilo |  |  |  | Safety |  |  |  | 5-Nov-25 I-RL-3010.2S-5400-98G-S2N-005 - DISPERSION ANALYSIS REPOR GAST to be submitted by KBR next week. |  | 02/01/2026 | ID: 101
E062B | M17 | Level-1 | M17-E062B | Detector shall be installed Maximum 300 mm from the Ceiling as per NFPA requirement DR90:Access for the Transformer Detector from top to be evaluated for testing and maintenance | Rafael | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[6cb1abe2effc494eb6247f8216d85581][2]_[13].png","originalImageName":"E062B"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[b50ffc2625054c4f80772194830ef9a5][2]_[15].png","originalImageName":"E062B-1"} | YES | INSTRUMENTATION | ABB/CIMC | 03/11/2025 | CIMC | Pending KBR | 02-SEP-2025:The update has been completed. 23-SEP-2025：Transformer room smoke detector future replacement is obviously impossible since NFPA requirement is priority to be satisfied. which CIMC already stated in discussion. Seatrium to confirm the access acceptance for other rooms. 29-SEP-25: Seatrium to confirm whether NFPA72 is mandotory requirement. if yes, all parties need a further discussion. 10-OCT-25: ABB to clarify 22-OCT-25: the current smoke detector arrangement already met the requirement of NFPA 72. due to the blockage of lots ducts,cable trays and pipes, it's not able to build temporaty scaffolding. ABB/CIMC suppgest that operator to approach the smoke dector by using of cable tray, Duct support for the replacement and re-assembly purpose. which is also the same solution for Tie-in cable pulling. please consider again. 22-OCT-25: The current smoke detector arrangement already meets the requirements of NFPA 72. Please be informed that due to the blockage caused by numerous ducts, cable trays, and pipes, it is not possible to install permanent or temporary scaffolding in the room. To comply with NFPA 72, CIMC suggests that operators access the smoke detectors by utilizing the cable tray supports and duct supports for heavy maintenance tasks. This approach is also the same solution used for tie-in cable pulling. For routine maintenance such as replacement or reassembly of detector heads, this can be performed directly using a test pole kit. Please acknowledge and confirm. 04-NOV-25: Transformer room smoke detector maintenance space are re-modeled as per what Mr Refael said during the DR60% closeout meeting. slightly clash shall not be considered temporarily which already agreed by PB. please review again. 2025/12/26, The detector maintenance volume clash had been cleared , refer to attachement for all transformer detector.ABB propose to use lifting table (max 6m ) and handling tools(3m) to replace detector. | 25/12/2025 | 0 | Sept-22: The required distance from the ceiling has been met, but SEA is to confirm elevation acceptance (>5m) from the flooring. Sept 25: ABB has provided their action response to SEA’s comments. SEA to review and confirm acceptance. 30-Sept-25: As per NFPA 72 section 17.6.3.1.3.1: "Unless otherwise modified by 17.6.3.7: "Spot-type heat-sensing fire detectors shall be located on the ceiling not less than 4 in (100 mm) from the sidewall or on the sidewalls between 4 in and 12 in (100 mm and 300 mm) from the ceiling. However, as per NFPA 72 section 17.6.3.7: "Where a detector is used in an application other than open area protection, the manufacturer’s published instructions shall be followed." If there is instruction for the detector's location from the manufacturer's, it shall be followed. Otherwise, NFPA 72 section 17.6.3.1.3.1 governs. |  | Roberto & Sesep Sianturi (KBR Safety) | 29-Sept: Seeking advice from KBR Safety based on the responses from SEA and ABB. |  | Safety |  | 30/09/2025 | 86.5770833333299 | Instrument |  | Guanyu Zhu | 22 Sep 25 Noted that 3D model is updated. Request ABB to make sure no access issue for future detector replacement. 25 Sep 25 Rejected because future disassembly is not possible for Transformer Room. 30 Sep 25 NFPA72 is a requirement under PB Spec. For specific cases where compliance is challenging, please raise a TQF to seek approval. 22 Oct 25 ABB proposal is subjected to PB approval |  |  | [U5D6 - 28/OCT/2025] ABB/CIMC please confirm that): a) The sensors will not be placed on above the transformers (so if anyone falls, they don't fall over a live equipment). b) lugs will be placed on the ceiling for Industrial Climbers to be able to go up to the detectors and trays at the top. It is also forbidden to use cable tray as a pathway for displacement. [U5D6 - 06/NOV/2025] In this room, the access to the instruments will be very challenging, and it will not be possible to solve before end of DR60. So, PB asked SEA/KBR/CIMC/ABB to expand the operation volume of the instruments so that the best location for the sensors can be selected in conjunction by SEA/KBR/CIMC/ABB and PB (with operation team agreement). For now, the expanded volume is acceptable (even clashing with other objects), because that volume is what will enable all parties to select appropriate location for the sensors. Therefore, we are sending this item to DR90 with the expanded volumes, and this item will need to be revisited in a meeting in the near future. | U5D6 |  |  |  | Instrument |  |  |  | pending Seatrium clarify lugs use |  | 26/12/2025 | ID: 839
E115B | M13R | Level-1 | M13R-E115B | SEATRIUM /KBR to provide the Equipment Tag no CSS Remote IO Panel | Rafael | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d4fe3bf1e0ff49a28083895dbaee9ee9][2]_[13].png","originalImageName":"115"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[316c18e42bd34333ac17dfef50047b53][2]_[27].png","originalImageName":"E115B"} | NO | INSTRUMENTATION | ABB/CIMC | 14/10/2025 | CIMC | Close | 2025/09/16: CSS remote IO panel tag already assigned 2025/09/22， please KBR provide the correct tag number,refer to attached email 2025/12/26： CSS remote IO panel are conbined as per KBR inform, refer to latest model. | 25/12/2025 | 15.0000000000000 | KBR has no comments. | 29/12/2025 | Roberto |  |  | Instrument | Refer to attachment M13R-E115B |  |  | Instrument |  | Guanyu Zhu | 17 Sep 25: 3D model has been updated. 29 Sep 25: CSS RIO panel is under sizing based on latest information. Tag No. to be finalized before ABB DR90 1/1/2026: no comment | 01/01/2026 | 9.29305555555766 | [U5D6 - 21/SEP/2025] PN-5520113C is an incorrect TAG. Both the drawing and the 3D model need to be updated. 113C ending means the panel would be the RIO for M13C and M13C does not exist. [U5D6 - 01/OCT/2025] Suggestion: will transfer to DR90. From what has been presented, it is not possible to solve now. If layout is going to be finalized in Feb 2026, who will update model then (this is after DR90)? [U5D6 - 11/JAN/2026] Can be closed as per closeout snapshot. | U5D6 |  | 10/01/2026 |  | Instrument |  | 10/01/2026 | -1.00000000000000 | CIMC |  | 11/01/2026 | ID: 399
E228B | M13R | Level-3 | M13R-E228B | General Comment: Secondary Cable tray for the instrument to be Modelled | Cid | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[c16001adaa344546812bddbce52883b5][2]_[13].png","originalImageName":"228"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[0052565e328a4c3e8d6bdeb6e2f222e8][2]_[24].png","originalImageName":"E228C"} | YES | INSTRUMENTATION | ABB/CIMC | 23/10/2025 | CIMC | Pending KBR | 19-SEP-25: According to the current cable book input, there are no instrument cables 2025/10/02, consider current instrument cable schedule input ,suggest to move this punch to DR90 2025/12/26: Refer to the latest model and cabel schedule 2026/01/13: ABB/CIMC confirmed that all secondary instrument tray modeling is completed, please indicate if any missed. | 12/01/2026 | 0 | 22-Sept: This is a general remark. SEA to confirm if the secondary tray part of DR60. 03-Oct: SEA to evaluate and provide advice on ABB's recommendation. 13-Jan: As per SEA’s comment, this punch list is a general comment for all levels of M-13R. ABB to confirm that the secondary tray modeling is completed and that no further trays need to be modeled. | 12/01/2026 | Roberto |  |  | Instrument |  |  |  | Instrument |  | Guanyu Zhu | 22 Sep 25 no comment 03 Oct 25: No comment for proposal to transferring to DR90 |  |  | [U5D6 - 28/SEP/2025] You either plan ahead and reserve some space now (not needed to model support), based on the instruments and JBs, or transfer to DR90. [U5D6 - 07/OCT/2025] All parties agreed with transfer to DR90. Changing status to "Transfer to DR90". | U5D6 |  |  |  | Instrument |  |  |  | CIMC |  | 13/01/2026 | ID: 839
E300B | M13R | Level-1&Level2&Level3 | M13R-E300B | For Level-1 ,Level-2,Level-3 & Roof Top UHF Active Rep System: it is missing to represent the coaxial cables route fixed on hangers outside some trays, which do not need to be Telecom trays, but anyone as close from headroom and paths to allow coverage. LV seems the best for better coverage. | Christiano | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[d5aca27e4e1b4c1d8c63472d0ca25f44][2]_[13].png","originalImageName":"300"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[57ad495ae71549fa842fed40fcd5ed0e][2]_[31].png","originalImageName":"300B"} | YES | Telecom | ABB/CIMC | 14/01/2026 | CIMC | Pending Petrobras | 2025-10-13: the simulation path of M13R leaky coaxial cable(Crf-DIV-5515002.004) is shown in 3D model 2025/10/27: cable simulation model are updated as per Seatrium advice 2025-11-21: DIV-5515002 model is updated as per PB/Seatrium advice 2025-11-25: DIV-5515002 model is updated as per PB/Seatrium advice 2025-12-26: All relative cables for DIV-5515002 are simulated(include jumper cable), refer to the latest model.there have no impact on escape route. | 01/01/2026 | -7.00000000000000 | Noted as per ABB/CIMC Update. 10/1/2025-Noted as per ABB/CIMC Update. |  | Manogar |  |  | Telecom |  |  |  | Telecom |  | Nur Haedzerin | 22/10/2025: To review and minimize the number of bends along the leaky cable route. Each bend introduces potential RF loss and might affect signal performance. 30/10/2025: Noted as per ABB/CIMC update 20/11/2025: 7/8" coaxial cable and 1/2" coaxial cable will be routed through the same splitter (DIV-5515002). With these two cables installed, there will be insufficient space for cable bending and creating a risk of cable damage. Please rectify as per PB recommendations. 24/11/2025: ABB/CIMC to rectify DIV-5515002 as per agreed during discussion with Seatrium 25/11/2025: Noted as per ABB update |  |  | 2025.11.18: there will be 2 coaxial cables of 7/8 in cable at this DIV-5515002 and also 2 coaxial cables of ½ in cable at this same DIV. The ones represented are the 7/8 in ones. There will be no space for cable bending without damage the cable. First attempt is to move the DIV to left so there is enough space on both sides. Second is to relocate the MCT at floor of deck above DIV to closer to the wall or to some beam. 2025.11.27: arrangement is still not functional and requires to be solved. 1/2" cable need to enter perpendicular to connector and cannot make 90º bend, which will let the cable so close to headroom just near the door. Look the attached picture. Some other solution shall be provided to protect people and the cable. | Chris |  |  |  | Telecom |  |  |  | CIMC |  | 26/12/2025 | ID: 839
E396B | M13R | Level-3 | M13R-E396B | EX Camera to be provided at M13R Roof Top, Seatrium/KBR to confirm to include in 3D Model, Telecom Layout and Telecom Cable Block Diagram | Allan | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[2a6b2b8c439f400ba9792ab1482afd71][2]_[13].png","originalImageName":"396"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[06e73a5b2bdb461eaa992563e5d729c4][2]_[26].png","originalImageName":"396B"} | YES | Telecom | ABB/CIMC | 14/01/2026 | CIMC | Pending Petrobras | 02-SEP-25: The EX camera has been placed on the port side 2025/12/26: EX camera location has been changed as per DR90 discussion, KBR/SEA to finalize the camera type | 25/12/2025 | 13.0000000000000 | Noted as per ABB/CIMC Update | 07/01/2026 | Manogar |  |  | Telecom |  |  |  | Telecom |  | Chew Weng Kit | Dual vision thermal camera was modelled with the temporary tag CAM-XXX. Final location to be advised by PB. 8/Jan/26: Camera model unchanged. | 07/01/2026 | 0 | Camera modelproposed in 3D is a thermal one, which is not required their. I guess a PTZ one is enough. The location looks like good, but Operation can confirm during DR90. | Christiano |  |  |  | Telecom |  |  |  | CIMC |  | 08/01/2026 | ID: 98
E471B | M17 | Level-5 | M17-E471B | HVAC External Duct support ( roof top ) design to be double checked . Bolted or welded .VAC roof top duct support system to check different loading condition and provide calculation as required . Lifting arrangement clash with roof duct , to be studied . | Prakash | {"fileName":"Reserved_ImageAttachment_[14]_[PunchSnapShot1][32]_[72fe9bed3af5420b9fb6d828eeded902][2]_[12].png","originalImageName":"471"} |  | {"fileName":"Reserved_ImageAttachment_[16]_[ClosingSnapShot1][32]_[1783c3ccda524ba380c69fb8099da4a4][2]_[14].png","originalImageName":"471-1"} | YES | HVAC | ABB | 29/11/2025 | ABB | Pending ABB/CIMC | 2025/11/03,HVAC external duct support will use welding support , for these items clash with lifting arrangment ,CIMC propose to loose supply,please seatrium confirm . 2025/11/05, CIMC completed the HVAC structual support calculation ,the result is fine,refer to snapshot .the detail calcualtion will be shown in local calculaiton report Rev A. 2025/11/13，please refer to attached structural local calculation report , CIMC already based on lifting clash to move HVAC duct support to hook up hierechy ,refer to snapshot . |  |  | 05Nov25: ABB / CIMC to provide the duct support calculation to establish the duct support integrity. Lifting plan shall also be provided. 06Nov25: Noted on Structural support calculation. However, calculation shall also be provided to establish integrity for the proposed "mini bracket" type of support for outdoor ducts. Furthermore, ABB to identify which are the ducts will be trail fitted, tested and ship loosed at (1) hook up area (2) clash due to final lifting. 14Nov25: ABB / CIMC to clarify if the "mini bracket" type support is still used as the structural calc report is not attached / submitted. |  | Allan |  |  | HVAC |  |  |  | HVAC |  | Mun Kek Chian | Please address KBR's comment. 17-Nov-2025: In email discussion, ABB proposed to change the duct support design to other type to substitute the "mini bracket" support design. This is contradicting to the closed out response by ABB here. Furthermore, there is no calculation or analysis being submitted to KBR/ SEA to justify the existing duct support design. Meanwhile, please provide submission plan for lifting plan as per Seatrium construction team's request in order to close this punch. 25-Nov-2025: Suggest transfer to “DR 90 “ wrt to Clash and Ship loose: 1)Reg external structural Duct support ( Bolted or welded ) after ship loose duct to be installed on board –does the duct support to be bolted or we need to weld on board . 2)Reg access ABB need shall have access to reach roof top elevation for required maintenance to access any damper, detectors, and others if any. | [7 empty] | HVAC |  |  |  | Pending ABB confirm on lifting plan. |  | 29/12/2025 | ID: 539